## BoQ1
Government eProcurement System Created By: Saubhik Pan Created Date/Time: 25-Apr-2025 05:39 PM Tender Title: Reconfiguration of Existing and Under-Construction Terminal Buildings- Phase-II. SH- Provision of Air Conditioning Tender ID: 2025_AAI_228823_1
Tender Inviting Authority: Airports Authority of india, Dibrugarh Airport
Name of Work: RECONFIGURATION OF EXISTING AND UNDER-CONSTRUCTION TERMINAL BUILDINGS-PH-II SH: PROVISION OF AIR CONDITIONING AT DIBRUGARH AIRPORT
Contract No: 2025_AAI_228823_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | SNOWMEX ENGINEERS LIMITED (GSTN-07AAMCS8717P1ZF) BID ID -838203 |  | Powermech Services Private Limited (GSTN-NA) BID ID -836254
[5 empty] | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply, Installation, Testing and commissioning of factory built floor mounted/Ceiling suspended chilled water double skin type air handling units made of panels consisting of pre plasticised G.I. casing of 0.60mm outside layer and 0.6 mm inside layer with polyurethane foam (PUF) insulation of 23+/-2 mm minimum thickness and 38 kg/cum density injected between them, complete with blower section with blower suitable for static pressure as detailed below, cooling coil section with aluminium finned copper tubes ( tubes thickness not less than 0.41mm) cooling coil, filter section with 50mm thick washable synthetic type air pre-filters belt drive package with TEFC drive motor (IE-2) suitable for 415±10% volts , 50Hz, 3 Phase AC supply, drain connections, stainless steel (18G) drain pan PUF insulation necessary vibration isolation arrangement etc. complete as per specification and of following capacities. Note: AHU should have provision for placing the adequate UVGI lamps/system
1.10 | FLOOR MOUNTED 18000 Cfm (nominal) of Static Pressue 50 mm of WC | 1.00 | Job | 803700.00 | 705000.00 | 705000.00 | 886060.00 | 886060.00 | 705000.00 | SNOWMEX ENGINEERS LIMITED
1.20 | FLOOR MOUNTED 12000 Cfm (nominal) of Static Pressue 50 mm of WC | 1.00 | Job | 515271.00 | 508000.00 | 508000.00 | 609166.00 | 609166.00 | 508000.00 | SNOWMEX ENGINEERS LIMITED
1.30 | CEILING SUSPENDED 3500 Cfm (nominal) of Static Pressue 50 mm of WC | 1.00 | Job | 202449.00 | 265000.00 | 265000.00 | 236898.00 | 236898.00 | 236898.00 | Powermech Services Private Limited
2.00 | Supplying, laying/ fixing, testing and commissioning of following nominal sizes of chilled water piping inside the building/masonry ducts (with necessary clamps, vibration isolators, bends, reducers, tees, supports, flow indicators etc. fittings but excluding valves, strainers, gauges etc.) duly insulated with following closed cell elastometric nitrile rubber of minimum 45 Kg / m3 density, thermal conductivity 0.037 W/MK or better at 20 deg. mean temperature class ‘O’ insulation applied by suitable adhesive complete including repairing of damage to building etc. as per specifications and as required complete in all respect. Note:- The Pipes of sizes 150 mm & below shall be M.S. ‘C’ class as per IS : 1239. (Nominal Thickness of the nitrile insulation shall be 32 mm).
2.10 | 80mm Dia. | 100.00 | Meter | 4199.00 | 1900.00 | 190000.00 | 1135.00 | 113500.00 | 113500.00 | Powermech Services Private Limited
2.20 | 65mm Dia. | 65.00 | Meter | 3305.00 | 1700.00 | 110500.00 | 982.00 | 63830.00 | 63830.00 | Powermech Services Private Limited
2.30 | 50mm Dia. | 25.00 | Meter | 2492.00 | 900.00 | 22500.00 | 847.00 | 21175.00 | 21175.00 | Powermech Services Private Limited
3.00 | Supply, installation, testing and commissioning of following normal sizes of insulated ( insulation thickness 9mm class O fire rated ) CPVC drain piping of 50mm (nominal) size with necessary claps, bends, supports, etc. as required and specified. 40 mm dia | 75.00 | Meter | 614.00 | 480.00 | 36000.00 | 419.00 | 31425.00 | 31425.00 | Powermech Services Private Limited
4.00 | SITC of Valves: Supply, fixing, testing and commissioning of following valves duly insulated with same specifications as that of connected piping complete with companion flanges, nuts, bolts, gaskets, adequate support etc. as specified. BUTTERFLY VALVE (MANUAL) with CI body SS Disc, Nitrile Rubber Seal & O- Ring for chilled water/hot water circulation as specified.
4.10 | 80mm Dia. | 4.00 | Job | 10122.00 | 3600.00 | 14400.00 | 11954.00 | 47816.00 | 14400.00 | SNOWMEX ENGINEERS LIMITED
4.20 | 65mm Dia. | 8.00 | Job | 9283.00 | 3200.00 | 25600.00 | 10958.00 | 87664.00 | 25600.00 | SNOWMEX ENGINEERS LIMITED
4.30 | 50mm Dia. | 2.00 | Job | 7547.00 | 1200.00 | 2400.00 | 9563.00 | 19126.00 | 2400.00 | SNOWMEX ENGINEERS LIMITED
5.00 | Supplying, fixing, testing and commissioning of following valves, strainers, gauges in the chilled water plumbing duly insulated to the same specifications as the connected piping and adequately supported as per specifications. BALANCING VALVE with C I body flanged construction with EPDM coated disc long pitch with protected out pipe insulation for chilled / hot water circulation as specified.
5.10 | 80 mm dia | 1.00 | Job | 15302.00 | 10900.00 | 10900.00 | 14458.00 | 14458.00 | 10900.00 | SNOWMEX ENGINEERS LIMITED
5.20 | 65mm Dia. | 2.00 | Job | 15302.00 | 8600.00 | 17200.00 | 12676.00 | 25352.00 | 17200.00 | SNOWMEX ENGINEERS LIMITED
6.00 | Supply, Installation, Testing and Commissioning of following sizes electronic 2 way modulating control valve. The actuator shall be capable of accepting upto 10V DC and upto 20mA electric signal and shall provide similar transduced feedback output to control system. Maximum close off pressure shall not be less than 6 Bar for upto 50 mm valves and 7 Bar for 65 mm & above. Valves should have pressure rating of 25 Bar minimum.
6.10 | 80 mm dia | 1.00 | Job | 15302.00 | 33500.00 | 33500.00 | 132824.00 | 132824.00 | 33500.00 | SNOWMEX ENGINEERS LIMITED
6.20 | 65 mm dia | 2.00 | Job | 15302.00 | 26200.00 | 52400.00 | 99618.00 | 199236.00 | 52400.00 | SNOWMEX ENGINEERS LIMITED
7.00 | SITC of 65 mm (NB) Dial type Pressure Gauge as directed by EIC | 6.00 | Job | 2576.00 | 850.00 | 5100.00 | 3652.00 | 21912.00 | 5100.00 | SNOWMEX ENGINEERS LIMITED
8.00 | SITC of 65 mm (NB) Dial type Temperature Gauge as directed by EIC | 6.00 | Job | 2576.00 | 850.00 | 5100.00 | 2989.00 | 17934.00 | 5100.00 | SNOWMEX ENGINEERS LIMITED
9.00 | SITC of Automatic Air Vent with ball valve in brass connection complete with nipples, union etc. as required at all high points in the pipe lines, The valve shall be such as to have non-return valves as integral part of the valve. | 12.00 | Job | 3560.00 | 850.00 | 10200.00 | 2989.00 | 35868.00 | 10200.00 | SNOWMEX ENGINEERS LIMITED
10.00 | Ducting work Supply, installation, balancing and commissioning of fabricated at site GSS sheet metal rectangular/round ducting complete with neoprene rubber gaskets, elbows, splitter dampers, vanes, hangers, supports etc. as per approved drawings and specifications of following sheet thickness complete as required.
10.10 | 22 gauge | 250.00 | SqM | 1817.00 | 1050.00 | 262500.00 | 1295.00 | 323750.00 | 262500.00 | SNOWMEX ENGINEERS LIMITED
10.20 | 24 gauge | 500.00 | SqM | 1448.00 | 950.00 | 475000.00 | 1071.00 | 535500.00 | 475000.00 | SNOWMEX ENGINEERS LIMITED
11.00 | Supplying and fixing of following thickness closed cell Nitrile rubber (Class “O”) insulation on existing duct after applying suitable adhesive for Nitrile rubber. The joints shall be sealed witt self-adhesive nitrile rubber tape insulation complete as per specifications and as required 25 mm thickness | 600.00 | SqM | 1473.00 | 840.00 | 504000.00 | 498.00 | 298800.00 | 298800.00 | Powermech Services Private Limited
12.00 | Acoustic Insulation Supply, installation, testing and commissioning of 10mm thick open cell Class O Nitrile Rubber acoustic insulation. | 150.00 | SqM | 1677.00 | 550.00 | 82500.00 | 747.00 | 112050.00 | 82500.00 | SNOWMEX ENGINEERS LIMITED
13.00 | Supply and fixing of Fresh / Exhaust air Aluminium extruded with bird screen, damper adjustable louvers as per specifications and drawings | 2.00 | SqM | 12685.00 | 5200.00 | 10400.00 | 29885.00 | 59770.00 | 10400.00 | SNOWMEX ENGINEERS LIMITED
14.00 | Supplying & fixing of powder coated extruded aluminium Supply Air Grills with aluminium volume control dampers as per specifications | 10.00 | SqM | 22096.00 | 8600.00 | 86000.00 | 23244.00 | 232440.00 | 86000.00 | SNOWMEX ENGINEERS LIMITED
15.00 | Supplying & fixing of powder coated extruded aluminium Return Air Grills with louvers but without volume control dampers complete as required. | 20.00 | SqM | 18904.00 | 4850.00 | 97000.00 | 19924.00 | 398480.00 | 97000.00 | SNOWMEX ENGINEERS LIMITED
16.00 | Supply, installation, testing and commissioning of louvers without VCD | 3.00 | SqM | 18904.00 | 4200.00 | 12600.00 | 26565.00 | 79695.00 | 12600.00 | SNOWMEX ENGINEERS LIMITED
17.00 | Supply, installation , testing and balancing of BMS compatible motorised fire damper | 1.00 | SqM | 75345.00 | 11800.00 | 11800.00 | 99618.00 | 99618.00 | 11800.00 | SNOWMEX ENGINEERS LIMITED
18.00 | Supply, installation, testing and commissioning of GI volume control duct damper complete with neoprene rubber gaskets, nuts, bolts, screws linkages, flanges etc., as per specifications. | 5.00 | SqM | 16737.00 | 4650.00 | 23250.00 | 29885.00 | 149425.00 | 23250.00 | SNOWMEX ENGINEERS LIMITED
19.00 | SITC of UVGI system for AHUs comprising of all necessary accessories i.e. UV lamps , Aluminium Reflectors, Electronic Ballast, anodized Aluminium extruded stand for lamp housing, Control Panel, necessary cabling/wiring/MCBs/switches, timer and any other accessories to make the whole system fully operational as specified in the technical specification and as per site requirement as directed by the Engineer-in-charge, to be installed inside AHUs. | 2.00 | Job | 35855.00 | 57500.00 | 115000.00 | 132824.00 | 265648.00 | 115000.00 | SNOWMEX ENGINEERS LIMITED
20.00 | Electrical Work
20.10 | Supply, installation, testing and commissioning of 2 mm. CRCA sheeted powder coated Starter Panel for AHU, including SITC of suitable incomer switchgear, VFD, bypass starter complete with push button ON/OFF switch, indication lamp, voltmeter, ammeter and necessary protection devices etc. for operating above mentioned AHUs.
20.11 | 18000 CFM | 1.00 | Job | 73265.00 | 125000.00 | 125000.00 | 41507.00 | 41507.00 | 41507.00 | Powermech Services Private Limited
20.12 | 12000 CFM | 1.00 | Job | 73265.00 | 112000.00 | 112000.00 | 38187.00 | 38187.00 | 38187.00 | Powermech Services Private Limited
20.13 | 3500 CFM | 1.00 | Job | 73265.00 | 55200.00 | 55200.00 | 31546.00 | 31546.00 | 31546.00 | Powermech Services Private Limited
20.20 | Supply, laying and termination of 3C x 1.5 Sqmm Copper Flexible cable as per IS 694. | 150.00 | Meter | 229.00 | 135.00 | 20250.00 | 85.00 | 12750.00 | 12750.00 | Powermech Services Private Limited
20.30 | Supply, installation, testing and commissioning of 4C x 10 Sqmm Aluminium Armoured cable for Incoming Power Supply for AHU Starter panel as per IS 7098. | 300.00 | Meter | 317.00 | 172.00 | 51600.00 | 181.00 | 54300.00 | 51600.00 | SNOWMEX ENGINEERS LIMITED
20.40 | Supply, installation, testing and commissioning of 3C x 10 Sqmm Aluminium Armoured cable for AHU power from Starter panel IS 7098. | 120.00 | Meter | 300.00 | 169.00 | 20280.00 | 142.00 | 17040.00 | 17040.00 | Powermech Services Private Limited
20.50 | Supply, installation, testing and commissioning of 8SWG Gl Earthing Wire | 600.00 | Meter | 49.00 | 25.00 | 15000.00 | 100.00 | 60000.00 | 15000.00 | SNOWMEX ENGINEERS LIMITED
20.60 | Supply, installation, testing and commissioning of GI Perforated type Cable Tray of minimum size 150 mm x 50 mm x 1.6 mm. | 100.00 | Meter | 869.00 | 590.00 | 59000.00 | 626.00 | 62600.00 | 59000.00 | SNOWMEX ENGINEERS LIMITED
20.70 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
20.71 | 3 C x 10 Sq.mm | 8.00 | Job | 869.00 | 650.00 | 5200.00 | 698.00 | 5584.00 | 5200.00 | SNOWMEX ENGINEERS LIMITED
20.72 | 4 C x 10 Sq.mm | 8.00 | Job | 869.00 | 650.00 | 5200.00 | 830.00 | 6640.00 | 5200.00 | SNOWMEX ENGINEERS LIMITED
21.00 | Fabrication work Steel work in M.S. Tubular section /M.S. Square section /M.S. Plates i/c cutting to required length welding | 500.00 | KG | 270.00 | 50.00 | 25000.00 | 158.00 | 79000.00 | 25000.00 | SNOWMEX ENGINEERS LIMITED
22.00 | Dismantling of Duct as per site requirement by necessary Scaffholding and safety arrangement.(Measurement shall be done meters) | 500.00 | Meter | 159.00 | 150.00 | 75000.00 | 830.00 | 415000.00 | 75000.00 | SNOWMEX ENGINEERS LIMITED
23.00 | Supply and fixing of under deck insulation using Expanded Polystyrene EPS Thermocol) Sheet having density 8 kg/m3 to 32 Kg/m3 with minimum thickness of 25 mm. | 100.00 | SqM | 722.00 | 250.00 | 25000.00 | 1494.00 | 149400.00 | 25000.00 | SNOWMEX ENGINEERS LIMITED
24.00 | Supply, Installation, Testing and Commissioning of Inline Exhaust Fan for Toilet area of nominal capacity 500 CFM, Static 20 mmhg | 2.00 | Job | 73653.00 | 12200.00 | 24400.00 | 19924.00 | 39848.00 | 24400.00 | SNOWMEX ENGINEERS LIMITED
25.00 | Supply, installation, testing and commissioning of 8 ft Aircurtain made of stainless steel with minimum air speed of 21 m/s, including provision of supports for installation as per site conditions, interconnections etc complete as required. | 4.00 | Job | 56863.00 | 27500.00 | 110000.00 | 99618.00 | 398472.00 | 110000.00 | SNOWMEX ENGINEERS LIMITED
26.00 | Providing complete HVAC design for the reconfiguring area of the terminal building Dibrugarh Airport, including providing HVAC duct design for the new areas(approximate area 1750 sq.m), providing AHU design for the new areas(approximate area 1750 sq.m), providing pipe line design, providing lAir distrubution system design for the new areas, providing exhaust design for the smoking room and toilets in the new area by providing 3 sets of shop drawings for approval. Basic AutoCad drawing of the buidling shall be provided by AAI. Design shall be done for the climatic conditions of Dibrugarh Airport and set indoor temperture shall be 23+/-1 degree celcuis. The design shall be as per ASHARE standards. | 1.00 | Job | 202000.00 | 55000.00 | 55000.00 | 332060.00 | 332060.00 | 55000.00 | SNOWMEX ENGINEERS LIMITED
27.00 | Dismantling of Floor Mounted AHU of approximate size 8000 cfm with pipelines and accessories at First Floor including provision of blank plates at the end of incoming and outgoing chilled pipeline, provision of blank plates for closing the supply and return air ducts, dismantling the pipeline and duct associated with AHU with shifting of the dismantled materials from the installed location to dismantled store(300 meters) | 1.00 | Job | 40400.00 | 22000.00 | 22000.00 | 73200.00 | 73200.00 | 22000.00 | SNOWMEX ENGINEERS LIMITED
| Total in Figures |  |  |  |  | 4498980.00 |  | 6936554.00
Lowest Amount Quoted BY: SNOWMEX ENGINEERS LIMITED(4498980.00)

## BOQ Summary
BOQ Summary Details Tender Title: Reconfiguration of Existing and Under-Construction Terminal Buildings- Phase-II. SH- Provision of Air Conditioning Tender ID: 2025_AAI_228823_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | SNOWMEX ENGINEERS LIMITED (BID ID -838203) | 4498980.00 | L1
| 2 | Powermech Services Private Limited (BID ID -836254) | 6936554.00 | L2