## BoQ1
Government eProcurement System Created By: JAYAN JAYANTHAN Created Date/Time: 08-Apr-2025 04:31 PM Tender Title: Construction of new DVOR building and allied works at Mysuru Airport. SH- Electrical works Tender ID: 2025_AAI_229211_1
Tender Inviting Authority: Manager (E-E), Airports Authority of India, Mysuru.
Name of Work: Construction of new DVOR building and allied works at Mysuru Airport.SH: Electrical Works.
Contract No: 2025_AAI_229211_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | C P MONCHESTER ELECTRICALS (GSTN-33AJOPP7842E1ZY) BID ID -835376 |  | surbhi association (GSTN-23AGKPD2522N1ZK) BID ID -836175
[5 empty] | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Wiring for light point/ fan point/ exhaust fan point/ call bell point with 1.5 sq.mm FRLSH PVC insulated copper conductor single core cable in surface / recessed steel conduit, with modular switch, modular plate, suitable GI box and earthing the point with 1.5 sq.mm. FRLS PVC insulated copper conductor single core cable etc as required. Group C | 24.00 | EACH | 100.00 | 1020.00 | 24480.00 | 1600.00 | 38400.00 | 24480.00 | C P MONCHESTER ELECTRICALS
2.00 | Wiring for group controlled (looped) light point/fan point/exhaust fan point/ call bell point ( without independent switch etc.) with 1.5 sq. mm FRLSH PVC insulated copper conductor single core cable in surface/ recessed PVC conduit, and earthing the point with 1.5 sq. mm FRLS PVC insulated copper conductor single core cable etc as required. Group C | 6.00 | EACH | 100.00 | 1020.00 | 6120.00 | 1000.00 | 6000.00 | 6000.00 | surbhi association
3.00 | Wiring for light/ power plug with 2X4 sq. mm FRLSH PVC insulated copper conductor single core cable in surface/ recessed steel conduit alongwith 1 No 4 sq. mm FRLSH PVC insulated copper conductor single core cable for loop earthing as required. | 225.00 | METER | 100.00 | 290.00 | 65250.00 | 350.00 | 78750.00 | 65250.00 | C P MONCHESTER ELECTRICALS
4.00 | Wiring for light/ power plug with 4X4 sq. mm FRLSH PVC insulated copper conductor single core cable in surface/ recessed steel conduit alongwith 2 Nos 4 sq. mm FRLSH PVC insulated copper conductor single core cable for loop earthing as required. | 345.00 | METER | 100.00 | 570.00 | 196650.00 | 450.00 | 155250.00 | 155250.00 | surbhi association
5.00 | Supplying and fixing suitable size GI box with modular plate and cover in front on surface or in recess, including providing and fixing 6 pin 5/6 & 15/16 A modular socket outlet and 15/16 A modular switch, connections etc. as required. | 12.00 | EACH | 100.00 | 900.00 | 10800.00 | 450.00 | 5400.00 | 5400.00 | surbhi association
6.00 | Supplying and fixing following size/ modules, GI box alongwith modular base & cover plate for modular switches in recess etc as required. 6 Module (200mmX75mm) | 21.00 | EACH | 100.00 | 550.00 | 11550.00 | 250.00 | 5250.00 | 5250.00 | surbhi association
7.00 | Supplying and fixing following modular switch/ socket on the existing modular plate & switch box including connections but excluding modular plate etc. as required. 15/16 A SWITCH | 42.00 | EACH | 100.00 | 350.00 | 14700.00 | 120.00 | 5040.00 | 5040.00 | surbhi association
8.00 | Supplying and fixing following modular switch/ socket on the existing modular plate & switch box including connections but excluding modular plate etc. as required. 6 pin 15/16 A socket outlet | 42.00 | EACH | 100.00 | 390.00 | 16380.00 | 200.00 | 8400.00 | 8400.00 | surbhi association
9.00 | Supplying and fixing suitable size/ modules weather proof enclosure IP 55 on surface including providing and fixing 6 pin 5/6 & 15/16 amps modular socket outlet and 15/16 amps modular switch, connection etc. as required. | 2.00 | EACH | 100.00 | 2100.00 | 4200.00 | 1000.00 | 2000.00 | 2000.00 | surbhi association
10.00 | Supplying and fixing following way, single pole and neutral, sheet steel, MCB distribution board, 240 V, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing and suitable cable end box etc. as required. (But without MCB/RCCB/Isolator) 12 way , Double door | 5.00 | EACH | 100.00 | 3000.00 | 15000.00 | 2500.00 | 12500.00 | 12500.00 | surbhi association
11.00 | Supplying and fixing following way, single pole and neutral, sheet steel, MCB distribution board, 240 V, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing and suitable cable end box etc. as required. (But without MCB/RCCB/Isolator) 8 way , Double door | 1.00 | EACH | 100.00 | 2700.00 | 2700.00 | 2000.00 | 2000.00 | 2000.00 | surbhi association
12.00 | Supplying and fixing 40 amps rating, 240/415 volts, C curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required. Single Pole and Neutral | 5.00 | EACH | 100.00 | 600.00 | 3000.00 | 550.00 | 2750.00 | 2750.00 | surbhi association
13.00 | Supplying and fixing 5 amps to 32 amps rating, 240/415 volts, C curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required. Single pole and Neutral | 1.00 | EACH | 100.00 | 600.00 | 600.00 | 500.00 | 500.00 | 500.00 | surbhi association
14.00 | Supplying and fixing 5 amps to 32 amps rating, 240/415 volts, C curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required. Single pole | 36.00 | EACH | 100.00 | 240.00 | 8640.00 | 150.00 | 5400.00 | 5400.00 | surbhi association
15.00 | Supplying and fixing single pole blanking plate in the existing MCB DB complete etc. as required. | 20.00 | EACH | 100.00 | 45.00 | 900.00 | 20.00 | 400.00 | 400.00 | surbhi association
16.00 | Supplying and fixing following size/ modules, GI box alongwith modular base & cover plate for modular switches in recess etc as required. 1 or 2 Module (75mmX75mm) | 3.00 | EACH | 100.00 | 300.00 | 900.00 | 120.00 | 360.00 | 360.00 | surbhi association
17.00 | Supplying and fixing following modular switch/ socket on the existing modular plate & switch box including connections but excluding modular plate etc. as required. Telephone socket outlet RJ 11 | 3.00 | EACH | 100.00 | 450.00 | 1350.00 | 150.00 | 450.00 | 450.00 | surbhi association
18.00 | Supply of 1200 mm sweep BLDC Ceiling fan, 5 star rated with double ball bearing , standard down rod and other standard accessories without regulator as required. | 3.00 | EACH | 100.00 | 3600.00 | 10800.00 | 2560.00 | 7680.00 | 7680.00 | surbhi association
19.00 | Supplying and fixing two module stepped type electronic fan regulator on the existing modular plate switch box including connections but excluding modular plate etc. as required. | 3.00 | EACH | 100.00 | 600.00 | 1800.00 | 300.00 | 900.00 | 900.00 | surbhi association
20.00 | Supply of 300 mm dia single phase 900 RPM heavy duty Exhaust fan including all accessories etc as required. | 2.00 | EACH | 100.00 | 3000.00 | 6000.00 | 3200.00 | 6400.00 | 6000.00 | C P MONCHESTER ELECTRICALS
21.00 | Supply of 20 W surface mounted extruded aluminium LED batten (4 feet) with opal diffuser along with all acessories like heat sink, constant current output driver, reflector, cover etc. complete suitable for operating at 230 V,50 Hz, single phase AC supply as per specifications. Model BAJAJ BCLAB 20 W LED PS or equivalent as per approved make list | 14.00 | EACH | 100.00 | 900.00 | 12600.00 | 1000.00 | 14000.00 | 12600.00 | C P MONCHESTER ELECTRICALS
22.00 | Supply of 20 W recess mounted extruded aluminium linear LED luminaire (1200 mm length) with flushed diffuser along with all acessories like heat sink, constant current output driver, reflector, cover etc. complete suitable for operating at 230 V,50 Hz, single phase AC supply as per specifications. Model BAJAJ BRCS 20W LED WH 4F or equivalent as per approved make list | 5.00 | EACH | 100.00 | 900.00 | 4500.00 | 1200.00 | 6000.00 | 4500.00 | C P MONCHESTER ELECTRICALS
23.00 | Supply of Integral 45 Watts LED Street Light Luminaire with pressure die cast aluminium housing with IP 66 protection along with all acessories like heat sink, constant current output driver, reflector, glass cover etc. complete suitable for operating at 230 V,50 Hz, single phase AC supply as per specifications. | 6.00 | EACH | 100.00 | 2100.00 | 12600.00 | 2000.00 | 12000.00 | 12000.00 | surbhi association
24.00 | Supply of rechargeable LED Emergency light with minimum 12 W output, with brightness control, battery rating minimum 3000 mAH. | 3.00 | EACH | 100.00 | 3000.00 | 9000.00 | 1500.00 | 4500.00 | 4500.00 | surbhi association
25.00 | Installation, testing and commissioning of ceiling fan, including wiring the down rods of standard length (upto 30 cm) with 1.5 sq. mm FRLSH PVC insulated, copper conductor, single core cable etc. as required. | 3.00 | EACH | 100.00 | 210.00 | 630.00 | 120.00 | 360.00 | 360.00 | surbhi association
26.00 | Installation of exhaust fan in the existing opening, including making good the damage, connection, testing, commissioning etc. as required. | 2.00 | EACH | 100.00 | 300.00 | 600.00 | 150.00 | 300.00 | 300.00 | surbhi association
27.00 | Installation, testing and commissioning of pre-wired, LED fitting of all types, complete with all accessories directly on ceiling/ wall, including connections with 1.5 sq. mm FRLSH PVC insulated, copper conductor, single core cable and earthing etc. as required. | 14.00 | EACH | 100.00 | 150.00 | 2100.00 | 120.00 | 1680.00 | 1680.00 | surbhi association
28.00 | Installation, testing and commissioning of pre-wired, LED fitting of all types, complete with all accessories on false ceiling, including connections with 1.5 sq. mm FRLSH PVC insulated, copper conductor, single core cable and earthing etc. as required. | 5.00 | EACH | 100.00 | 210.00 | 1050.00 | 120.00 | 600.00 | 600.00 | surbhi association
29.00 | ITC of Street Light Luminaire on wall with suitable Medium class GI pipe bent to shape including wiring the pipe,making connections etc.complete as required. | 6.00 | EACH | 100.00 | 2100.00 | 12600.00 | 650.00 | 3900.00 | 3900.00 | surbhi association
30.00 | Supplying and fixing One number Daily/Weekly programmable time switch with digital display, nominal switching current of 16 A, with 1 NO contact, power reserve for minimum 3 years and One number 3 pole contactor with 22 amps rating (AC3) suitable for 230 V, 50 HZ AC Supply in suitable metal enclosure including providing connections testing and commissioning etc. as required. | 5.00 | EACH | 100.00 | 3000.00 | 15000.00 | 5000.00 | 25000.00 | 15000.00 | C P MONCHESTER ELECTRICALS
31.00 | Supplying and fixing 32 amps, 415 volts, TPN industrial type, socket outlet, with 3 Pole + Neutral + earth, metal enclosed plug top alongwith 32 amps "C" curve, TPN MCB, in sheet steel enclosure, on surface or in recess, with chained metal cover for the socket out let and complete with connections, testing and commissioning etc. as required. | 2.00 | EACH | 100.00 | 7200.00 | 14400.00 | 4500.00 | 9000.00 | 9000.00 | surbhi association
32.00 | Supply of XLPE insulated, PVC inner sheathed, armoured copper conductor power cable of 1.1 KV grade conforming to IS-7098 Part 1(1988) amended up to date. 3 X 6 sq mm | 300.00 | METER | 100.00 | 410.00 | 123000.00 | 400.00 | 120000.00 | 120000.00 | surbhi association
33.00 | Supplying and laying of following size HDPE pipe of PE 80, grade PN 8 pressure rating ISI marked along with all accessories like socket, bend, couplers etc. conforming to IS 4984 -2016 complete with fitting and cutting, jointing etc.direct in ground (75 cm below ground level) including excavation and refilling the trench but excluding sand cushioning and protective covering etc. , omplete as required. 50 mm OD | 100.00 | METER | 100.00 | 270.00 | 27000.00 | 220.00 | 22000.00 | 22000.00 | surbhi association
34.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/ HUME/ METAL pipe as required. Upto 35 sq. mm | 100.00 | METER | 100.00 | 30.00 | 3000.00 | 25.00 | 2500.00 | 2500.00 | surbhi association
35.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on wall surface/cable tray etc. as required Upto 35 sq. mm (clamped with 1mm thick saddle) | 160.00 | METER | 100.00 | 120.00 | 19200.00 | 25.00 | 4000.00 | 4000.00 | surbhi association
36.00 | Supplying and making end termination with brass compression gland and copper lugs for following size of PVC insulated and PVC sheathed / XLPE copper conductor cable of 1.1 KV grade as required. 3 core x 6 sq. mm | 15.00 | SET | 100.00 | 900.00 | 13500.00 | 200.00 | 3000.00 | 3000.00 | surbhi association
37.00 | Earthing with copper Earth plate 600mm x 600mm x 3mm thick including accessories and providing masonary enclosure with cover plate having locking arrangement and watering pipe of 2.7 meter long etc. with charcoal/ coke and salt as required. | 2.00 | SET | 100.00 | 18000.00 | 36000.00 | 18500.00 | 37000.00 | 36000.00 | C P MONCHESTER ELECTRICALS
38.00 | Providing and fixing 25 mm X 5 mm copper strip in 40 mm dia G.I. pipe from earth electrode including connection with brass nut, bolt, spring, washer excavation and refilling etc. as required. | 20.00 | METER | 100.00 | 2100.00 | 42000.00 | 1400.00 | 28000.00 | 28000.00 | surbhi association
39.00 | Providing and fixing 25 mm X 5 mm copper strip on surface or in recess for connections etc. as required. | 20.00 | METER | 100.00 | 1450.00 | 29000.00 | 1100.00 | 22000.00 | 22000.00 | surbhi association
40.00 | Jointing copper / G.I. tape (with another copper/ G I tape, base of the finial or any other metallic object) by riveting / nut bolting/ sweating and soldering etc as required. (Brazing of Copper Earth Strip Joints) | 210.00 | EACH | 100.00 | 120.00 | 25200.00 | 200.00 | 42000.00 | 25200.00 | C P MONCHESTER ELECTRICALS
41.00 | Supply, Installation, Testing and Commissioning of Indoor LT electric panel, floor mounted, cubicle type, made out of CRCA sheet not less than 2.0 mm thick for load bearing members and 1.6 mm for doors of LT panels totally enclosed, IP 54, protection, dust and vermin proof , compartmentalised with powder coated painting suitable for operation on 3 Phase and neutral, 415V, 50 Hz AC supply system with 200 A copper busbar,din bar, copper earth bar, removeable gland plates of 3 mm thick, interconnections etc. complete as required and consisting of:- | 1.00 | EACH | 100.00 | 375000.00 | 375000.00 | 245000.00 | 245000.00 | 245000.00 | surbhi association
41.01 | INCOMER 1. 160 A Four Pole MCCB with 36 KA short circuit rating with Thermal and Magnetic Trip Unit including Phase Barriers, Spreader Terminals, Extended Rotary Handle - 2 Nos (ATS Incomer side) 2. 160 A 4 Pole Automatic Transfer Switch -1 No. 3. HRC Fuse Unit 160A - 1 SET (3 Phase) 4. 160 A Four Pole MCCB with 36 KA short circuit rating with Thermal and Magnetic Trip Unit including Phase Barriers, Spreader Terminals, Extended Rotary Handle - 1 Nos. (ATS Outgoing side) 5. LED Multi Function Meter Class 0.5 with provision to monitor V, A, F, PF, kW, kVA, kVAR, kWh, kVAh, kVARh,Runhours, On hours, Phase angle, Interrupts, THD with RS 485 Port with built in Selector Swithes including suitable resin cast CT s.-1 No. 6. RYB Phase Indicators LED Type with control MCB s -1 Set
41.02 | Provision for installaiton of three phase and neutral (4 Module) Surge Protection Device (DIN rail mounted) shall be provided (COST OF SPD NOT TO BE INCLUDED)
41.03 | OUTGOINGS 1. RCBO 63 A DP, 100 mA - 3 Nos. (1 No. per Phase) 2. 40 A DP MCB C Series -12 Nos.(4 Nos. per Phase) 3. 20 A DP MCB C Series - 6 Nos. (2 Nos. per Phase) 4. 63 A , 4 Pole, MCCB, 18 KA short circuit rating with Thermal and Magnetic Trip Unit including Phase Barriers, Spreader Terminals, Extended Rotary Handle with Provision for installaiton of three phase and neutral (4 Module) Surge Protection Device (DIN rail mounted) - 2 Nos. (COST OF SPD NOT TO BE INCLUDED) 5. 40 A, TPN MCB C Series- 1 NO. 6. 32 A, TPN MCB C Series - 4 NOS. 7. 32 A DP RCBO 100 mA - 1 NO 8. 20 A DP MCB C Series -1 NO.
42.00 | Supply, Installation, Testing and Commissioning of Surge Protection Device (SPD) Class B/Type1 for power line protection as per IEC 61643 -1, Three Numbers of Encapsulated, non-extinguishing spark gap arrester with nominal voltage 230 V, 50 Hz, Lightning current arresting capacity to 50 kA (10/350) per pole and up to 150 kA (10/350) in total, with function display (between LINE and NEUTRAL) and one number of combination arrestor with arresting capacity 125 kA (10/350 µs) (between NEUTRAL to PROTECTIVE EARTH), Response time shall be less than 100 nano sec. Voltage protection level < 1.5 kV in the existing panel complete with connections, testing and commissioning etc. as required. | 3.00 | EACH | 100.00 | 20000.00 | 60000.00 | 50000.00 | 150000.00 | 60000.00 | C P MONCHESTER ELECTRICALS
43.00 | Supply and fixing ISI certified, 2 mm thick, 3.3 KV Grade Electrical insulating mat conforming to IS 15652/2006 with dielectric strength 30 KV as required. | 2.00 | Sq M | 100.00 | 9000.00 | 18000.00 | 1000.00 | 2000.00 | 2000.00 | surbhi association
44.00 | Supply of aluminium conductor XLPE insulated, PVC inner sheathed, armoured power cable of 1.1 KV grade conforming to IS-7098 Part 1(1988) amended up to date. 3.5 X 185 sq mm | 1100.00 | METER | 100.00 | 990.00 | 1089000.00 | 1050.00 | 1155000.00 | 1089000.00 | C P MONCHESTER ELECTRICALS
45.00 | Supplying and laying of following size DWC HDPE pipe ISI marked along with all accessories like socket, bend, couplers etc. conforming to IS 14930, Part II complete with fitting and cutting, jointing etc.direct in ground (75 cm below ground level) including excavation and refilling the trench but excluding sand cushioning and protective covering etc. , complete as required. 90 mm dia (OD-90 mm & ID-76 mm nominal) | 1100.00 | METER | 100.00 | 210.00 | 231000.00 | 250.00 | 275000.00 | 231000.00 | C P MONCHESTER ELECTRICALS
46.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/ HUME/ METAL pipe as required. Above 95 sq. mm and upto 185 sq. mm | 1100.00 | METER | 100.00 | 90.00 | 99000.00 | 40.00 | 44000.00 | 44000.00 | surbhi association
47.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. 3½ X 185 sq. mm (57mm) | 4.00 | METER | 100.00 | 3000.00 | 12000.00 | 1200.00 | 4800.00 | 4800.00 | surbhi association
48.00 | Supplying and making straight through joint with heat shrinkable kit including ferrules and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. 3½ X 185 sq. mm | 4.00 | SET | 100.00 | 14000.00 | 56000.00 | 4500.00 | 18000.00 | 18000.00 | surbhi association
49.00 | Supply and laying 100 mm size B class GI pipe in ground in the existing trench as required (across road crossings) | 24.00 | METER | 100.00 | 1200.00 | 28800.00 | 1200.00 | 28800.00 | 28800.00 | C P MONCHESTER ELECTRICALS, surbhi association
50.00 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering - All work up to plinth level : 1:2:4 (1 cement : 2 coarse sand (zone-III) derived from natural sources : 4 graded stone aggregate 20 mm nominal size derived from natural sources) | 5.00 | CUM | 100.00 | 9000.00 | 45000.00 | 6500.00 | 32500.00 | 32500.00 | surbhi association
51.00 | Supplying and making cable route marker with cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size ) of size 60 cm X 60 cm at the bottom and 50 cm X 50 cm at the top with a thickness of 10cm including inscription duly engraved as required. | 20.00 | EACH | 100.00 | 900.00 | 18000.00 | 500.00 | 10000.00 | 10000.00 | surbhi association
52.00 | Supply of 2 HP (1.5 KW) Three Phaase Open Well Submersible Pump suitable to operate at 415 V, 3 Phase, 50 Hz supply, discharge 1.7 LPS at a Head of 30 Meter, 40 mm discharge pipe size. Kirloskar KOS-235M or equivalent | 1.00 | EACH | 100.00 | 30000.00 | 30000.00 | 15000.00 | 15000.00 | 15000.00 | surbhi association
53.00 | Supply, installation, testing and commissioning of DOL Starter sutiable for 2 HP 3 Phase Openwell Submersible Pump and suitable to operate at 415 V, 3 Ph, 50 Hz AC supply consisting of Voltmeter, Ammeter, overload relay 2.4-3.8 A, Contacor with rating 16 A etc. as required | 1.00 | EACH | 100.00 | 7200.00 | 7200.00 | 9500.00 | 9500.00 | 7200.00 | C P MONCHESTER ELECTRICALS
54.00 | Supply of 3 Core 2.5 sq.mm PVC Insulated & PVC Sheathed Industrial Cable for Submersible Pump Motors 1100 Volt, conforming to IS 694 | 50.00 | METER | 100.00 | 210.00 | 10500.00 | 150.00 | 7500.00 | 7500.00 | surbhi association
55.00 | Supply of 40 mm Dia HDPE pipe of PE 80 grade PN 8 pressure rating conforming to IS 4984 -2016 . | 50.00 | METER | 100.00 | 300.00 | 15000.00 | 150.00 | 7500.00 | 7500.00 | surbhi association
56.00 | Installation, testing and commissioning of Openwell Submersible Pump in the existing sump, complete with acessories such as Nylon rope, clamps, Delivery pipe line connections, Electrical Cable Connections etc. as required. | 1.00 | JOB | 100.00 | 21000.00 | 21000.00 | 1500.00 | 1500.00 | 1500.00 | surbhi association
57.00 | Supply, Installation, Testing and Commissioning of 3.0 TR (nominal capacity) Ductable Inverter Air conditioners Comprising of Fan Coil Units, Out Door unit comprising of Compressor, Cooling fan, Copper Condensing Coil with eco-friendly refrigerant suitable for operation on 415 V +/- 10% , 50 HZ, 3 Ph. AC supply including installation of Fan Coil Unit (Indoor Unit) and Out Door Unit, Copper Pipe (suction and discharge) connections between ID and OD unit , Electrical Connections, drain water piping including all accessories and first charge of refrigerant etc. complete as required | 2.00 | EACH | 100.00 | 120000.00 | 240000.00 | 125000.00 | 250000.00 | 240000.00 | C P MONCHESTER ELECTRICALS
58.00 | Supply & Installation of 4core Communication cable from IDU To ODU as per OEM Specifications. | 12.00 | METER | 100.00 | 300.00 | 3600.00 | 150.00 | 1800.00 | 1800.00 | surbhi association
59.00 | Supply & Installation of Copper Pipe wih 10mm Rubber Nitrile insulation & fittings as per OEM Specifications. | 12.00 | METER | 100.00 | 900.00 | 10800.00 | 2250.00 | 27000.00 | 10800.00 | C P MONCHESTER ELECTRICALS
60.00 | Supply & Installation of Alluminum Powder coated Linear Grill as per OEM Specifications | 1.00 | SQ.M | 100.00 | 21000.00 | 21000.00 | 12000.00 | 12000.00 | 12000.00 | surbhi association
61.00 | Supply & Installation of Outdoor Stand as per OEM Specifications | 2.00 | EACH | 100.00 | 4500.00 | 9000.00 | 2500.00 | 5000.00 | 5000.00 | surbhi association
62.00 | Supply & Installation of GI Type Ducting mouth piece with rubber nitrile insulation & canvas connection as per OEM Specifications. | 2.00 | EACH | 100.00 | 12000.00 | 24000.00 | 10000.00 | 20000.00 | 20000.00 | surbhi association
63.00 | Supply & Installation of Fire Damper for Return Air as per OEM Specifications | 1.00 | SQ.M | 100.00 | 21000.00 | 21000.00 | 15000.00 | 15000.00 | 15000.00 | surbhi association
64.00 | Supply & Installation of Liquid Foam filler as per OEM Specifications | 2.00 | EACH | 100.00 | 7200.00 | 14400.00 | 10000.00 | 20000.00 | 14400.00 | C P MONCHESTER ELECTRICALS
65.00 | Supply and Installation of Thermal Insulated Box for housing the fan coil units (indoor) of ductable split air conditioner unit of 3 Ton capacity, of size as per Manufacturer's recommendations, made out of 1.25 mm thick (18G) GI sheet internally insulated with 25 mm thick Nitrile Rubber, Frame made out of 25 mm x 25 mm x 5 mm angle iron, epoxy painted having suitable door opening with frame for the maintenance of Fan Coil Units complete with neoprene rubber gaskets, hangers, MS angle/channel supports etc. The box shall have suitable arrangement for the protection from rain water ingression. Suitable opening at the bottom shall be provided for the entry of refrigerant pipes, drain pipes and cables. All the openings/joints shall be properly sealed with sealants to prevent entry of external air after completion of installation. | 2.00 | EACH | 100.00 | 45000.00 | 90000.00 | 75000.00 | 150000.00 | 90000.00 | C P MONCHESTER ELECTRICALS
66.00 | Supply, Installation, Testing and Commissioning of 1.5 TR (nominal capacity), High wall mounted, Inverter Split type Air-conditioner with BEE star rating 5, consisting of non-ductable type indoor units (fan coil) with cord less remote control and one number out door unit comprising of compressor, cooling fan, copper condensing coil suitable for operation on single phase, 230 +/- 10% volts, 50 HZ, AC supply including installing the indoor (fan coil) unit and outdoor unit on wall on suitable stand, providing and fixing insulated copper piping (suction and discharge) and electrical connections with flexible copper cable of suitable size as per manufacturer's recommendations, between the indoor and outdoor units up to a length of 3 (three) meters, wrapping the insulated refrigerant line with white wrapping tape, providing drain piping (up to 3 meter length), drilling the hole on wall, making good the opening after installation including first charge of refrigerant etc. complete as required | 5.00 | EACH | 100.00 | 51000.00 | 255000.00 | 45500.00 | 227500.00 | 227500.00 | surbhi association
67.00 | Supply, Installaiton, Testing and Commissioning of Voltage stabilizer with initial time delay, high and low voltage cut off suitable for 1.5 TR Inverter type split AC units | 5.00 | EACH | 100.00 | 3000.00 | 15000.00 | 3000.00 | 15000.00 | 15000.00 | C P MONCHESTER ELECTRICALS, surbhi association
68.00 | Supply, Installation, Testing and Commissioning of 80 litre capacity, seamless, high pressure, cylinder assembly, conforming to IS - 7285 (PT-2): 2004 or UL - 2166 etc. complete as required including valve, bracket assembly, pressure guage and 2 inch flexible discharge hose etc. complete as required. (FOR EQUIPMENT ROOM) | 1.00 | EACH | 100.00 | 90000.00 | 90000.00 | 125000.00 | 125000.00 | 90000.00 | C P MONCHESTER ELECTRICALS
69.00 | Supply, Installation, Testing and Commissioning of 34 litre capacity, seamless, high pressure, cylinder assembly, conforming to IS - 7285 (PT-2): 2004 or UL - 2166 etc. complete as required including valve, bracket assembly and 2 inch flexible discharge hose etc. complete as required. (FOR ELECTRICAL ROOM & UPS ROOM) | 2.00 | EACH | 100.00 | 45000.00 | 90000.00 | 109500.00 | 219000.00 | 90000.00 | C P MONCHESTER ELECTRICALS
70.00 | Supply and filling of clean, odourless, colour less, UL listed and suitable for fire class - A, B & C fire suppression agent (FK-5-1-12 Clean Agent) etc. complete as required. | 88.00 | KG | 100.00 | 2100.00 | 184800.00 | 3150.00 | 277200.00 | 184800.00 | C P MONCHESTER ELECTRICALS
71.00 | Supply, Installation, Testing and Commissioning of 24 V DC, Electric Actuator and Local /manual pneumatic actuator for triggering the cylinder assembly etc. complete as required. | 3.00 | EACH | 100.00 | 7200.00 | 21600.00 | 85000.00 | 255000.00 | 21600.00 | C P MONCHESTER ELECTRICALS
72.00 | Supplying, installation, testing and commissioning of Low pressure switch for the cylinder assembly etc. complete as required. | 3.00 | EACH | 100.00 | 4500.00 | 13500.00 | 19500.00 | 58500.00 | 13500.00 | C P MONCHESTER ELECTRICALS
73.00 | Supplying, installation, testing and commissioning of Manual Gas Release Station etc. complete as required. | 3.00 | EACH | 100.00 | 21000.00 | 63000.00 | 4500.00 | 13500.00 | 13500.00 | surbhi association
74.00 | Supplying, installation, testing and commissioning of Manual Gas Abort Station etc. complete as required. | 3.00 | EACH | 100.00 | 21000.00 | 63000.00 | 4500.00 | 13500.00 | 13500.00 | surbhi association
75.00 | Supllying and fixing of suitable size ( as per hydraulic flow calculation ) nozzle with orfices etc. complete as required. | 6.00 | EACH | 100.00 | 7200.00 | 43200.00 | 8750.00 | 52500.00 | 43200.00 | C P MONCHESTER ELECTRICALS
76.00 | Supply and laying of MS pipe (M.S. Seamless To ASTM A-106, SCH. 40) red painted with all fittings & supports, etc. on surface/ recess/ above false ceiling/ concealed space/ wall concealed complete as required as per site requirement. (Note: Lot comprises of required length of suitable size MS pipe and associated pipe accessories like Bend, Tee, Elbow & Coupling etc. for each location) | 3.00 | JOB | 100.00 | 45000.00 | 135000.00 | 75000.00 | 225000.00 | 135000.00 | C P MONCHESTER ELECTRICALS
77.00 | Supply, Installation, Testing & Commissioning of UL / EN listed (latest version) Modular Microprocessor based expandable intelligent Addressable Type Fire Alarm Control Panel of Two loops, with minimum 80-character graphics / LCD display with touch screen or other keypad and minimum 800 events history log in the non-volatile memory (EPROM), The panel should be equipped with loop capacity to take minimum 240 intelligent addressable detectors/ devices (In any combination) in one loop. Four access levels, capable of taking Protocol Devices, Graphical Display, sufficient numbers of programmable relay controls for controlling ventilation fan, fire pump room, monitoring of fire sprinkler and fire hydrant pump, 230 volts, 50 Hz AC power supply, automatic battery charger, 24 volts sealed maintenance free lead acid batteries sufficient for 2 hours normal working and then be capable of operating the system for 30 minutes during an emergency / fault conditions along with battery stand as required. The panel shall have facility for seamless integration with PA system (For Giving triger Signal to Start Pre-recorded Digital Voice Evacuation from PA system in case of fire). The panel shall be compatible for Building Management System with open protocol BACNET / MODBUS etc. as per specification, complete as required. (HONEYWELL NOTIFIER NFS 2-640 intelligent Fire Alarm Control Panel or equivalent as per Approved make) The panel shall be capable of activating Gas Releasing Control Module on activation of Smoke+ Heat detectors for operating the Gas based Fire Suppression System. | 1.00 | EACH | 100.00 | 300000.00 | 300000.00 | 300000.00 | 300000.00 | 300000.00 | C P MONCHESTER ELECTRICALS, surbhi association
78.00 | Supply, installation, testing and commissioning of UL listed (latest version), FM Approved Intelligent Addressable Gas Releasing Control Module/ Relay Module (output module) specifically designed for fire suppression releasing applications with suitable surface mounting modular box complete with termination etc. complete as required and as per enclosed specifications. (HONEYWELL NOTIFIER FCM-1-REL Releasing Control Module or equivalent as per Approved make) | 3.00 | EACH | 100.00 | 45000.00 | 135000.00 | 5000.00 | 15000.00 | 15000.00 | surbhi association
79.00 | Supply, installation, testing and commissioning of UL / EN listed (latest version) Intelligent addressable Control Module/ Relay Module (output module) with inbuilt fault isolator / isolator module for tripping of AHU & Ventilation / pressurisation fans / hooter complete with termination etc. complete as required and as per enclosed specifications. (For fire damper of Ductable split AC Units) | 2.00 | EACH | 100.00 | 45000.00 | 90000.00 | 5000.00 | 10000.00 | 10000.00 | surbhi association
80.00 | Supply, Installation, Testing & commissioning of UL / EN listed (latest version) intelligent addressable multi criteria detector {Smoke + heat } with inbuilt fault isolator / isolator base and with unique optical sensing chamber, visible LED, fully coated circuit board, superior RF / Transient protection suitable for 2 wires loop connection, complete with plug into common separate base & housing constructed of LEXAN (or polycarbonate) complete with connections etc. as required and to be installed below / above false ceiling roof and concealed space and as per enclosed specifications ,complete as required. (Cost of plug in common base shall deemed to be included in cost of detectors) | 6.00 | EACH | 100.00 | 21000.00 | 126000.00 | 3000.00 | 18000.00 | 18000.00 | surbhi association
81.00 | Supply, installation, testing and commissioning of UL / EN listed (Latest Version) Response Indicators for getting fire indications of detectors i/c mounting boxes installed above false ceiling area interconnecting to loop cable etc. as per specification complete as required. | 2.00 | EACH | 100.00 | 1800.00 | 3600.00 | 850.00 | 1700.00 | 1700.00 | surbhi association
82.00 | Supply, Installation, Testing & commissioning of UL / EN listed (latest version) intelligent addressable Manual call station (Resetable pull / push type) suitable for semi flush mounting, IP 54 for indoor use & IP 65 for outdoor use with inbuilt fault isolator / isolator module with double gang outlet box, equipment for key operated test-reset lock, electronic or rotary switches for address setting. Manual pull station shall be connected with two wire to SLC loop of Fire Control Panel. Cover shall be made out of LEXAN (or poly carbonate equivalent) with clear operating instruction and the word Fire appearing on the front complete with connections etc. as required and as per enclosed specifications. | 1.00 | EACH | 100.00 | 3600.00 | 3600.00 | 1500.00 | 1500.00 | 1500.00 | surbhi association
83.00 | Supply, installation, testing and commissioning of UL / EN listed (latest version) loop powered addressable Hooter-cum- strobe with inbuilt fault isolator / isolator module with adjustable sound level in the range of min. 90 db to Max. 120 db at 1M distance complete with termination etc. as required and as per enclosed specification. | 1.00 | EACH | 100.00 | 7200.00 | 7200.00 | 6500.00 | 6500.00 | 6500.00 | surbhi association
84.00 | Supply, installation, testing and commissioning of conventional Fire Alarm control panel having minimum of 2 zones suitable for connecting sensors, manual call points, Hooters and Response indicators operation on 230 Volts, 50 Hz power supply, LCD display to indicate fire and normal operation & power supply status, push button for accept and Reset, sealed leadacid batteries with minimum 24V DC backup on alarm mode & normal operation mode with battery charger etc., shall be complete as required. Panel shall have necessary provision for connecting and functioning with auto dialer etc as required. (Make: As per AAI approved makes list) | 1.00 | EACH | 100.00 | 30000.00 | 30000.00 | 25000.00 | 25000.00 | 25000.00 | surbhi association
85.00 | Supply & fixing of conventional type Photoelectric, Multi sensor smoke detectors along with mounting base with unique optical sensing chamber, visible LED's fully coated circuit boards with RF/transient protection, complete with all accessories including connections etc. as required. (As per approved makes list) | 4.00 | EACH | 100.00 | 3000.00 | 12000.00 | 2200.00 | 8800.00 | 8800.00 | surbhi association
86.00 | Supplying, installation, testing & commissioning of heat detector operating at 54ºC/57ºC with rate of rise cum fixed tempreature (dual thermistor) type with mounting base complete with all connection etc. as required. | 1.00 | EACH | 100.00 | 3600.00 | 3600.00 | 2500.00 | 2500.00 | 2500.00 | surbhi association
87.00 | Supplying, installation, testing & commissioning of manual call box of ABS type in surface/recess with stainless steel chain & hammer assembly complete with glass and push button etc. as required. | 1.00 | EACH | 100.00 | 4100.00 | 4100.00 | 500.00 | 500.00 | 500.00 | surbhi association
88.00 | Supplying, installation, testing & commissioning fire alarm sounder with facility to make announcement, mounted in A.B.S. box with hinged cover plate & suitable for operation with amplifier i/c line matching transformer etc. complete as required. | 1.00 | EACH | 100.00 | 3000.00 | 3000.00 | 5000.00 | 5000.00 | 3000.00 | C P MONCHESTER ELECTRICALS
89.00 | Supplying, installation, testing & commissioning of Auto dialer fault alert system for call and SMS alert with provision for configuring 20 user mobile numbers complete as required. | 1.00 | EACH | 100.00 | 7200.00 | 7200.00 | 9500.00 | 9500.00 | 7200.00 | C P MONCHESTER ELECTRICALS
90.00 | Supplying & laying of 2x1.5 sqmm fire alarm armoured cable, 600/1000V rated with annealed copper conductor having XLPE insulation, steel wire armouring & FRLS outer sheath complete as required. 2 x 1.5 sq. mm | 200.00 | METER | 100.00 | 270.00 | 54000.00 | 120.00 | 24000.00 | 24000.00 | surbhi association
91.00 | Supply of copper plate 600 mm x 600 mm x 3.15 mm thickness with purity of copper not less than 90% (For earthing) | 17.00 | EACH | 100.00 | 9600.00 | 163200.00 | 14000.00 | 238000.00 | 163200.00 | C P MONCHESTER ELECTRICALS
92.00 | Supply of 25 mm x 3 mm thick copper strip with purity of copper not less than 90% (Earth stips) | 1000.00 | METER | 100.00 | 570.00 | 570000.00 | 950.00 | 950000.00 | 570000.00 | C P MONCHESTER ELECTRICALS
93.00 | Supply of 4 mm dia non-stranded bare copper wire with purity of copper not less than 90% (Earth wire) | 400.00 | METER | 100.00 | 180.00 | 72000.00 | 200.00 | 80000.00 | 72000.00 | C P MONCHESTER ELECTRICALS
94.00 | Supply of 1 inch dia 5 feet long solid copper rod with purit of copper not less than 90% | 10.00 | EACH | 100.00 | 3600.00 | 36000.00 | 5000.00 | 50000.00 | 36000.00 | C P MONCHESTER ELECTRICALS
95.00 | Supply of FR PVC insulated copper conductor cable of of 70sqmm cross section conforming to IS 694:2010 amended up to date. | 200.00 | METER | 100.00 | 720.00 | 144000.00 | 950.00 | 190000.00 | 144000.00 | C P MONCHESTER ELECTRICALS
96.00 | Supply of 2 inch x 30 feet ( 50 mm x 9 meter) B class GI pipe with Socket and reducer (2inch-1inch) | 4.00 | EACH | 100.00 | 9600.00 | 38400.00 | 5400.00 | 21600.00 | 21600.00 | surbhi association
97.00 | Supply of 4-inch x 10 feet (100 mm x3 meter) B class GI pipe with Suitable GI base plate of 300 mm x 300 mm x 6 mm thick to mount 4- inch GI Pipe | 4.00 | EACH | 100.00 | 3600.00 | 14400.00 | 5000.00 | 20000.00 | 14400.00 | C P MONCHESTER ELECTRICALS
98.00 | Supply of 40 mm dia, 10 feet (3 Meter) length B class Perforated GI Earthing Pipe | 17.00 | EACH | 100.00 | 1700.00 | 28900.00 | 3000.00 | 51000.00 | 28900.00 | C P MONCHESTER ELECTRICALS
99.00 | Supply of 2-inch x 20 feet (50 mm x 6 Meter) UV Resistant UPVC PIPE | 50.00 | EACH | 100.00 | 1400.00 | 70000.00 | 500.00 | 25000.00 | 25000.00 | surbhi association
100.00 | Supply of DWC HDPE PIPE of size 110 mm (Outer Dia) conforming to IS 16205: PART 24: 2017 including couplers are required. | 20.00 | METER | 100.00 | 360.00 | 7200.00 | 200.00 | 4000.00 | 4000.00 | surbhi association
101.00 | Supply of salt granular (for earth pits) | 4250.00 | KG | 100.00 | 10.00 | 42500.00 | 10.00 | 42500.00 | 42500.00 | C P MONCHESTER ELECTRICALS, surbhi association
102.00 | Supply of Charcoal granular (for earth pits) | 4250.00 | KG | 100.00 | 45.00 | 191250.00 | 20.00 | 85000.00 | 85000.00 | surbhi association
103.00 | Supply of 6” x 10 feet x 18 gauge (150 mm x 3 Meter x 1.2 mm thickness) GI Raceway with L and T junction | 4.00 | EACH | 100.00 | 7200.00 | 28800.00 | 2000.00 | 8000.00 | 8000.00 | surbhi association
104.00 | Supply of 3 Meter Length MS perforated cable tray Hot Dip Galvanized 150 mm x 50 mm x 1.6 mm with L and T Junction | 4.00 | EACH | 100.00 | 7200.00 | 28800.00 | 850.00 | 3400.00 | 3400.00 | surbhi association
105.00 | Supply of PVC extension board having 4 (four) numbers of 6 pin 15/16 amps modular socket outlet (2 Module) with 4 (four) numbers of 16 A Switch (1 Module), extension cord of 3 x 1.5 sq.mm PVC sheathed armoured copper conductor cable of 30 metr length. | 2.00 | EACH | 100.00 | 7200.00 | 14400.00 | 3500.00 | 7000.00 | 7000.00 | surbhi association
106.00 | Supply of heavy duty two fold self supporting aluminium ladder extendable to 20 feet height. | 1.00 | EACH | 100.00 | 27000.00 | 27000.00 | 75000.00 | 75000.00 | 27000.00 | C P MONCHESTER ELECTRICALS
107.00 | Supply of heavy duty self supporting aluminium ladder 7 ft height with anti slip shoes | 1.00 | EACH | 100.00 | 8684.00 | 8684.00 | 14000.00 | 14000.00 | 8684.00 | C P MONCHESTER ELECTRICALS
108.00 | Supply of DWC HDPE PIPE of size 63 mm (Outer Dia) conforming to IS 16205: PART 24: 2017 including couplers are required. | 90.00 | METER | 100.00 | 120.00 | 10800.00 | 100.00 | 9000.00 | 9000.00 | surbhi association
109.00 | Supply of 1.5-inch (40 mm) size Heavy Duty PVC Hose pipe | 100.00 | METER | 100.00 | 120.00 | 12000.00 | 100.00 | 10000.00 | 10000.00 | surbhi association
110.00 | Supply of XLPE insulated, PVC inner sheathed, armoured copper conductor power cable of 1.1 KV grade conforming to IS-7098 Part 1(1988) amended up to date. 3 X 2.5 sq mm | 40.00 | METER | 100.00 | 360.00 | 14400.00 | 300.00 | 12000.00 | 12000.00 | surbhi association
111.00 | Supply of 16 Amps, 3 Pin Plug Top. | 10.00 | EACH | 100.00 | 300.00 | 3000.00 | 75.00 | 750.00 | 750.00 | surbhi association
112.00 | Supply of 4 Meter Length, 100 mm dia, Frangible Fiber Reinforced Plastic (FRP) poles with thickness not less than 5mm with GI base plate of size 200x200x10mm with 04 nos. of SS anchor bolt of 255 mm length and suitable SS nuts, painted with UV stabilized Poly Urethane paint of Red & white color alternatively for clear vision of pole.for installation of lightning arrestors. | 4.00 | EACH | 100.00 | 12000.00 | 48000.00 | 15000.00 | 60000.00 | 48000.00 | C P MONCHESTER ELECTRICALS
| Total in Figures |  |  |  |  | 6681234.00 |  | 7074520.00
Lowest Amount Quoted BY: C P MONCHESTER ELECTRICALS(6681234.00)

## BOQ Summary
BOQ Summary Details Tender Title: Construction of new DVOR building and allied works at Mysuru Airport. SH- Electrical works Tender ID: 2025_AAI_229211_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | C P MONCHESTER ELECTRICALS (BID ID -835376) | 6681234.00 | L1
| 2 | surbhi association (BID ID -836175) | 7074520.00 | L2