## BoQ1
Government eProcurement System Created By: Parmeet Dahiya Created Date/Time: 13-May-2025 10:54 AM Tender Title: AAI/RHQ/NR/SME/NGL-FIRE Tender ID: 2025_AAI_229520_1
TENDER INVITING AUTHORITY: SENIOR MANAGER ENGG(E), AAI RHQ, NR, NATS COMPLEX, NEW DELHI - 110037.
NAME OF WORK: S.I.T.C. OF ADDRESSABLE FIRE DETECTION & ALARM SYSTEM AT AAI NANGLOI GAGAN PROJECT.
Tender ID No.: 2025_AAI_229520_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | NATIONAL SAFETY ENGINEERS (GSTN-07ADCPT3599E3Z6) BID ID -837102 |  | ARC SERVICESS (GSTN-NA) BID ID -837023
[5 empty] | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply, Installation, Testing & Commissioning of 4 loops (with 2 loop card) Microprocessor based Intelligent Digitally Addressable Fire Alarm Control Panel with minimum 250 devices (250 in any combination per loop). The panel shall have minimum 7 inch screen display with soft keys for displaying alarm, events and operating functions, compatible with graphic user interface for pin point the identification of the fire location suitable to operate on 240 volts AC power supply. The panel shall be equipped with automatic battery charger, 24 volts maintenance free batteries sufficient for 24 hours working in normal condition & and then be capable of operating the system for minimum 30 minutes during an emergency conditions as required. (EN/UL 10th Edition & FM approved with latest amended upto date). The fire alarm panel shall have storage of 10000 event log and dongle free programming. The panel shall have interfacing connectivity on BACNET / MODBUS / Open protocol for interfacing with Building Management System complete as required. | 1.00 | EACH |  | 225000.00 | 225000.00 | 210000.00 | 210000.00 | 210000.00 | ARC SERVICESS
2.00 | Supply, Installation, Testing & Commissioning of EN/ UL listed Fire Alarm Repeater Panel with 4.3 inch screen display complete system function keys for programming and control like System Reset, Alarm Acknowledge, Alarm Silence, Trouble Acknowledge etc.The Panel shall be connected/ Interface to Main Fire Alarm Panel. (EN/UL latest edition & FM approved) | 1.00 | EACH |  | 98000.00 | 98000.00 | 125000.00 | 125000.00 | 98000.00 | NATIONAL SAFETY ENGINEERS
3.00 | Supply, Installation, Testing & Commissioning of UL / EN listed Intelligent Photoelectric Smoke Detector with Inbuilt Fault Isolator/Isolator Base, Alarm Indication LED with Electronic Addressing Feature to programme the detectors complete as required to be installed under/ above false ceiling, roof & concealed space etc. inter-connecting to loop cable complete as required. (EN/UL latest edition & FM approved) | 51.00 | EACH |  | 2360.00 | 120360.00 | 2000.00 | 102000.00 | 102000.00 | ARC SERVICESS
4.00 | Supply, Installation, Testing & Commissioning of EN/ UL listed Intelligent Addressable Multi Criteria Type (photoelectric smoke detection & thermal fixed cum rate of rise temperature detection) Smoke Detector with Inbuilt Fault Isolator/Isolator Base, Alarm Indication LED with Electronic Addressing feature to programme the detectors complete as required to be installed under/ above false ceiling, roof & concealed space etc. inter-connecting to loop cable complete as required. (EN/UL latest edition & FM approved) | 14.00 | EACH |  | 2380.00 | 33320.00 | 2050.00 | 28700.00 | 28700.00 | ARC SERVICESS
5.00 | Supply, Installation, Testing & Commissioning of Response Indicator (METAL CLADE) which consists of steady glowing LED. This LED shall be mounted within a M.S. box and connected in parallel to the built in indicator of the detector as per specifications. The RI shall come "ON" as soon as the detector activates complete in all respects as per specification. (EN/UL latest edition & FM approved) | 31.00 | EACH |  | 140.00 | 4340.00 | 320.00 | 9920.00 | 4340.00 | NATIONAL SAFETY ENGINEERS
6.00 | Providing, Installation, Testing & Commissioning of EN/ UL listed Addresable Relay Module with Inbuilt Fault Isolator/ Isolator Module with minimum IP50 load 1A @ 24V DC (for control of AHU, ventilation fan etc) complete as required. (EN/UL latest edition & FM approved) | 3.00 | EACH |  | 3550.00 | 10650.00 | 2250.00 | 6750.00 | 6750.00 | ARC SERVICESS
7.00 | Supply, Installation, Testing & Commissioning of EN/UL listed monitor module with Inbuilt Fault Isolator/ Isolator Module with minimum IP50 (for monitoring different electrical/mechanical device like flow switch etc.) (EN/UL latest edition & FM approved) | 3.00 | EACH |  | 3550.00 | 10650.00 | 2250.00 | 6750.00 | 6750.00 | ARC SERVICESS
8.00 | Supply, Testing and Commissioning of Loop Powered Hooter cum Strobe/Supervised Power Supply with Inbuilt Fault Islolator/Isolator Module complete with all accessories and base as required. (EN/UL approved) | 3.00 | EACH |  | 6600.00 | 19800.00 | 2250.00 | 6750.00 | 6750.00 | ARC SERVICESS
9.00 | Supply, Installation, Testing & Commissioning of EN / UL listed Addressable type Manual Call Point (resetting type) complete with Inbuilt Fault Isolator/Isolator Module with minimum IP40. (EN/UL latest edition & FM approved) | 3.00 | EACH |  | 3250.00 | 9750.00 | 2250.00 | 6750.00 | 6750.00 | ARC SERVICESS
10.00 | Supplying & laying of 2x1.5 sqmm Fire Survival Armoured Cable, 600/1000V rated with annealed copper conductor having glass mica fire barrier tape covered by an extruded layer of Cross Linkable Ethylene Propylene Rubber (EPR) insulation and LSZH inner bedding, steel wire armouring & LSZH outer sheath complete as required. | 2500.00 | MTR. |  | 220.00 | 550000.00 | 180.00 | 450000.00 | 450000.00 | ARC SERVICESS
11.00 | Supply and laying of 4 core x 1.5 sqmm screened copper cable for communication between Fire Alarm Panels and Repeater Panels. | 500.00 | MTR. |  | 245.00 | 122500.00 | 75.00 | 37500.00 | 37500.00 | ARC SERVICESS
| Total in Figures |  |  |  |  | 1204370.00 |  | 990120.00
Lowest Amount Quoted BY: ARC SERVICESS(990120.00)

## BOQ Summary
BOQ Summary Details Tender Title: AAI/RHQ/NR/SME/NGL-FIRE Tender ID: 2025_AAI_229520_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | ARC SERVICESS (BID ID -837023) | 990120.00 | L1
| 2 | NATIONAL SAFETY ENGINEERS (BID ID -837102) | 1204370.00 | L2