## BoQ1
Government eProcurement System Created By: Mukesh Meena Created Date/Time: 16-Apr-2025 04:58 PM Tender Title: Relocation of Outer Feeder Pillar at Old DVOR and other Electrical Works inside operational Area at C.S.M.I.Airport, Mumbai. Tender ID: 2025_AAI_229991_1
Tender Inviting Authority: Asstt.General Manager (Engg.-Elect.), ATS Complex, Mumbai.
Name of Work: "Relocation of Outer Feeder Pillar at Old DVOR and other Electrical Works inside operational Area at C.S.M.I.Airport, Mumbai.”
Contract No: MUM/ATS/ENGG-E/eNIT-09/2024-25
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | SARASWAT ENGINEERING SERVICES (GSTN-27AAZFS6239C1ZO) BID ID -838007 |  | Awasthi Electric Works (GSTN-09ABAPA1866D1Z5) BID ID -838103 |  | K Sharma Electricals Private Limited (GSTN-NA) BID ID -836060
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Design, Supply, Installation, Testing & Commissioning of Double door mounted on MS angle stand of suitable size, totally enclosed, compartmentalized, cubical, dust, vermin proof and outdoor type panel IP-56 fabricated out of 2 mm thick cold rolled carbon anealed, sheet steel, internally strengthened with angle iron frame work with following incoming and outgoing feeders (fabricated out of 2 mm CRCA Sheet steel) including supplying and mounting including making connections/inter-connections with lugs / glands crimping tools etc complete as required. (Note : Atleast 400 mm mounting legs are to be provided and ITC to be done inside operational Area, i/c minor Civil for installation of Panel) Incomer : a) 250 A, MCCB, 4P, 35-37 KA (Icu= 100% Ics) with extended rotary handle and spreaders - 02 Nos. b) Digital Voltmeter with RS 485 Port - 02 Nos. c) Digital Ammeter with RS 485 Port - 02 nos. d) Indication Lamp R, Y & B (LED Type) -02 set e) ON/OFF Indication Lamp (LED Type): - 02 set f) SPD Type(1+2) with by pass arrangement - 02 Nos. Bus Coupler (with mechanical interlock) : a) 250 A, MCCB, 4P, 35-37 KA (Icu= 100% Ics) with extended rotary handle - 01 No. b) ON/OFF Indication Lamp: - 02 set Outgoing : a) 100 A, MCCB, 4P, 25 KA (Icu= 100% Ics) with extended rotary handle and spreaders - 10 Nos. b) ON/OFF Indication lamp (LED type) - 10 Set Other : a) 300A Copper busbar, 3 Phase and Neutral b) Necessary CT & PT Control wiring arrangement c) 15 A switch Scoket d) lamp with holder (Maintenance) | 1.00 | Job |  | 587653.00 | 587653.00 | 730000.00 | 730000.00 | 530000.00 | 530000.00 | 530000.00 | K Sharma Electricals Private Limited
2.00 | Design, Supply, Installation, Testing & Commissioning of Double door mounted on MS angle stand of suitable size, totally enclosed, dust, vermin proof and outdoor type panel IP-56 fabricated out of 2 mm thick cold rolled carbon anealed, sheet steel, internally strengthened with angle iron frame work with following incoming and outgoing feeders (fabricated out of 2 mm CRCA Sheet steel) including supplying and mounting including making connections/inter-connections with lugs / glands crimping tools etc complete as required. (Note : Atleast 600 mm mounting legs are to be provided and ITC to be done inside operational Area i/c minor Civil for installation of Panel) (a) 125 A, MCCB, 4P, 15-18 KA (Icu= 100% Ics) with extended rotary handle and spreaders - 02 No. (b) 3 phase Energy Meter Class -1, 4 Wire TVM, 10 - 60A c) 15 A switch Scoket d) lamp with holder (Maintenance) | 2.00 | Job |  | 166165.00 | 332330.00 | 190000.00 | 380000.00 | 39500.00 | 79000.00 | 79000.00 | K Sharma Electricals Private Limited
3.00 | Supply, installation, testing and commissioning of 125 Amp.,4 pole, 15-18kA rating, adjustable thermal fixed magnetic release , Ics=Icu=100% , 415V AC, MCCB with spreader links in suitable MS enclosure suitable for Termination of Cable of size upto 120 sq.mm. | 2.00 | Each |  | 31073.00 | 62146.00 | 15500.00 | 31000.00 | 12000.00 | 24000.00 | 24000.00 | K Sharma Electricals Private Limited
4.00 | Supply of following sizes XLPE insulated PVC sheathed armoured Aluminium conductor cable of grade 1.1 KV , confirming to IS 7098 Part-I with up to date amendments.
4.10 | 3.5 c X 120 Sq.mm. | 1500.00 | Mtr. |  | 728.00 | 1092000.00 | 570.00 | 855000.00 | 650.00 | 975000.00 | 855000.00 | Awasthi Electric Works
4.20 | 3.5 c X 70 Sq.mm. | 1000.00 | Mtr. |  | 474.00 | 474000.00 | 360.00 | 360000.00 | 418.00 | 418000.00 | 360000.00 | Awasthi Electric Works
5.00 | Supply of following sizes PVC insulated PVC sheathed unarmoured Copper conductor cable of grade 1.1 KV , confirming to IS 694: 2010 with up to date amendments.
5.10 | 4 c x 25 sq.mm. | 200.00 | Mtr. |  | 1296.00 | 259200.00 | 1100.00 | 220000.00 | 1310.00 | 262000.00 | 220000.00 | Awasthi Electric Works
5.20 | 1 c x 10 sq.mm. | 100.00 | Mtr. |  | 123.00 | 12300.00 | 115.00 | 11500.00 | 127.00 | 12700.00 | 11500.00 | Awasthi Electric Works
6.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/ HUME/ METAL/ HDPE/DWC pipe as required.
6.10 | Above 35 sq. mm. and upto 95 sq. mm. | 690.00 | Mtr. |  | 62.00 | 42780.00 | 65.00 | 44850.00 | 50.00 | 34500.00 | 34500.00 | K Sharma Electricals Private Limited
6.20 | Above 95 sq. mm. and upto 185 sq. mm. | 650.00 | Mtr. |  | 83.00 | 53950.00 | 90.00 | 58500.00 | 75.00 | 48750.00 | 48750.00 | K Sharma Electricals Private Limited
7.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on wall surface as required.
7.10 | Upto 35 sq. mm. (clamped with 1 mm. thick saddle) | 35.00 | Mtr. |  | 47.00 | 1645.00 | 65.00 | 2275.00 | 40.00 | 1400.00 | 1400.00 | K Sharma Electricals Private Limited
7.20 | Above 35 sq. mm. and upto 95 sq. mm. | 15.00 | Mtr. |  | 75.00 | 1125.00 | 130.00 | 1950.00 | 70.00 | 1050.00 | 1050.00 | K Sharma Electricals Private Limited
7.30 | Above 95 sq. mm. and upto 185 sq. mm. | 170.00 | Mtr. |  | 104.00 | 17680.00 | 175.00 | 29750.00 | 85.00 | 14450.00 | 14450.00 | K Sharma Electricals Private Limited
8.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on cable tray as required.
8.10 | Upto 35 sq. mm. | 10.00 | Mtr. |  | 36.00 | 360.00 | 65.00 | 650.00 | 40.00 | 400.00 | 360.00 | SARASWAT ENGINEERING SERVICES
8.20 | Above 35 sq. mm. and upto 95 sq. mm. | 10.00 | Mtr. |  | 62.00 | 620.00 | 110.00 | 1100.00 | 75.00 | 750.00 | 620.00 | SARASWAT ENGINEERING SERVICES
8.30 | Above 95 sq. mm. and upto 185 sq. mm. | 10.00 | Mtr. |  | 83.00 | 830.00 | 130.00 | 1300.00 | 85.00 | 850.00 | 830.00 | SARASWAT ENGINEERING SERVICES
9.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing masonry open duct as required.
9.10 | Above 35 sq. mm. and upto 95 sq. mm. | 25.00 | Mtr. |  | 62.00 | 1550.00 | 50.00 | 1250.00 | 70.00 | 1750.00 | 1250.00 | Awasthi Electric Works
9.20 | Above 95 sq. mm. and upto 185 sq. mm. | 50.00 | Mtr. |  | 83.00 | 4150.00 | 70.00 | 3500.00 | 85.00 | 4250.00 | 3500.00 | Awasthi Electric Works
10.00 | Laying of 160 mm. DWC HDPE pipe ISI marked along with all accessories like socket, bend, couplers etc.in the existing trench/Surface, complete as required. | 150.00 | Mtr. |  | 265.00 | 39750.00 | 125.00 | 18750.00 | 25.00 | 3750.00 | 3750.00 | K Sharma Electricals Private Limited
11.00 | Laying of following size DWC HDPE pipe ISI marked along with all accessories like socket, bend, couplers, etc. complete with fitting and cutting, jointing etc.direct in ground (75 cm. below ground level) including excavation and refilling the trench but excluding sand cushioning and protective covering, etc., complete as required. | 400.00 | Mtr. |  | 318.00 | 127200.00 | 450.00 | 180000.00 | 145.00 | 58000.00 | 58000.00 | K Sharma Electricals Private Limited
12.00 | Drawing of FRLS PVC insulated copper conductor, single core cable in the existing surface/ recessed steel/ PVC conduit as required. 1 c x 10 sq.mm. | 150.00 | Mtr. |  | 16.00 | 2400.00 | 40.00 | 6000.00 | 34.00 | 5100.00 | 2400.00 | SARASWAT ENGINEERING SERVICES
13.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
13.10 | 3.5 c X 70 sq. mm. | 2.00 | Each |  | 552.00 | 1104.00 | 550.00 | 1100.00 | 675.00 | 1350.00 | 1100.00 | Awasthi Electric Works
13.20 | 3.5 c X 120 sq. mm. | 8.00 | Each |  | 788.00 | 6304.00 | 800.00 | 6400.00 | 750.00 | 6000.00 | 6000.00 | K Sharma Electricals Private Limited
14.00 | Supplying and making end termination with brass compression gland and Copper lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. 4 c X 25 Sq.mm. | 4.00 | Each |  | 447.00 | 1788.00 | 500.00 | 2000.00 | 700.00 | 2800.00 | 1788.00 | SARASWAT ENGINEERING SERVICES
15.00 | Supplying and making straight through joint with heat shrinkable kit including ferrules and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
15.10 | 3.5 c X 70 sq. mm. | 4.00 | Each |  | 3698.00 | 14792.00 | 5000.00 | 20000.00 | 5700.00 | 22800.00 | 14792.00 | SARASWAT ENGINEERING SERVICES
15.20 | 3.5 c X 120 sq. mm. | 5.00 | Each |  | 4375.00 | 21875.00 | 5500.00 | 27500.00 | 7500.00 | 37500.00 | 21875.00 | SARASWAT ENGINEERING SERVICES
16.00 | Supply, Installation Testing and commissioning of 50KVA Air Cooled Servo Controlled Voltage Stabilizer. Input Voltage Range : 340-480VAC Output Voltage : 415VAC Phase: 3PH-3PH ( To be installed in the New DVOR inside Operational Area) | 1.00 | Job |  | 134401.00 | 134401.00 | 195000.00 | 195000.00 | 110000.00 | 110000.00 | 110000.00 | K Sharma Electricals Private Limited
17.00 | Supply of 10KVA Air Cooled Servo Controlled Voltage Stabilizer. Input Voltage Range : 340-480VAC Output Voltage : 415VAC Phase: 3PH-3PH | 1.00 | Each |  | 70674.00 | 70674.00 | 88000.00 | 88000.00 | 60075.00 | 60075.00 | 60075.00 | K Sharma Electricals Private Limited
18.00 | Supply installation testing and commissioning of onload 250A 4P (I-O-II) change over switch with enclosure. | 1.00 | Job |  | 29463.00 | 29463.00 | 28000.00 | 28000.00 | 22000.00 | 22000.00 | 22000.00 | K Sharma Electricals Private Limited
19.00 | Supply, Installation, Testing & Commissioning of Digital Grounding Device 240 KA 3 phase 4 wire Portable type built in Low Impedance equipment Grounding & bonding system. Provides protection against Lightning Surges, static charge, ensuring clear bonding potential (earth to Neutral voltage) arround 1.0V with lightning impulse current upto 45KA And having pre wired, pulverent body painted metallic enclosure which is to be connected with the existing power supply circuit. | 10.00 | Job |  | 119992.00 | 1199920.00 | 100000.00 | 1000000.00 | 100000.00 | 1000000.00 | 1000000.00 | K Sharma Electricals Private Limited, Awasthi Electric Works
20.00 | Supply, Installation, Testing and Commissioningof 3P+N, Type 1+2 surge protection device with I(max) = 50 kA, I(imp) = 12.5 kA in suitable size box, including connection interconnection with 10 sq.mm. copper conductor to incomers or as directed by the EIC. The Enclosure are to be mounted on the frangible wall by providing suitable size GI strip on both the wall with the support of GI Nut and bolt or as per site requirement. | 6.00 | Each |  | 69014.00 | 414084.00 | 64000.00 | 384000.00 | 15000.00 | 90000.00 | 90000.00 | K Sharma Electricals Private Limited
21.00 | Supply of Digital time switch suitable for configuration offeeder pillars / Lighting DBs for automatic switching On & OFF with manual override facility with 12/24 hour display format. | 4.00 | Each |  | 5362.00 | 21448.00 | 4150.00 | 16600.00 | 2500.00 | 10000.00 | 10000.00 | K Sharma Electricals Private Limited
22.00 | Earthing with G.I. earth plate 600 mm. X 600 mm. X 6 mm. thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long, etc. with charcoal/ coke and salt as required. | 4.00 | Each |  | 35378.00 | 141512.00 | 16000.00 | 64000.00 | 7200.00 | 28800.00 | 28800.00 | K Sharma Electricals Private Limited
23.00 | Providing and fixing 25 mm. X 5 mm. G.I. strip in 40 mm. dia. G.I. pipe from earth electrode including connection with G.I. nut, bolt, spring, washer excavation and re-filling, etc. as required. | 18.00 | Mtr. |  | 969.00 | 17442.00 | 700.00 | 12600.00 | 550.00 | 9900.00 | 9900.00 | K Sharma Electricals Private Limited
24.00 | Supplying and laying 25 mm. X 5 mm. G.I strip at 0.50 metre below ground as strip earth electrode, including connection/ terminating with G.I. nut, bolt, spring, washer, etc. as required. | 5.00 | Mtr. |  | 187.00 | 935.00 | 250.00 | 1250.00 | 125.00 | 625.00 | 625.00 | K Sharma Electricals Private Limited
25.00 | Providing and fixing 25 mm. X 5 mm. G.I. strip on surface or in recess for connections, etc. as required. | 10.00 | Mtr. |  | 187.00 | 1870.00 | 200.00 | 2000.00 | 250.00 | 2500.00 | 1870.00 | SARASWAT ENGINEERING SERVICES
26.00 | Supplying and installing following size of perforated Hot Dipped Galvanised Iron cable tray (Galvanisation thickness not less than 50 microns) with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with G.I. suspenders including G.I. bolts & nuts, etc./or on Ground by providing suitable GI Supports in the ground as required.
26.10 | 150 mm. width X 50 mm. depth X 1.6 mm. thickness | 6.00 | Mtr. |  | 1056.00 | 6336.00 | 550.00 | 3300.00 | 700.00 | 4200.00 | 3300.00 | Awasthi Electric Works
26.20 | 300 mm. width X 50 mm. depth X 1.6 mm. thickness | 6.00 | Mtr. |  | 1563.00 | 9378.00 | 1200.00 | 7200.00 | 975.00 | 5850.00 | 5850.00 | K Sharma Electricals Private Limited
27.00 | Providing, laying and fixing following dia G.I. pipe (medium class) in ground complete with G.I. fittings including trenching (75 cm deep)and re-filling etc as required 100 mm. Dia. | 30.00 | Mtr. |  | 1769.00 | 53070.00 | 1250.00 | 37500.00 | 1600.00 | 48000.00 | 37500.00 | Awasthi Electric Works
28.00 | Providing and laying in position cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size) in foundation etc including form work, etc as required. | 10.00 | Cu.M. |  | 11669.00 | 116690.00 | 8500.00 | 85000.00 | 900.00 | 9000.00 | 9000.00 | K Sharma Electricals Private Limited
29.00 | Excavation and refilling in soft soil including dressing of sides and ramming of bottoms, lift upto 1.5 m. including getting out the excavated soil and disposal of surplus excavated soil as directed, within a lead of 50 metres. | 20.00 | Cu.M. |  | 636.00 | 12720.00 | 800.00 | 16000.00 | 700.00 | 14000.00 | 12720.00 | SARASWAT ENGINEERING SERVICES
30.00 | Demolishing cement concrete manually/ by mechanical means including disposal of material within 50 metres lead as per direction of Engineer - in - charge. Nominal concrete 1:3:6 or richer mix (i/c equivalent design mix) | 15.00 | Cu.M. |  | 4243.00 | 63645.00 | 1000.00 | 15000.00 | 1000.00 | 15000.00 | 15000.00 | K Sharma Electricals Private Limited, Awasthi Electric Works
31.00 | Dismantling of existing LT/HT cable from masonary duct/HUME/GI pipe. Upto 185 sq.mm. | 70.00 | Mtr. |  | 106.00 | 7420.00 | 50.00 | 3500.00 | 160.00 | 11200.00 | 3500.00 | Awasthi Electric Works
32.00 | Providing and fixing 6 SWG dia. G.I. wire on surface or in recess for loop earthing as required. | 100.00 | Mtr. |  | 38.00 | 3800.00 | 35.00 | 3500.00 | 27.00 | 2700.00 | 2700.00 | K Sharma Electricals Private Limited
| Total in Figures |  |  |  |  | 5464340.00 |  | 4956825.00 |  | 3990000.00
Lowest Amount Quoted BY: K Sharma Electricals Private Limited(3990000.00)

## BOQ Summary
BOQ Summary Details Tender Title: Relocation of Outer Feeder Pillar at Old DVOR and other Electrical Works inside operational Area at C.S.M.I.Airport, Mumbai. Tender ID: 2025_AAI_229991_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | K Sharma Electricals Private Limited (BID ID -836060) | 3990000.00 | L1
| 2 | Awasthi Electric Works (BID ID -838103) | 4956825.00 | L2
| 3 | SARASWAT ENGINEERING SERVICES (BID ID -838007) | 5464340.00 | L3