## BoQ1
Government eProcurement System Created By: VIVEKANAND PRASAD MORIL Created Date/Time: 27-Jun-2025 11:44 AM Tender Title: Provision of perimeter lighting along with the perimeter road in operational area and city side area at civil enclave Pathankot Airport Tender ID: 2025_AAI_231213_1
Tender Inviting Authority: <Asstt. GM Engg (Elect), Airports Authority of India, Sri Guru Ram Dass Jee, International Airport, Amritsar - 143101>
Name of Work: <Provision of perimeter lighting along with the perimeter road in operational area and city side area at civil enclave,Pathankot Airport.>
Tender ID: <2025_AAI_ 231213 _1>
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Awasthi Electric Works (GSTN-09ABAPA1866D1Z5) BID ID -845084 |  | B L ENTERPRISES (GSTN-NA) BID ID -845233 |  | JCC ENGINEERS PRIVATE LIMITED (GSTN-NA) BID ID -843835 |  | Shiva Enterprises (GSTN-NA) BID ID -845155
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply and Erection of following Length hot dip galvanised octagonal continuously tapered street light pole (with 130 mm bottom, 70 mm top) with minimum 1000 mm long double arm GI bracket (length of bracket shall be based on design) for installation of LED street light luminaire suitable for wind velocity as per IS 875 (but not less than 50 m/sec.), fabricated out of 3 mm MS plate in single section, suitable for installation on a precast foundation with supply of 4 nos. of foundation bolt & anchor plate, rigid flange plate (200x200x12mm min.) welded with the base of pole for fixing on foundation bolts complete as reqd. for structural stability as specified, weather proof door flush with the exterior surface containing a terminal plate of 5 mm thick backlite sheet with 32 Amp heavy duty connector for loop in loop out cable terminations suitable for upto two numbers 4 core 25 Sq.mm cables & 6A DP MCB for each fixture connections, earthing bolts for continuous earth connection complete as required & as specified. Job includes Erection of pole & bracket with all accessories in reinforced cement concrete foundation (as per OEM design or minimum 400mmx400mmx1.2mtr) including excavation and refilling including positioning of template & foundation bolts & providing and fixing of HDPE pipe of size 50 mm dia (2 pieces of min. 0.75 m length) in the foundation for loop-in-loop-out of the cable to the pole complete as required and as specified.
1.10 | 04 Mtr High Pole (Double Arm) | 76.00 | Each |  | 17500.00 | 1330000.00 | 8500.00 | 646000.00 | 14310.00 | 1087560.00 | 8850.00 | 672600.00 | 646000.00 | B L ENTERPRISES
1.20 | 09 Mtr High Pole (Double Arm) | 26.00 | Each |  | 26500.00 | 689000.00 | 14500.00 | 377000.00 | 21200.00 | 551200.00 | 15900.00 | 413400.00 | 377000.00 | B L ENTERPRISES
2.00 | Supply of Energy efficient 45 watt or above LED street light fixtures with sufficient number of LEDs, control gear / driver and all other associated accessories and conforming to the degree of protection IP65 complete as required and as specified. | 152.00 | Nos. |  | 1700.00 | 258400.00 | 2500.00 | 380000.00 | 3850.00 | 585200.00 | 1550.00 | 235600.00 | 235600.00 | Shiva Enterprises
3.00 | Supply of Energy efficient 110 Watt or above LED street light fixtures with sufficient number of LEDs, control gear / driver and all other associated accessories and conforming to the degree of protection IP65 complete as required and as specified. | 52.00 | Nos. |  | 3270.00 | 170040.00 | 4500.00 | 234000.00 | 9640.00 | 501280.00 | 3200.00 | 166400.00 | 166400.00 | Shiva Enterprises
4.00 | Supply of 1.1 KV grade, XLPE insulated and PVC sheathed Aluminium conductor, armored LT Cable, conforming to IS 7098 (Part -1) 1988 with upto date amendments and as specified, of following sizes.
4.10 | 4C x 16 Sqmm | 2500.00 | Mtr |  | 140.00 | 350000.00 | 200.00 | 500000.00 | 242.00 | 605000.00 | 142.00 | 355000.00 | 350000.00 | Awasthi Electric Works
4.20 | 3.5C x 25 Sqmm | 1400.00 | Mtr |  | 172.00 | 240800.00 | 250.00 | 350000.00 | 310.00 | 434000.00 | 174.00 | 243600.00 | 240800.00 | Awasthi Electric Works
4.30 | 3.5C x 50 Sqmm | 500.00 | Mtr |  | 280.00 | 140000.00 | 300.00 | 150000.00 | 480.00 | 240000.00 | 290.00 | 145000.00 | 140000.00 | Awasthi Electric Works
4.40 | 3.5C X 95 Sqmm | 300.00 | Mtr |  | 475.00 | 142500.00 | 400.00 | 120000.00 | 650.00 | 195000.00 | 480.00 | 144000.00 | 120000.00 | B L ENTERPRISES
5.00 | Supply & Laying 3X1.5 Sqmm Cu flexible wire inside street light pole for connection of light fixtures including Making Connection and end termination with aluminium lugs complete as required and as specified. (1 No. for 01 light fixture)
5.10 | Inside 04 mtr. Pole | 152.00 | Nos. |  | 325.00 | 49400.00 | 100.00 | 15200.00 | 850.00 | 129200.00 | 470.00 | 71440.00 | 15200.00 | B L ENTERPRISES
5.20 | Inside 09 mtr. Pole | 52.00 | Nos. |  | 650.00 | 33800.00 | 200.00 | 10400.00 | 1200.00 | 62400.00 | 820.00 | 42640.00 | 10400.00 | B L ENTERPRISES
6.00 | Supply of HDPE pipes, conforming to IS 14930 (Part II) with upto date amendments of following size complete as required.
6.10 | 50 mm dia. | 2000.00 | Mtr. |  | 90.00 | 180000.00 | 125.00 | 250000.00 | 92.00 | 184000.00 | 145.00 | 290000.00 | 180000.00 | Awasthi Electric Works
6.20 | 63 mm dia. | 1700.00 | Mtr. |  | 140.00 | 238000.00 | 170.00 | 289000.00 | 139.00 | 236300.00 | 160.00 | 272000.00 | 236300.00 | JCC ENGINEERS PRIVATE LIMITED
6.30 | 90 mm dia | 300.00 | Mtr. |  | 275.00 | 82500.00 | 230.00 | 69000.00 | 180.00 | 54000.00 | 235.00 | 70500.00 | 54000.00 | JCC ENGINEERS PRIVATE LIMITED
7.00 | Laying of HDPE pipes upto Size 90 mm, direct in ground upto a depth of 0.75 Mtr. including excavation and refilling the trench etc. complete as required. | 3500.00 | Mtr |  | 130.00 | 455000.00 | 20.00 | 70000.00 | 120.00 | 420000.00 | 100.00 | 350000.00 | 70000.00 | B L ENTERPRISES
8.00 | Laying of HDPE pipes Upto Size 90 mm, direct on surface with required accessories like clamp, joint etc. complete as required. | 200.00 | Mtr |  | 70.00 | 14000.00 | 20.00 | 4000.00 | 100.00 | 20000.00 | 50.00 | 10000.00 | 4000.00 | B L ENTERPRISES
9.00 | Laying of HDPE Pipe Upto Size 90 mm, in road crossing and hard surface upto a depth of 1 Mtr. through HDD/ Horizontal boaring as required & as per the direction of Engineer-in-charge. | 200.00 | Mtr |  | 150.00 | 30000.00 | 300.00 | 60000.00 | 600.00 | 120000.00 | 500.00 | 100000.00 | 30000.00 | Awasthi Electric Works
10.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade Upto 95 Sqmm size in the existing RCC / HDPE / DWC / HUME / STONEWARE / METAL pipe complete as required. | 4000.00 | Mtr |  | 85.00 | 340000.00 | 10.00 | 40000.00 | 39.00 | 156000.00 | 45.00 | 180000.00 | 40000.00 | B L ENTERPRISES
11.00 | Laying and fixing of one number PVC insulated and PVC sheathed/ XLPE power cable of 1.1 KV grade Upto 95 Sqmm size (clamped with 1mm thick saddle) on wall surface complete as required. | 300.00 | Mtr |  | 140.00 | 42000.00 | 30.00 | 9000.00 | 150.00 | 45000.00 | 35.00 | 10500.00 | 9000.00 | B L ENTERPRISES
12.00 | Supplying and making end termination with aluminium lugs, with brass compression gland for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. (Each set contains lugs for all cores and a brass gland of suitable size)
12.10 | 4C x 16 Sqmm | 210.00 | Set |  | 210.00 | 44100.00 | 40.00 | 8400.00 | 100.00 | 21000.00 | 295.00 | 61950.00 | 8400.00 | B L ENTERPRISES
12.20 | 3.5C x 25 Sqmm | 30.00 | Set |  | 255.00 | 7650.00 | 50.00 | 1500.00 | 200.00 | 6000.00 | 350.00 | 10500.00 | 1500.00 | B L ENTERPRISES
12.30 | 3.5C x 50 Sqmm | 10.00 | Set |  | 365.00 | 3650.00 | 70.00 | 700.00 | 350.00 | 3500.00 | 410.00 | 4100.00 | 700.00 | B L ENTERPRISES
12.40 | 3.5C X 95 Sqmm | 6.00 | Set |  | 450.00 | 2700.00 | 100.00 | 600.00 | 400.00 | 2400.00 | 470.00 | 2820.00 | 600.00 | B L ENTERPRISES
13.00 | Installation, Testing and commissioning of 01 nos. LED street light fixtures on the existing octagonal pole with bracket complete required. | 204.00 | Each |  | 300.00 | 61200.00 | 50.00 | 10200.00 | 120.00 | 24480.00 | 250.00 | 51000.00 | 10200.00 | B L ENTERPRISES
14.10 | Earthing with G.I. earth pipe 4.5 meter long, 40 mm dia including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe etc. with charcoal / coke and salt as required. | 10.00 | Set |  | 11000.00 | 110000.00 | 2500.00 | 25000.00 | 6500.00 | 65000.00 | 7000.00 | 70000.00 | 25000.00 | B L ENTERPRISES
14.20 | Earthing with G.I. earth plate 600 mm X 600 mm X 6 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with charcoal/ coke and salt as required. | 10.00 | Set |  | 16000.00 | 160000.00 | 4000.00 | 40000.00 | 7500.00 | 75000.00 | 10000.00 | 100000.00 | 40000.00 | B L ENTERPRISES
15.00 | Providing and fixing 6 SWG dia G.I. wire on surface/in pipe or in recess for loop earthing as required. | 2300.00 | Mtr |  | 28.00 | 64400.00 | 20.00 | 46000.00 | 30.00 | 69000.00 | 18.00 | 41400.00 | 41400.00 | Shiva Enterprises
16.00 | Supply of LED type flood light luminaire suitable for installation on High Mast as per specification having anodised reflector with lenses, housing body made of pressure die cast aluminium with extruded aluminium heat sink with heat resistant toughned glass minimum IP 65 protection with integral potted electronic driver suitable to operate on 230 +/- 10% volts AC, 50 Hz single phase supply with input surge open & short protection having minimum 110 lm/watt output with life expectancy of min 50,000 hrs for LED of required white color. It shall meet AAI technical specifications complete in all respect and as required as per the direction & satisfaction of Engineer-Incharge.
16.10 | 300W LED Flood Light | 24.00 | Nos. |  | 9500.00 | 228000.00 | 14000.00 | 336000.00 | 19200.00 | 460800.00 | 10110.00 | 242640.00 | 228000.00 | Awasthi Electric Works
16.20 | 350W LED Flood Light | 16.00 | Nos. |  | 10050.00 | 160800.00 | 18000.00 | 288000.00 | 22500.00 | 360000.00 | 12050.00 | 192800.00 | 160800.00 | Awasthi Electric Works
17.00 | Supply of raising lowering system for high mast comprising double drum winch, 6mm diameter SS wire rope, 8C x 2.5 Sqmm. copper conductor trailing cable, connector, integral power tool motor, manual handle, junction box, lightening finial Suitable for existing 25 mtr Bajaj Make high mast. | 5.00 | Nos. |  | 82000.00 | 410000.00 | 100000.00 | 500000.00 | 90000.00 | 450000.00 | 110000.00 | 550000.00 | 410000.00 | Awasthi Electric Works
18.00 | Supply of LED Aviation Obstruction light suitable to operate on 230+/- 10% volts AC,50 HZ single phase supply, as per ICAO standard etc.complete as required suitable for installation on existing high masts. | 10.00 | Nos. |  | 6900.00 | 69000.00 | 5000.00 | 50000.00 | 6500.00 | 65000.00 | 8200.00 | 82000.00 | 50000.00 | B L ENTERPRISES
19.00 | Replacement of existing High mast accessories, including Winch, Wirerope, Trailing Cable, Motor, torque limiter, Motor and winch housing etc. complete raising and lowering system.The job includes dismantling of complete set of high mast accessories as mentioned and re-assembling the same.The job also includes installation,setting, testing &commissioning of LED flood light fitting,LED obstruction lights as per specifications.All the incidental jobs(like uninstalling/ reinstallation of high masts etc)are included in this job work. The job also includes the shifting of dismantled material from site up to AAI stores and proper stacking of dismantled material. | 5.00 | Job |  | 125000.00 | 625000.00 | 5000.00 | 25000.00 | 15000.00 | 75000.00 | 32000.00 | 160000.00 | 25000.00 | B L ENTERPRISES
20.00 | Supply and Installation of Lantern Carriage suitable for 25 Mtr. mast. The lantern carriage shall be suitable for installation of LED flood light fixtures as recommended by OEM. The carriage shall be complete with all its accessories required for successful installation of carriage on existing high mast. | 1.00 | Job |  | 80000.00 | 80000.00 | 5000.00 | 5000.00 | 32000.00 | 32000.00 | 20000.00 | 20000.00 | 5000.00 | B L ENTERPRISES
21.00 | Supplying, installation, testing and commissioning of cubical type, dust & vermin proof, out door type, floor mounted electrical panel with IP 54 protection, suitable for 415 V,3 phase, 50 Hz AC supply system fabricated in compartmentalized design from CRCA sheet steel of 2mm thick for frame work and covers, 3mm thick detachable gland plate and front hinged door locking arrangement, i/c cleaning & finishing complete with 7 tank process for powder coating in approved shade, having extendable TPN Aluminum Alloy bus bars of high conductivity, DMC/ SMC bus bar supports, bottom base channel of MS section not less than 50 mm x 50 mm x 4mm thick, fabrication shall be done in transportable sections, entire panel shall have a common GI earth bar of size 25mm x 5mm at the rear with 2 Nos. earth stud, solid connections from main bus bar to switch gears with required size of Al. bus bars and control wiring with 2.5 sq.mm. PVC insulated copper conductor cable, cable alleys, cable gland plates, arrangement for incomers and necessary interlocking, floor mounted with MS angle leg ( 50 mm x 50 mm x 4mm thick), making PCC work etc., i/c providing following switch gears:- INCOMING :- MCCB FP 150A, 25KA, breaking capacities shall be ICS=ICU with built in thermal magnetic release- 02 Nos INSTRUMENTS :- -2 Nos. digital multifunction meter including suitable rating CTs for 3 phase, 4 wire operation as per specification. -2 Sets of RYB phase LED indicating lamps each controlled by 2 amp MCB. Bus Bar:- 250 Amps Aluminium busbar for 3 phase and neutral - 01 Set OUTGOINGS :- MCCB FP 63 A, 25KA with built in thermal magnetic release- 02 Nos MCCB FP 40 A, 25KA with built in thermal magnetic release- 05 Nos | 1.00 | Nos. |  | 275000.00 | 275000.00 | 225000.00 | 225000.00 | 175000.00 | 175000.00 | 140000.00 | 140000.00 | 140000.00 | Shiva Enterprises
22.00 | Supplying, installation, testing and commissioning of cubical type, dust & vermin proof, out door type, floor mounted electrical panel with IP 54 protection, suitable for 415 V,3 phase, 50 Hz AC supply system fabricated in compartmentalized design from CRCA sheet steel of 2mm thick for frame work and covers, 3mm thick detachable gland plate and front hinged door locking arrangement, i/c cleaning & finishing complete with 7 tank process for powder coating in approved shade, having extendable TPN Aluminum Alloy bus bars of high conductivity, DMC/ SMC bus bar supports, bottom base channel of MS section not less than 50 mm x 50 mm x 4mm thick, fabrication shall be done in transportable sections, entire panel shall have a common GI earth bar of size 25mm x 5mm at the rear with 2 Nos. earth stud, solid connections from main bus bar to switch gears with required size of Al. bus bars and control wiring with 2.5 sq.mm. PVC insulated copper conductor cable, cable alleys, cable gland plates, arrangement for incomers and necessary interlocking, floor mounted with MS angle leg ( 50 mm x 50 mm x 4mm thick), making PCC work etc., i/c providing following switch gears:- INCOMING :- MCCB FP 125A, 25KA, breaking capacities shall be ICS=ICU with built in thermal magnetic release- 02 Nos INSTRUMENTS :- -2 Nos. digital multifunction meter including suitable rating CTs for 3 phase, 4 wire operation as per specification. -2 Sets of RYB phase LED indicating lamps each controlled by 2 amp MCB. Bus Bar:- 200 Amps Aluminium busbar for 3 phase and neutral - 01 Set OUTGOINGS :- MCCB FP 40 A, 25KA with built in thermal magnetic release- 05 Nos | 1.00 | Nos. |  | 230000.00 | 230000.00 | 175000.00 | 175000.00 | 150000.00 | 150000.00 | 130000.00 | 130000.00 | 130000.00 | Shiva Enterprises
23.00 | Supplying, installation, testing and commissioning of cubical type, Suitable size not less than 1000mm X 500mm X 300mm, dust & vermin proof, out door type, floor mounted with 40x40x5mm MS angle leg of height 800mm, Feeder Pillar Panel with IP 54 protection on MS channel foundation, fabricated with 2mm thick CRCA Sheet and suitable size MS angle complete with detachable gland plate and front hinged door locking arrangment duly powder coated of approved shade as per approved drawings/SLD, requied MCB/Contracters/auto manual switch/MCB LED indicater lamp/Suitable capacity Busbar as require rating, accessories including connection, inter connection, wiring with minimum 2.5 sqmm flexible copper wire & provision for earth connection etc complete as required: i) 40A, 10 KA FP MCB incomer-01 No., ii) Control system for Raising/ Lowering of Mast light with available 3 phase moter upto 2 hp capacity in existing High Mast-01 No. ii) 32A TP contactors operated through 24 hrs timer switch for automatic switching of luminaries along with Auto/Manual selector switch -01 iii) 32 A, 10 KA, TPN MCB- 02 nos, 16A, 10KA, SP-2 Nos, to feed the luminaries & aviation light. iv) LED type indicating lamps with toggle switches. v) Suitable capacity overload relay & single phase preventer for moter protection | 5.00 | Nos. |  | 63000.00 | 315000.00 | 30000.00 | 150000.00 | 50000.00 | 250000.00 | 32500.00 | 162500.00 | 150000.00 | B L ENTERPRISES
24.00 | Supplying, installation, testing and commissioning of cubical type, dust & vermin proof, out door type, floor mounted electrical panel with IP 54 protection, suitable for 415 V,3 phase, 50 Hz AC supply system fabricated in compartmentalized design from CRCA sheet steel of 2mm thick for frame work and covers, 3mm thick detachable gland plate and front hinged door locking arrangement, i/c cleaning & finishing complete with 7 tank process for powder coating in approved shade, having extendable TPN Aluminum Alloy bus bars of high conductivity, DMC/ SMC bus bar supports, bottom base channel of MS section not less than 50 mm x 50 mm x 4mm thick, fabrication shall be done in transportable sections, entire panel shall have a common GI earth bar of size 25mm x 5mm at the rear with 2 Nos. earth stud, solid connections from main bus bar to switch gears with required size of Al. bus bars and control wiring with 2.5 sq.mm. PVC insulated copper conductor cable, cable alleys, cable gland plates, arrangement for incomers and necessary interlocking, floor mounted with MS angle leg ( 50 mm x 50 mm x 4mm thick), making PCC work etc., i/c providing following switch gears:- INCOMING :- MCCB FP 63A, 25KA, breaking capacities shall be ICS=ICU with built in thermal magnetic release- 01 Nos INSTRUMENTS :- -1 Nos. digital multifunction meter including suitable rating CTs for 3 phase, 4 wire operation as per specification. -1 Sets of RYB phase LED indicating lamps each controlled by 2 amp MCB. Bus Bar:- 100 Amps Aluminium busbar for 3 phase and neutral - 01 Set OUTGOINGS :- MCB TPN 16 A with built in thermal magnetic release- 05 Nos | 2.00 | Set |  | 88000.00 | 176000.00 | 40000.00 | 80000.00 | 35000.00 | 70000.00 | 40000.00 | 80000.00 | 70000.00 | JCC ENGINEERS PRIVATE LIMITED
25.00 | Supplying, installation, testing and commissioning of cubical type, dust & vermin proof, out door type, floor mounted electrical panel with IP 54 protection, suitable for 415 V,3 phase, 50 Hz AC supply system fabricated in compartmentalized design from CRCA sheet steel of 2mm thick for frame work and covers, 3mm thick detachable gland plate and front hinged door locking arrangement, i/c cleaning & finishing complete with 7 tank process for powder coating in approved shade, having extendable TPN Aluminum Alloy bus bars of high conductivity, DMC/ SMC bus bar supports, bottom base channel of MS section not less than 50 mm x 50 mm x 4mm thick, fabrication shall be done in transportable sections, entire panel shall have a common GI earth bar of size 25mm x 5mm at the rear with 2 Nos. earth stud, solid connections from main bus bar to switch gears with required size of Al. bus bars and control wiring with 2.5 sq.mm. PVC insulated copper conductor cable, cable alleys, cable gland plates, arrangement for incomers and necessary interlocking, floor mounted with MS angle leg ( 50 mm x 50 mm x 4mm thick), making PCC work etc., i/c providing following switch gears:- INCOMING :- MCB FP 40A, 25KA, breaking capacities shall be ICS=ICU with built in thermal magnetic release- 01 Nos INSTRUMENTS :- -1 Set of RYB phase LED indicating lamps each. TIMER:- -40 A TPN Contactor operated with digital/analog 24 hrs Timer - 01 Nos | 4.00 | Set |  | 29000.00 | 116000.00 | 25000.00 | 100000.00 | 48500.00 | 194000.00 | 25000.00 | 100000.00 | 100000.00 | Shiva Enterprises, B L ENTERPRISES
32.00 | Note: 1. Rate quoted shall be inclusive of any taxes, duties, Cess, fee, royalty charges etc. levied under any statute but exclusive of GST. Goods & Services Tax (GST) shall be paid to the contractor for any taxable supply/ services/works against a valid tax invoice as per terms and conditions of the contract.
| Total in Figures |  |  |  |  | 7923940.00 |  | 5640000.00 |  | 8174320.00 |  | 5974390.00
Lowest Amount Quoted BY: B L ENTERPRISES(5640000.00)

## BOQ Summary
BOQ Summary Details Tender Title: Provision of perimeter lighting along with the perimeter road in operational area and city side area at civil enclave Pathankot Airport Tender ID: 2025_AAI_231213_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | B L ENTERPRISES (BID ID -845233) | 5640000.00 | L1
| 2 | Shiva Enterprises (BID ID -845155) | 5974390.00 | L2
| 3 | Awasthi Electric Works (BID ID -845084) | 7923940.00 | L3
| 4 | JCC ENGINEERS PRIVATE LIMITED (BID ID -843835) | 8174320.00 | L4