## BoQ1
Government eProcurement System Created By: SREEKUMAR P V Created Date/Time: 09-Aug-2025 02:01 PM Tender Title: Providing illumination to Helicopter Parking Stands at Donyi Polo Airport, Itanagar Tender ID: 2025_AAI_232093_1
Tender Inviting Authority: Senior Manager (Engg.-Elect.)
Name of Work:Providing illumination to Helicopter Parking Stand at Donyi Polo Airport, Itanagar
Contract No: 2025_AAI_232093_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | sudarshnacoolingcentre andelectricals (GSTN-18AAJFM8760E1ZZ) BID ID -845544 |  | BR Power Control and Automation Services (GSTN-06AREPS4024K1ZP) BID ID -847631
[5 empty] | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Earth Excavation and making foundation with PCC, Supply and Installation of GI Pipe painted in aviation yellow mounted vertically in the foundation to a depth of 300mm, Supply and fixing of SMC box including SMC connector on the GI Pole, Installation of LED luminaire and making necessary connection. Supply and installation of MCB etc complete as required with following specification. A. Foundation: • PCC: 1:3:6, dimension 300Lx300Wx450D in mm including centering and shuttering, necessary earth excavation work as required. B. GI Pipe: • Length: 1.3 Mtr ( 1Mtr above PCC foundation & 0.3Mtr inside PCC Foundation), Class B GI Pipe Painted with two coats of primer and two coats of synthetic enamel paint of aviation yellow colour. • Providing suitable closing at top of pipe to prevent water entry. • Suitable Provisions at top for mounting 400W LED luminaire, • Suitable size Holes on pipe for wire entry and exit from SMC box for LED Luminaire, C. SMC Box: • Minimum dimension of 300x200x105mm IP 55, including SMC Connector for looping 2 No.s 3.5Cx25 Sqmm cable & fixing Single Pole MCB, provision for GI Earth Wire looping/Termination, • Suitable Holes for the following: o For compression gland fixing at entry of 2 No.s 3.5Cx25 Sqmm cables o For GI Wire entry o For interconnection between MCB,SMC Connector and LED Luminaire , D. LED Luminaire Installation: • Using 3corex4sqmm wire E. SP MCB: • 2A, C curve Installation, testing & Commissioning of the above-mentioned work complete as required. | 16.00 | Job |  | 6760.11 | 108161.76 | 9193.00 | 147088.00 | 108161.76 | sudarshnacoolingcentre andelectricals
2.00 | Supply of 400W LED integral type flood light fitting with all accessories nut & bolts etc. as per the enclosed technical specifications and AAI preferred make (Model Reference :-Surya SLE FL 400W IP66 LIVIA G1 Y3) or with Equivalent specification | 16.00 | Each |  | 11957.27 | 191316.32 | 20189.00 | 323024.00 | 191316.32 | sudarshnacoolingcentre andelectricals
3.00 | Supply of following sizes of 1.1 KV grade XLPE insulated PVC sheathed, Aluminimum Conductor armoured power cable confirming to IS 7098 (Part (i)) 3.5C X 25 sq mm | 950.00 | Mtr |  | 224.04 | 212838.00 | 194.00 | 184300.00 | 184300.00 | BR Power Control and Automation Services
4.00 | Supplying and laying of following size DWC HDPE pipe ISI marked along with all accessories like socket, bend, couplers etc. conforming to IS 14930 Part II complete with fitting and cutting, jointing etc direct in ground (75cm below ground level) including excavation and refilling the trench but excluding sand cushioning and protective covering etc., complete as required. 63 mm dia (OD-63 mm & ID-51 mm nominal) | 950.00 | Mtr |  | 127.40 | 121030.00 | 295.00 | 280250.00 | 121030.00 | sudarshnacoolingcentre andelectricals
5.00 | Laying of one number PVC insulated and PVC sheathed/ XLPE power cable of 1.1 KV grade of following size in the existing RCC/HUME/METAL/DWC HDPE Pipe as required. Upto 35 Sqmm | 950.00 | Mtr |  | 30.80 | 29260.00 | 67.00 | 63650.00 | 29260.00 | sudarshnacoolingcentre andelectricals
6.00 | Providing and fixing 6 SWG dia G.I. wire on surface/in recess/ in existing RCC/HUME/METAL/DWC HDPE Pipe for loop earthing as required. | 950.00 | Mtr |  | 82.11 | 78004.50 | 52.00 | 49400.00 | 49400.00 | BR Power Control and Automation Services
7.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC Sheathed/ XLPE aluminium conductor cable of 1.1 KV grade as required. 3C X 4 Sq. mm | 16.00 | Set |  | 293.47 | 4695.52 | 372.00 | 5952.00 | 4695.52 | sudarshnacoolingcentre andelectricals
8.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC Sheathed/ XLPE aluminium conductor cable of 1.1 KV grade as required. 3.5C X 25 Sq. mm | 32.00 | Set |  | 430.78 | 13784.96 | 568.00 | 18176.00 | 13784.96 | sudarshnacoolingcentre andelectricals
9.00 | Supply and Laying 100 mm dia Class B pipe in concrete/bitumen road by cutting the concrete/bitumen and finish/Making good the surface with 1:2:4 Cement Concrete Etc as required | 12.00 | Mtr |  | 2894.35 | 34732.20 | 1766.00 | 21192.00 | 21192.00 | BR Power Control and Automation Services
| Total in Figures |  |  |  |  | 793823.26 |  | 1093032.00
Lowest Amount Quoted BY: sudarshnacoolingcentre andelectricals(793823.26)

## BOQ Summary
BOQ Summary Details Tender Title: Providing illumination to Helicopter Parking Stands at Donyi Polo Airport, Itanagar Tender ID: 2025_AAI_232093_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | sudarshnacoolingcentre andelectricals (BID ID -845544) | 793823.26 | L1
| 2 | BR Power Control and Automation Services (BID ID -847631) | 1093032.00 | L2