## BoQ1
Government eProcurement System Created By: Debdeep Dutta Created Date/Time: 28-May-2025 06:58 PM Tender Title: Provision of Fire Fighting System and augmentation / re-orientation of water supply system at Bagdogra Airport. Tender ID: 2025_AAI_232514_1
Tender Inviting Authority: AGM(E-E)
Name of Work: Provision of Fire Fighting System and augmentation / re-orientation of water supply system at Bagdogra Airport.
Contract No: 2025_AAI_232514_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | M/S JAYSHWAL ENTERPRISES (GSTN-24AEFPC8401C1Z9) BID ID -845724 |  | CENTRE TAP ENGINEERING (GSTN-24AGPPP8172K1ZP) BID ID -847216 |  | Modern Agencies (GSTN-04AAWFM7893FIZL) BID ID -847247 |  | J.K.DEFENCE FIRE ENGG. SERVICES (GSTN-NA) BID ID -846909 |  | FAIRDEAL ASSOCIATES (GSTN-NA) BID ID -848919 |  | VOID FIRE CONSULTANTS (GSTN-NA) BID ID -847182
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | A. FIRE FIGHTING SYSTEM Supply, installation, testing and commissioning of Electric driven main fire pump suitable for automatic operation and consisting of following: complete in all respect as required as per specifications. (a) Horizontal type, centrifugal, split casing pump of cast iron body and bronze impeller with stainless steel shaft, mechanical seal to ensure a minimum pressure of 3.5 kg/sq.cm.at highest and farthest outlet at specified flow of 2850 lpm at 70 m. head conforming to IS 1520 (b) Suitable HP squirrel cage induction motor, TEFC, synchronous speed 1500 RPM, suitable for operation on 415 volts, 3 phase 50 Hz. AC with IP 55 protection for enclosure, horizontal foot mounted type with Class-'F' insulation, conforming to IS- 325. (c) M.S. fabricated Common base plate, coupling, coupling guard, foundation bolts etc. duly painted as required. | 1.00 | Set | 667000.00 | 435600.00 | 435600.00 | 625000.00 | 625000.00 | 685000.00 | 685000.00 | 600000.00 | 600000.00 | 762718.00 | 762718.00 | 505000.00 | 505000.00 | 435600.00 | M/S JAYSHWAL ENTERPRISES
2.00 | Supply, installation, testing and commissioning of Diesel Engine driven fire pump suitable for automatic operation comprising of the following and conforming to BS 649/IS 10002 all amended upto date. Horizontal, centrifugal end suction top discharge single stage pump set. The installation shall be complete with flexible coupling and coupling guard as required. Fire pump shall have C.I. casing, CS diffusers, bronze impeller (hard finished and dynamically balanced) and SS (304) shaft with mechanical seal, capable for delivering 2850 LPM at head of 70 mts to ensure a minimum pressure of 3.5 Kg/Sqcm at the farthest or topmost hydrant / sprinkler. The installation shall be complete with necessary pressure gauge with gun metal shut off cock on delivery side (The pump should be tested for bench mark at factory and shall be gotten approved by the Local fire Authority). Pump shall be capable of furnishing not less than 150% of rated capacity at a head of not less than 65% of the rated head. The shut off head shall not exceed 120% of rated head. | 1.00 | Set | 750000.00 | 682500.00 | 682500.00 | 700000.00 | 700000.00 | 785000.00 | 785000.00 | 750000.00 | 750000.00 | 774970.00 | 774970.00 | 817600.00 | 817600.00 | 682500.00 | M/S JAYSHWAL ENTERPRISES
3.00 | Radiator cooled (secondary cooling) diesel engine of speed 1500 RPM suitable for the above pump with automatic starting mechanism and other accessories including fuel tank (fabricated from 3mm MS sheet, painted with two coats of synthetic enamel paint over a coat of primer) of capacity adequate to sustain pump operation for 8 hours continuous working. The tank shall be fitted with MH with cover, drain valve, air vent including structural supports (painted with approved shade), 2 Nos. 12 volt battery 120 AH, heat exchanger with necessary piping connections & fittings, flexible coupling, coupling guard & exhaust pipe connection complete as required. Common base plate for M.S. channel of required size and suitable cement concrete foundation with plaster complete as required.
4.00 | Supply, Installation, testing and commissioning of electric driven pressurisation (Jockey) pump suitable for automatic operation and consisting of following: complete in all respect as required as per specifications. (a) Horizontal type, centrifugal pump of cast iron body and bronze impeller with stainless steel shaft, mechanical seal and flow of 180 lpm at 70 m. head conforming to IS : 1520. (b) Suitable HP SQ cage induction motor TEFC type suitable for operation of 415 volts, 3 phase 50 Hz. AC with IP 55 class of protection for enclosure, horizontal foot mounted type with Class-'F' insulation, conforming to IS : 325. (c) M.S. fabricated Common base plate, coupling, coupling guard, foundation bolts etc. duly painted as required. | 1.00 | Set | 150667.00 | 125000.00 | 125000.00 | 142000.00 | 142000.00 | 165000.00 | 165000.00 | 225000.00 | 225000.00 | 170536.00 | 170536.00 | 164000.00 | 164000.00 | 125000.00 | M/S JAYSHWAL ENTERPRISES
5.00 | Supplying, testing, installation & commissioning of pressure switches for Fire fighting system including necessary wiring upto control panel & other materials as required as per specifications. | 4.00 | Each | 4000.00 | 3000.00 | 12000.00 | 3700.00 | 14800.00 | 4200.00 | 16800.00 | 3000.00 | 12000.00 | 2800.00 | 11200.00 | 1182.00 | 4728.00 | 4728.00 | VOID FIRE CONSULTANTS
6.00 | Providing & fixing dial type (100 mm) pressure gauge with isolation ball valve suitable for working pressure of 250 PSI, short pieces, nipples, elbows, stainless steel 'U' tube & ball valve, etc as required as per specifications. | 4.00 | Each | 4070.00 | 2000.00 | 8000.00 | 3800.00 | 15200.00 | 4200.00 | 16800.00 | 2000.00 | 8000.00 | 2500.00 | 10000.00 | 606.00 | 2424.00 | 2424.00 | VOID FIRE CONSULTANTS
7.00 | PIPES & VALVES Providing, laying, testing and comissioning of 'C' Class heavy duty GI Pipe conforming to IS:1239 / 3589 fittings like tees, elbows, flanges, tapers, compressed asbestos gaskets, nuts and bolts, etc. Fixing the pipe on wall / ceiling/ supported on existing structure with suitable clamps painting with two or more coats of synthetic enamel paint of required shade complete as required as per specifications.
8.00 | 25 mm dia | 30.00 | Metre | 650.00 | 430.00 | 12900.00 | 600.00 | 18000.00 | 700.00 | 21000.00 | 700.00 | 21000.00 | 275.00 | 8250.00 | 318.00 | 9540.00 | 8250.00 | FAIRDEAL ASSOCIATES
9.00 | 65 mm dia | 30.00 | Metre | 1550.00 | 990.00 | 29700.00 | 1400.00 | 42000.00 | 1600.00 | 48000.00 | 900.00 | 27000.00 | 690.00 | 20700.00 | 834.00 | 25020.00 | 20700.00 | FAIRDEAL ASSOCIATES
10.00 | 80 mm dia | 300.00 | Metre | 1700.00 | 1194.00 | 358200.00 | 1600.00 | 480000.00 | 1800.00 | 540000.00 | 1100.00 | 330000.00 | 910.00 | 273000.00 | 1032.00 | 309600.00 | 273000.00 | FAIRDEAL ASSOCIATES
11.00 | 150 mm dia | 2220.00 | Metre | 3164.00 | 2430.00 | 5394600.00 | 3000.00 | 6660000.00 | 3250.00 | 7215000.00 | 2600.00 | 5772000.00 | 2060.00 | 4573200.00 | 2300.00 | 5106000.00 | 4573200.00 | FAIRDEAL ASSOCIATES
12.00 | 200 mm dia | 30.00 | Metre | 3758.00 | 3400.00 | 102000.00 | 3500.00 | 105000.00 | 3700.00 | 111000.00 | 2800.00 | 84000.00 | 2730.00 | 81900.00 | 3149.00 | 94470.00 | 81900.00 | FAIRDEAL ASSOCIATES
13.00 | 250 mm dia | 30.00 | Metre | 4885.00 | 4200.00 | 126000.00 | 4600.00 | 138000.00 | 5000.00 | 150000.00 | 3000.00 | 90000.00 | 3380.00 | 101400.00 | 3940.00 | 118200.00 | 90000.00 | J.K.DEFENCE FIRE ENGG. SERVICES
14.00 | Supplying, laying, testing and commissioning of pipes of following sizes of MS 'C' class heavy duty along with necessary clamps, vibration isolators and fittings such as elbows, tees, flanges, tapers, nut bolts, gaskets etc..but excluding valves, strainers, gauges etc. adequately supported on cement concrete supports, anti corrosive treatment with coaltar / Asphalt tape as per lS : 1022 duly painted and buried in ground, excavation and refilling the trench etc. as per specifications and as required complete in all respect. Note : The Pipes size 150 mm & below shall be M.S. 'C' class as per lS : 1239 and pipes size above 150 mm shall be welded black steel pipe heavy class as per lS: 3589, from minimum 6.35 mm thick M.S. Sheet for pipes upto 350 mm dia.
15.00 | 150mm dia. (for External) | 200.00 | Metre | 3460.00 | 2850.00 | 570000.00 | 3250.00 | 650000.00 | 3600.00 | 720000.00 | 2750.00 | 550000.00 | 2260.00 | 452000.00 | 3400.00 | 680000.00 | 452000.00 | FAIRDEAL ASSOCIATES
16.00 | 100mm dia. (for External) | 30.00 | Metre | 3050.00 | 2100.00 | 63000.00 | 2850.00 | 85500.00 | 3150.00 | 94500.00 | 1400.00 | 42000.00 | 1320.00 | 39600.00 | 2243.00 | 67290.00 | 39600.00 | FAIRDEAL ASSOCIATES
17.00 | 80mm dia. (for External) | 50.00 | Metre | 2000.00 | 1600.00 | 80000.00 | 1900.00 | 95000.00 | 2100.00 | 105000.00 | 1200.00 | 60000.00 | 1500.00 | 75000.00 | 1776.00 | 88800.00 | 60000.00 | J.K.DEFENCE FIRE ENGG. SERVICES
18.00 | Providing & fixing of following sizes of butterfly valve of rating PN 16, wafer type, in cast iron body with Ductile lron disc, EPDM seal, SS single piece shaft, conforming to lS-13095 of the following sizes complete with cast iron hand lever companion flanges, bolts, nuts, washers & inserted rubber gaskets, as required and as per enclosed specifications.
19.00 | 40 mm dia | 1.00 | Each | 2500.00 | 2500.00 | 2500.00 | 2300.00 | 2300.00 | 2600.00 | 2600.00 | 3000.00 | 3000.00 | 1600.00 | 1600.00 | 2008.00 | 2008.00 | 1600.00 | FAIRDEAL ASSOCIATES
20.00 | 65 mm dia | 1.00 | Each | 4700.00 | 3000.00 | 3000.00 | 4400.00 | 4400.00 | 5000.00 | 5000.00 | 4000.00 | 4000.00 | 3550.00 | 3550.00 | 2668.00 | 2668.00 | 2668.00 | VOID FIRE CONSULTANTS
21.00 | 80 mm dia | 20.00 | Each | 8050.00 | 4000.00 | 80000.00 | 7600.00 | 152000.00 | 8500.00 | 170000.00 | 5500.00 | 110000.00 | 4450.00 | 89000.00 | 3011.00 | 60220.00 | 60220.00 | VOID FIRE CONSULTANTS
22.00 | 100 mm dia | 1.00 | Each | 9750.00 | 4500.00 | 4500.00 | 9200.00 | 9200.00 | 10500.00 | 10500.00 | 5950.00 | 5950.00 | 7300.00 | 7300.00 | 3647.00 | 3647.00 | 3647.00 | VOID FIRE CONSULTANTS
23.00 | 150 mm dia | 8.00 | Each | 13750.00 | 5500.00 | 44000.00 | 13000.00 | 104000.00 | 14500.00 | 116000.00 | 6500.00 | 52000.00 | 10395.00 | 83160.00 | 5511.00 | 44088.00 | 44000.00 | M/S JAYSHWAL ENTERPRISES
24.00 | 200 mm dia | 1.00 | Each | 20250.00 | 11500.00 | 11500.00 | 19000.00 | 19000.00 | 21000.00 | 21000.00 | 9500.00 | 9500.00 | 13897.00 | 13897.00 | 8103.00 | 8103.00 | 8103.00 | VOID FIRE CONSULTANTS
25.00 | Providing & fixing CI dual plate check valve PN 16, including rubber gasket, flanges, union, nuts, bolts, washers & painting complete as required as per specifications.
26.00 | 80 mm dia | 2.00 | Each | 10000.00 | 4200.00 | 8400.00 | 6100.00 | 12200.00 | 11000.00 | 22000.00 | 4000.00 | 8000.00 | 1920.00 | 3840.00 | 3109.00 | 6218.00 | 3840.00 | FAIRDEAL ASSOCIATES
27.00 | 100 mm dia | 2.00 | Each | 6500.00 | 5200.00 | 10400.00 | 9400.00 | 18800.00 | 13000.00 | 26000.00 | 7500.00 | 15000.00 | 4450.00 | 8900.00 | 4430.00 | 8860.00 | 8860.00 | VOID FIRE CONSULTANTS
28.00 | 150 mm dia | 2.00 | Each | 15000.00 | 7000.00 | 14000.00 | 14000.00 | 28000.00 | 17500.00 | 35000.00 | 12500.00 | 25000.00 | 3720.00 | 7440.00 | 7764.00 | 15528.00 | 7440.00 | FAIRDEAL ASSOCIATES
29.00 | 200 mm dia | 1.00 | Each | 22750.00 | 15200.00 | 15200.00 | 21500.00 | 21500.00 | 24000.00 | 24000.00 | 15000.00 | 15000.00 | 5785.00 | 5785.00 | 12620.00 | 12620.00 | 5785.00 | FAIRDEAL ASSOCIATES
30.00 | Providing & fixing of Cl double flange sluice valve of rating PN 16 with non rising SS spindle, Bronze/Gun Metal seat conforming to lS -780 complete with flanges,nut-bolts, gasket, washers etc. as required and as per enclosed speciflcations.
31.00 | 80 mm dia | 3.00 | Each | 15625.00 | 8500.00 | 25500.00 | 14400.00 | 43200.00 | 15000.00 | 45000.00 | 15000.00 | 45000.00 | 9633.00 | 28899.00 | 11387.00 | 34161.00 | 25500.00 | M/S JAYSHWAL ENTERPRISES
32.00 | 150 mm dia | 7.00 | Each | 15167.00 | 18800.00 | 131600.00 | 14500.00 | 101500.00 | 22000.00 | 154000.00 | 30000.00 | 210000.00 | 25766.00 | 180362.00 | 18568.00 | 129976.00 | 101500.00 | CENTRE TAP ENGINEERING
33.00 | 200 mm dia | 2.00 | Each | 38548.00 | 30500.00 | 61000.00 | 36000.00 | 72000.00 | 40000.00 | 80000.00 | 38000.00 | 76000.00 | 37297.00 | 74594.00 | 35211.00 | 70422.00 | 61000.00 | M/S JAYSHWAL ENTERPRISES
34.00 | Providing & fixing of Stainless Steel double flange suction "Y'' type strainer fabricated out of minimum 1.2 mm thick Stainless Steel sheet. perforation holes including nuts, bolts and 2 mm thick rubber insertion complete & tested to 16 Kg/Sq.cm pressure complete as required and as per enclosed specifications.
35.00 | 80 mm dia | 1.00 | Each | 12100.00 | 6000.00 | 6000.00 | 11000.00 | 11000.00 | 12000.00 | 12000.00 | 20000.00 | 20000.00 | 11295.00 | 11295.00 | 5536.00 | 5536.00 | 5536.00 | VOID FIRE CONSULTANTS
36.00 | 200 mm dia | 2.00 | Each | 32500.00 | 29200.00 | 58400.00 | 30000.00 | 60000.00 | 31500.00 | 63000.00 | 45000.00 | 90000.00 | 19300.00 | 38600.00 | 25000.00 | 50000.00 | 38600.00 | FAIRDEAL ASSOCIATES
37.00 | Providing & fixing of Flow Switch with all accessories. paddle type SPDT WFS, Operating Pressure 10kgf/cm², Withstand Pressure 17.5Kgf/cm² Temperature of Fluid Max 100°C .
38.00 | 150 mm NB | 2.00 | Each | 10750.00 | 7500.00 | 15000.00 | 10000.00 | 20000.00 | 12000.00 | 24000.00 | 9500.00 | 19000.00 | 4200.00 | 8400.00 | 2336.00 | 4672.00 | 4672.00 | VOID FIRE CONSULTANTS
39.00 | 100 mm NB | 8.00 | Each | 5800.00 | 6500.00 | 52000.00 | 5400.00 | 43200.00 | 6000.00 | 48000.00 | 7500.00 | 60000.00 | 4200.00 | 33600.00 | 2366.00 | 18928.00 | 18928.00 | VOID FIRE CONSULTANTS
40.00 | Providing and fixing forged brass ball valve with forged brass ball PN 16 rating with nut, bolts & washers, painting etc complete as required as per specifications.
41.00 | 25 mm dia | 12.00 | Each | 1317.00 | 650.00 | 7800.00 | 1200.00 | 14400.00 | 1500.00 | 18000.00 | 2000.00 | 24000.00 | 750.00 | 9000.00 | 670.00 | 8040.00 | 7800.00 | M/S JAYSHWAL ENTERPRISES
42.00 | 40 mm dia | 4.00 | Each | 2500.00 | 12500.00 | 50000.00 | 2300.00 | 9200.00 | 2700.00 | 10800.00 | 2500.00 | 10000.00 | 1910.00 | 7640.00 | 2390.00 | 9560.00 | 7640.00 | FAIRDEAL ASSOCIATES
43.00 | Providing & fixing gun metal single headed fire hydrant landing valve (external & internal) with flanged inlet, brass spindle controlled 63 mm dia female instantaneous outlet type. CI wheel, GM (gun metal) coupling, blank cap, chain, twist release type lug & all accessories. Conforming to IS:5290 complete as required as per specifications. | 26.00 | Each | 8952.00 | 10500.00 | 273000.00 | 8400.00 | 218400.00 | 9500.00 | 247000.00 | 9500.00 | 247000.00 | 4450.00 | 115700.00 | 11534.00 | 299884.00 | 115700.00 | FAIRDEAL ASSOCIATES
44.00 | Providing & fixing permaline delivery fire hose pipe (as per IS : 636) of 63 mm dia and 15 meter length. The hose shall be rated for brust pressure of 35.7 Kg/sqcm. Hose shall be complete with ISI marked brass male & female coupling (IS:903) bound & rivetted to hose pipe with copper rivets & copper wire as required as per specifications. (Location : Internal fire hydrant) | 52.00 | Each | 5750.00 | 5500.00 | 286000.00 | 5400.00 | 280800.00 | 6000.00 | 312000.00 | 5500.00 | 286000.00 | 3550.00 | 184600.00 | 5329.00 | 277108.00 | 184600.00 | FAIRDEAL ASSOCIATES
45.00 | Providing and Fixing 63 mm dia instantaneous pattern branch short gunmetal pipe, 20 mm dia nozzle conforming to IS 903, suitable for instantaneous connection to hose pipe coupling complete as required as per specifications. | 26.00 | Each | 2550.00 | 3000.00 | 78000.00 | 2400.00 | 62400.00 | 3000.00 | 78000.00 | 2950.00 | 76700.00 | 1850.00 | 48100.00 | 2920.00 | 75920.00 | 48100.00 | FAIRDEAL ASSOCIATES
46.00 | Supplying and fixing First-Aid-Hose Reel with MS construction spray painted in Post office red, conforming to IS 884 with upto date ammendments, complete with the following as required. 30m long 20mm (nominal internal) dia water hose thermoplastic as per IS:12585. 20mm (nominal internal) dia gun metal globe valve & nozzle.Drum and brackets for fixing the equipments on wall, including Connections from riser with 40mm dia stop valve (gun metal) & G.I.pipe | 10.00 | Each | 12500.00 | 8500.00 | 85000.00 | 12000.00 | 120000.00 | 12000.00 | 120000.00 | 12000.00 | 120000.00 | 3990.00 | 39900.00 | 8760.00 | 87600.00 | 39900.00 | FAIRDEAL ASSOCIATES
47.00 | Providing and fixing of following weather proof lockable cabinet of size not less than 0.75 x 0.60 x 0.25 mtr suitable to accomodate 2 Nos. 15 m long, hose pipes and 1 No. branch pipe made out of Powder coated MS sheet of approved shade, 2mm thick having central opening and 6 mm thick glazed glass doors (Two nos.), stainless steel hinges, break glass recess key holder, suitably marked on the outside with the letters "FIRE HOSE" including necessary locking arrangement and approved shade complete as required.
48.00 | Providing and fixing of Pedestal mounted type Fire Hose Cabinet with sloping top including constructing suitable stand made out of steel structure or brickwork as per site requirement. | 14.00 | Each | 8067.00 | 15500.00 | 217000.00 | 7500.00 | 105000.00 | 9000.00 | 126000.00 | 8500.00 | 119000.00 | 4500.00 | 63000.00 | 5548.00 | 77672.00 | 63000.00 | FAIRDEAL ASSOCIATES
49.00 | Providing and fixing of Wall mounted type Fire Hose Cabinet including drilling of holes and fixing with suitable fasteners as per site requirement. | 12.00 | Each | 6585.00 | 4500.00 | 54000.00 | 6000.00 | 72000.00 | 6500.00 | 78000.00 | 6000.00 | 72000.00 | 2500.00 | 30000.00 | 4526.00 | 54312.00 | 30000.00 | FAIRDEAL ASSOCIATES
50.00 | Providing & fixing double flanged flexicon rubber expansion joint (suitable for system test pressure) of standard length as per manufacturers specs including rubber gaskets, flanges, nuts, bolts and washers complete as required as per specifications.
51.00 | 80 mm dia | 1.00 | Each | 9600.00 | 8500.00 | 8500.00 | 9000.00 | 9000.00 | 10000.00 | 10000.00 | 7500.00 | 7500.00 | 2500.00 | 2500.00 | 9865.00 | 9865.00 | 2500.00 | FAIRDEAL ASSOCIATES
52.00 | 150 mm dia | 2.00 | Each | 10750.00 | 11200.00 | 22400.00 | 10000.00 | 20000.00 | 12000.00 | 24000.00 | 10500.00 | 21000.00 | 3200.00 | 6400.00 | 15023.00 | 30046.00 | 6400.00 | FAIRDEAL ASSOCIATES
53.00 | Providing & fixing of 25mm dia. gunmetal air release valve with all fittings and forged ball valve on header complete as required and as per enclosed speciflcations. | 2.00 | Each | 2983.00 | 850.00 | 1700.00 | 2800.00 | 5600.00 | 3500.00 | 7000.00 | 5000.00 | 10000.00 | 1950.00 | 3900.00 | 1109.00 | 2218.00 | 1700.00 | M/S JAYSHWAL ENTERPRISES
54.00 | Supplying and fixing of 3 way fire brigade connection of cast iron body with 4 nos. Gun metal male instantaneous inlet couplings complete with cap and chain as required for 150 mm dia MS pipe connection, conforming to IS 904 as required as per specifications. | 2.00 | Each | 12500.00 | 10000.00 | 20000.00 | 11500.00 | 23000.00 | 12000.00 | 24000.00 | 15000.00 | 30000.00 | 4800.00 | 9600.00 | 5986.00 | 11972.00 | 9600.00 | FAIRDEAL ASSOCIATES
55.00 | Supplying and fixing of fire brigade suction hose coupling (Two way Draw out connection) in CI body , Gun metal internal connection with nut for female coupling required for 150mm dia GI pipe connection as per IS 904 as required. | 1.00 | Each | 11200.00 | 7200.00 | 7200.00 | 10500.00 | 10500.00 | 10000.00 | 10000.00 | 10500.00 | 10500.00 | 5500.00 | 5500.00 | 4234.00 | 4234.00 | 4234.00 | VOID FIRE CONSULTANTS
56.00 | Providing & fixing of MS cabinet to enclose fire brigade connection inlet and draw out connection fabricated from MS sheet 2mm thick with 2mm thick MS sheet frame with full front glass door and locking arrangement duly painted with one coat of primer and two or more coats of synthetic enamel paint of approved make and shade as required as per specifications. | 3.00 | Set | 10000.00 | 15000.00 | 45000.00 | 9400.00 | 28200.00 | 12000.00 | 36000.00 | 9500.00 | 28500.00 | 2200.00 | 6600.00 | 3942.00 | 11826.00 | 6600.00 | FAIRDEAL ASSOCIATES
57.00 | Constructing masonry chamber 90x90x100cm inside designation brick work in cement mortar 1:5 (1 cement : 5 fine sand) and RCC top slab 1:2:4 mix (1 cement : 2 coarse sand : 4 graded stone aggregate 20mm nominal size), necessary excavation, foundation concrete 1:5:10 mix (1 cement : 5 fine sand:10 grades stone aggregate 40mm nominal size), and inside plastering with cement mortar 1:3 (1cement : 3 coarse sand), 12mm thick finished with a floating coat of neat cement, including providing and fixing CI medium duty manhole cover with frame of 560 mm internal dia complete as per standard design with FPS bricks | 2.00 | Each | 15000.00 | 15600.00 | 31200.00 | 14000.00 | 28000.00 | 16000.00 | 32000.00 | 7500.00 | 15000.00 | 5400.00 | 10800.00 | 10950.00 | 21900.00 | 10800.00 | FAIRDEAL ASSOCIATES
58.00 | Supply and fixing air vessel made of 250 mm dia, 8 mm thick MS sheet, 1200 mm in height with air release valve on top and flanged connection to riser, drain arrangement with 25mm dia valve, with all required accessories, pressure gauge and painting with synthetic enamel paint of approved shade as required as per specifications. | 1.00 | Each | 49500.00 | 25000.00 | 25000.00 | 46500.00 | 46500.00 | 45000.00 | 45000.00 | 45000.00 | 45000.00 | 8500.00 | 8500.00 | 20440.00 | 20440.00 | 8500.00 | FAIRDEAL ASSOCIATES
59.00 | Supply, Installation, Testing & Commissioning of fire hydrant panel, cubicle type body made out of 2mm thick CRCA sheet,totally enclosed, IP 42, floor/wall mounted with channel base frame, dust and vermin proof, indoor, compartmentalised, suitable for operation on 3 phase and neutral, 415 V, 50Hz AC system with extensible busbars on both sides, making interlocking arrangement between incomers breakers, including control wiring with 2.5 sq mm size wires/cable and control MCBs of 2A rating, interconnection, duly powder coated painting etc. including supply & installation of following switchgears,metering instruments and accessories as per specifications.
60.00 | INCOMER
61.00 | 2 Nos. 250 Amp four pole Moulded Case Circuit Breaker (Ics value 35 KA) Icu=100% of Ics with built in microprocessor based release unit with adjustable setting with interlocking between two incomers (2 lock & 1 key).
62.00 | INSTRUMENTS
63.00 | Digital Ammeter & Voltmeter, Class 1 for 3 phase as per specifications. - 2 Nos. each
64.00 | 2 Sets of RYB phase indicating lamps controlled by 2 amp MCB (Line Side) and ON/OFF LED indicator
65.00 | BUSBARS
66.00 | 400 Amp TPN busbars of high conductivity electrolytic quality aluminium alloy
67.00 | OUTGOING
68.00 | a. 2 Nos. 160 amps TP MCCB, 35 KA (Ics=100% Icu) with inbuilt thermal based release single phase preventer complete with all accessories with Star delta starters of suitable rating for out going feeders to Main Hydrant pump motor. The compartment shall contain suitable rating analogue type ammeter with CTs and indicating lamp with MCBs for `ON'/OFF`TRIP' status of motor including control wiring as per specifications.
69.00 | b. 1 Nos. 63 amps TP MCCB, 35 KA (Ics=100% Icu) with inbuilt thermal based release with single phase preventer complete with all accessories along with DOL/Star-Delta starter as applicable for out going feeders to Jockey pump motor.The compartment shall contain suitable rating analogue type ammeter with CTs and indicating lamp with MCBs for `ON'/OFF`TRIP' status of motor including control wiring as per specifications..
70.00 | c. 1No. 100 amps TP MCCB,35 KA (Ics=100% Icu) - Spare (with compartment size equal suitable for housing DOL starter)
71.00 | All MCCBs shall be provided with spreader links and rotary handle suitable accessories. | 1.00 | Set | 455500.00 | 175000.00 | 175000.00 | 428000.00 | 428000.00 | 500000.00 | 500000.00 | 650000.00 | 650000.00 | 248000.00 | 248000.00 | 325000.00 | 325000.00 | 175000.00 | M/S JAYSHWAL ENTERPRISES
72.00 | Power cable, Control cable and cable tray with all accessories Supply of following XLPE insulated and PVC sheathed armoured Power Cable of 1.1KV grade, confirming to IS 7098, Part-I 1988 with up to date amendments and confirming to technical specifications. (The outer sheath shall be FRLS.)
73.00 | 3.5 C x 70 Sq. mm Aluminum conductor. | 60.00 | Metre | 805.00 | 620.00 | 37200.00 | 750.00 | 45000.00 | 900.00 | 54000.00 | 750.00 | 45000.00 | 52.00 | 3120.00 | 652.00 | 39120.00 | 3120.00 | FAIRDEAL ASSOCIATES
74.00 | 3.5 C x 50 Sq. mm Aluminum conductor. | 50.00 | Metre | 597.00 | 535.00 | 26750.00 | 550.00 | 27500.00 | 600.00 | 30000.00 | 600.00 | 30000.00 | 209.00 | 10450.00 | 480.00 | 24000.00 | 10450.00 | FAIRDEAL ASSOCIATES
75.00 | 4 C x 16 Sq. mm Aluminum conductor. | 40.00 | Metre | 297.00 | 350.00 | 14000.00 | 275.00 | 11000.00 | 350.00 | 14000.00 | 350.00 | 14000.00 | 285.00 | 11400.00 | 260.00 | 10400.00 | 10400.00 | VOID FIRE CONSULTANTS
76.00 | Supply of following PVC insulated FRLS copper conductor cable for Voltage upto 1100 Volts conforming to IS-694:1990 of following size:
77.00 | 3 C x 2.5 Sq.mm (For Motor Space Heater) | 30.00 | Metre | 130.00 | 280.00 | 8400.00 | 120.00 | 3600.00 | 150.00 | 4500.00 | 500.00 | 15000.00 | 155.00 | 4650.00 | 362.00 | 10860.00 | 3600.00 | CENTRE TAP ENGINEERING
78.00 | 2C x 1.5 Sq. mm | 60.00 | Metre | 57.00 | 120.00 | 7200.00 | 55.00 | 3300.00 | 70.00 | 4200.00 | 300.00 | 18000.00 | 78.00 | 4680.00 | 195.00 | 11700.00 | 3300.00 | CENTRE TAP ENGINEERING
79.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of Upto 35 sq. mm (clamped with 1mm thick saddle) on wall surface as required. | 220.00 | Metre | 50.00 | 100.00 | 22000.00 | 48.00 | 10560.00 | 60.00 | 13200.00 | 160.00 | 35200.00 | 360.00 | 79200.00 | 51.00 | 11220.00 | 10560.00 | CENTRE TAP ENGINEERING
80.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
81.00 | 3.5C x 70 Sq. mm | 4.00 | Each | 578.00 | 1550.00 | 6200.00 | 550.00 | 2200.00 | 750.00 | 3000.00 | 500.00 | 2000.00 | 810.00 | 3240.00 | 730.00 | 2920.00 | 2000.00 | J.K.DEFENCE FIRE ENGG. SERVICES
82.00 | 3.5C x 50 Sq.mm | 2.00 | Each | 515.00 | 1250.00 | 2500.00 | 500.00 | 1000.00 | 650.00 | 1300.00 | 400.00 | 800.00 | 590.00 | 1180.00 | 584.00 | 1168.00 | 800.00 | J.K.DEFENCE FIRE ENGG. SERVICES
83.00 | 4C x 16 Sq.mm | 4.00 | Each | 338.00 | 1000.00 | 4000.00 | 320.00 | 1280.00 | 550.00 | 2200.00 | 300.00 | 1200.00 | 360.00 | 1440.00 | 438.00 | 1752.00 | 1200.00 | J.K.DEFENCE FIRE ENGG. SERVICES
84.00 | Providing and fixing 6 SWG dia G.I. wire on surface or in recess for loop earthing along with existing surface/ recessed conduit/submain wiring/ cable as required. | 200.00 | Metre | 37.00 | 200.00 | 40000.00 | 32.00 | 6400.00 | 50.00 | 10000.00 | 145.00 | 29000.00 | 62.00 | 12400.00 | 39.50 | 7900.00 | 6400.00 | CENTRE TAP ENGINEERING
85.00 | Supplying and installing following size of perforated Hot Dipped Galvanised Iron cable tray (Galvanisation thickness not less than 50 microns) with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with G.I. suspenders including G.I. bolts & nuts, etc. as required.
86.00 | 150 mm width X 50 mm depth X 1.6 mm thickness | 40.00 | Metre | 843.00 | 950.00 | 38000.00 | 800.00 | 32000.00 | 1050.00 | 42000.00 | 550.00 | 22000.00 | 750.00 | 30000.00 | 460.00 | 18400.00 | 18400.00 | VOID FIRE CONSULTANTS
87.00 | Earthing with G.I. earth plate 600 mm X 600 mm X 6 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with charcoal/ coke and salt as required. | 2.00 | Lot | 6347.00 | 25600.00 | 51200.00 | 6000.00 | 12000.00 | 9500.00 | 19000.00 | 12500.00 | 25000.00 | 9500.00 | 19000.00 | 13870.00 | 27740.00 | 12000.00 | CENTRE TAP ENGINEERING
88.00 | Providing and fixing 25 mm X 5 mm GI strip in 40 mm dia G.I. pipe from earth electrode including connection with brass nut, bolt, spring, washer excavation and re-filling etc. as required. | 20.00 | Metre | 626.00 | 1250.00 | 25000.00 | 600.00 | 12000.00 | 750.00 | 15000.00 | 250.00 | 5000.00 | 325.00 | 6500.00 | 577.00 | 11540.00 | 5000.00 | J.K.DEFENCE FIRE ENGG. SERVICES
89.00 | Providing and fixing 25 mm X 5 mm GI strip on surface or in recess for connections etc. as required. | 40.00 | Metre | 201.00 | 800.00 | 32000.00 | 190.00 | 7600.00 | 250.00 | 10000.00 | 220.00 | 8800.00 | 125.00 | 5000.00 | 189.00 | 7560.00 | 5000.00 | FAIRDEAL ASSOCIATES
90.00 | Required Civil & Structural Work & Misclenious work Required Structural Support/ Scaffolding & Accessories, MS fabricated for instalation of all the Hydrant & Sprinkler system. | 1.00 | Lot | 150000.00 | 1000000.00 | 1000000.00 | 140000.00 | 140000.00 | 200000.00 | 200000.00 | 200000.00 | 200000.00 | 8500.00 | 8500.00 | 450000.00 | 450000.00 | 8500.00 | FAIRDEAL ASSOCIATES
91.00 | Required Earth Cutting & back filling. | 280.00 | CuM | 350.00 | 250.00 | 70000.00 | 320.00 | 89600.00 | 500.00 | 140000.00 | 400.00 | 112000.00 | 280.00 | 78400.00 | 511.00 | 143080.00 | 70000.00 | M/S JAYSHWAL ENTERPRISES
92.00 | Hydro testing for all the pipe lines as per specification. | 1.00 | lot | 50000.00 | 300000.00 | 300000.00 | 47000.00 | 47000.00 | 100000.00 | 100000.00 | 75000.00 | 75000.00 | 150.00 | 150.00 | 43800.00 | 43800.00 | 150.00 | FAIRDEAL ASSOCIATES
93.00 | Supply & fixing of Hume Pipe, DN300 Class NP-3 Flush Joint Rainforcement Pipe excluding earth cutting. | 50.00 | Metre | 1500.00 | 850.00 | 42500.00 | 1400.00 | 70000.00 | 1400.00 | 70000.00 | 1200.00 | 60000.00 | 530.00 | 26500.00 | 890.00 | 44500.00 | 26500.00 | FAIRDEAL ASSOCIATES
94.00 | Advisory, consultancy & all required formalities to collect NOC for Fire from Statutory Authority. | 1.00 | Job | 300000.00 | 400000.00 | 400000.00 | 282000.00 | 282000.00 | 350000.00 | 350000.00 | 300000.00 | 300000.00 | 9500.00 | 9500.00 | 650000.00 | 650000.00 | 9500.00 | FAIRDEAL ASSOCIATES
95.00 | Fire Extinguishers Supply & installation of following ISI Marked Fire Extinguishers for Terminal building, DG Room & Admin Building.
96.00 | 6 Kg DCP type Fire Extinguishers | 20.00 | Each | 2615.00 | 1750.00 | 35000.00 | 2450.00 | 49000.00 | 2800.00 | 56000.00 | 2200.00 | 44000.00 | 2530.00 | 50600.00 | 1788.00 | 35760.00 | 35000.00 | M/S JAYSHWAL ENTERPRISES
97.00 | 9 Kg DCP type Fire Extinguishers | 8.00 | Each | 3565.00 | 2500.00 | 20000.00 | 3350.00 | 26800.00 | 3800.00 | 30400.00 | 2500.00 | 20000.00 | 2950.00 | 23600.00 | 2370.00 | 18960.00 | 18960.00 | VOID FIRE CONSULTANTS
98.00 | 2 Kg CO2 type Fire Extinguishers | 10.00 | Each | 3000.00 | 3500.00 | 35000.00 | 2800.00 | 28000.00 | 3800.00 | 38000.00 | 4000.00 | 40000.00 | 3705.00 | 37050.00 | 4635.00 | 46350.00 | 28000.00 | CENTRE TAP ENGINEERING
99.00 | 4.5 Kg CO2 type Fire Extinguishers | 34.00 | Each | 6500.00 | 4400.00 | 149600.00 | 6100.00 | 207400.00 | 6500.00 | 221000.00 | 7000.00 | 238000.00 | 4800.00 | 163200.00 | 5657.00 | 192338.00 | 149600.00 | M/S JAYSHWAL ENTERPRISES
100.00 | 9 Kg CO2 type Fire Extinguishers (Trolley Mounted) | 4.00 | Each | 10000.00 | 12500.00 | 50000.00 | 9400.00 | 37600.00 | 11500.00 | 46000.00 | 12500.00 | 50000.00 | 12350.00 | 49400.00 | 11095.00 | 44380.00 | 37600.00 | CENTRE TAP ENGINEERING
101.00 | RRL Delivery hose (30 meters) with gunmetal coupling | 20.00 | Each | 8000.00 | 8500.00 | 170000.00 | 7500.00 | 150000.00 | 10000.00 | 200000.00 | 9500.00 | 190000.00 | 6900.00 | 138000.00 | 7735.00 | 154700.00 | 138000.00 | FAIRDEAL ASSOCIATES
102.00 | Canvas Delivery hose (30 meters) | 10.00 | Each | 7000.00 | 8500.00 | 85000.00 | 6500.00 | 65000.00 | 9000.00 | 90000.00 | 12500.00 | 125000.00 | 6750.00 | 67500.00 | 4234.00 | 42340.00 | 42340.00 | VOID FIRE CONSULTANTS
103.00 | 25mm Branch and Nozzle (Ordinary branch) | 10.00 | Each | 1500.00 | 2500.00 | 25000.00 | 1400.00 | 14000.00 | 1800.00 | 18000.00 | 3000.00 | 30000.00 | 1600.00 | 16000.00 | 5184.00 | 51840.00 | 14000.00 | CENTRE TAP ENGINEERING
104.00 | 12.5mm Branch and Nozzle (Ordinary branch) | 10.00 | Each | 1000.00 | 2000.00 | 20000.00 | 950.00 | 9500.00 | 1500.00 | 15000.00 | 3500.00 | 35000.00 | 1200.00 | 12000.00 | 2920.00 | 29200.00 | 9500.00 | CENTRE TAP ENGINEERING
105.00 | Rubber washer for hydrant outlet 63mm | 100.00 | Each | 100.00 | 150.00 | 15000.00 | 90.00 | 9000.00 | 70.00 | 7000.00 | 150.00 | 15000.00 | 280.00 | 28000.00 | 95.00 | 9500.00 | 7000.00 | Modern Agencies
106.00 | Fire Alarm Panel SITC of of UL listed & FM approved Addressable Multisensor detector with Standardbase having inbuit isolator. Model no OH921 + DB11E or equivalent. | 50.00 | Nos | 2279.00 | 2450.00 | 122500.00 | 2150.00 | 107500.00 | 2500.00 | 125000.00 | 7500.00 | 375000.00 | 2400.00 | 120000.00 | 3504.00 | 175200.00 | 107500.00 | CENTRE TAP ENGINEERING
107.00 | Supply,Installation,Testing & Commissioning of UL listed & FM approved addressable Monitor module with inbuilt fault isolator. | 7.00 | Nos | 3770.00 | 5500.00 | 38500.00 | 3550.00 | 24850.00 | 4000.00 | 28000.00 | 4250.00 | 29750.00 | 3200.00 | 22400.00 | 3430.00 | 24010.00 | 22400.00 | FAIRDEAL ASSOCIATES
108.00 | Supply,Installation,Testing & Commissioning of Manual Call Point. | 3.00 | Nos | 2294.00 | 6500.00 | 19500.00 | 2150.00 | 6450.00 | 3000.00 | 9000.00 | 5000.00 | 15000.00 | 3675.00 | 11025.00 | 5320.00 | 15960.00 | 6450.00 | CENTRE TAP ENGINEERING
109.00 | Supply and laying of 2C x 1.5 sq mm Fire alarm armoured cable. | 50.00 | Meter | 114.00 | 110.00 | 5500.00 | 105.00 | 5250.00 | 130.00 | 6500.00 | 150.00 | 7500.00 | 85.00 | 4250.00 | 116.00 | 5800.00 | 4250.00 | FAIRDEAL ASSOCIATES
110.00 | Graphics modification and Recommissioning of existing addressable Fire Alarm Panel. | 1.00 | Job | 8346.00 | 185000.00 | 185000.00 | 7850.00 | 7850.00 | 50000.00 | 50000.00 | 300000.00 | 300000.00 | 150000.00 | 150000.00 | 125000.00 | 125000.00 | 7850.00 | CENTRE TAP ENGINEERING
111.00 | B. WATER TRANSFER SYSTEM Dewatering of water from the existing sump and cleaning of surface with agencies own arrangement as required for SITC of New Pump Motor Sets in sump. | 1.00 | Job | 15254.00 | 65000.00 | 65000.00 | 14250.00 | 14250.00 | 18000.00 | 18000.00 | 50000.00 | 50000.00 | 41500.00 | 41500.00 | 23000.00 | 23000.00 | 14250.00 | CENTRE TAP ENGINEERING
112.00 | Making C.C foundation with necessary steel tod for installation of 3 nos. mono submersible pump motor sets. | 3.27 | CFT | 2585.00 | 5000.00 | 16350.00 | 2450.00 | 8011.50 | 3500.00 | 11445.00 | 12500.00 | 40875.00 | 12000.00 | 39240.00 | 10950.00 | 35806.50 | 8011.50 | CENTRE TAP ENGINEERING
113.00 | SITC of Mono Submersible Pump motor set of 5HP/3.7 KW, 2900 RPM, 3Phase, 415 Volt +/- 10% having 65/50 mm dia. Suction delivery of discharging capacity 400 LPM on 30 mtr, Head. | 3.00 | Set | 36898.00 | 52600.00 | 157800.00 | 34600.00 | 103800.00 | 45000.00 | 135000.00 | 65000.00 | 195000.00 | 79000.00 | 237000.00 | 52560.00 | 157680.00 | 103800.00 | CENTRE TAP ENGINEERING
114.00 | Supply & Fixing following Gun Metal Valve as required.
115.00 | 50mm dia (Horizontal) NRV. | 3.00 | Each | 4193.00 | 3000.00 | 9000.00 | 3900.00 | 11700.00 | 4500.00 | 13500.00 | 12500.00 | 37500.00 | 4800.00 | 14400.00 | 4950.00 | 14850.00 | 9000.00 | M/S JAYSHWAL ENTERPRISES
116.00 | 80mm dia (H) Gate Value. | 3.00 | Each | 5687.00 | 8500.00 | 25500.00 | 5300.00 | 15900.00 | 6500.00 | 19500.00 | 15000.00 | 45000.00 | 4500.00 | 13500.00 | 13165.00 | 39495.00 | 13500.00 | FAIRDEAL ASSOCIATES
117.00 | Supply & Fixing following G.I. Pipes:
118.00 | 50mm dia. | 15.00 | Metre | 549.00 | 793.00 | 11895.00 | 520.00 | 7800.00 | 750.00 | 11250.00 | 750.00 | 11250.00 | 450.00 | 6750.00 | 945.00 | 14175.00 | 6750.00 | FAIRDEAL ASSOCIATES
119.00 | 80mm dia. | 13.00 | Metre | 830.00 | 1194.00 | 15522.00 | 780.00 | 10140.00 | 1000.00 | 13000.00 | 900.00 | 11700.00 | 750.00 | 9750.00 | 1498.00 | 19474.00 | 9750.00 | FAIRDEAL ASSOCIATES
120.00 | Supply & Fixing following G.I. Fittings as required.
121.00 | 50mm X 300mm long G.I. Niple. | 6.00 | Each | 357.00 | 250.00 | 1500.00 | 330.00 | 1980.00 | 450.00 | 2700.00 | 1000.00 | 6000.00 | 1200.00 | 7200.00 | 219.00 | 1314.00 | 1314.00 | VOID FIRE CONSULTANTS
122.00 | 80mm X 150mm long G.I. Niple. | 3.00 | Each | 156.00 | 350.00 | 1050.00 | 150.00 | 450.00 | 300.00 | 900.00 | 1200.00 | 3600.00 | 1600.00 | 4800.00 | 160.00 | 480.00 | 450.00 | CENTRE TAP ENGINEERING
123.00 | 50mm dia Elbow. | 3.00 | Each | 252.00 | 250.00 | 750.00 | 230.00 | 690.00 | 350.00 | 1050.00 | 500.00 | 1500.00 | 85.00 | 255.00 | 146.00 | 438.00 | 255.00 | FAIRDEAL ASSOCIATES
124.00 | 50mm dia Socket. | 4.00 | Each | 200.00 | 260.00 | 1040.00 | 200.00 | 800.00 | 300.00 | 1200.00 | 200.00 | 800.00 | 85.00 | 340.00 | 205.00 | 820.00 | 340.00 | FAIRDEAL ASSOCIATES
125.00 | 50mm dia Tee. | 2.00 | Each | 379.00 | 450.00 | 900.00 | 350.00 | 700.00 | 500.00 | 1000.00 | 700.00 | 1400.00 | 510.00 | 1020.00 | 220.00 | 440.00 | 440.00 | VOID FIRE CONSULTANTS
126.00 | 50mm dia Union. | 3.00 | Each | 450.00 | 600.00 | 1800.00 | 420.00 | 1260.00 | 575.00 | 1725.00 | 650.00 | 1950.00 | 710.00 | 2130.00 | 250.00 | 750.00 | 750.00 | VOID FIRE CONSULTANTS
127.00 | 50mm dia Flang with rubber sheet and nut bolts. | 4.00 | Pair | 754.00 | 150.00 | 600.00 | 700.00 | 2800.00 | 850.00 | 3400.00 | 1000.00 | 4000.00 | 560.00 | 2240.00 | 450.00 | 1800.00 | 600.00 | M/S JAYSHWAL ENTERPRISES
128.00 | 80mm dia Elbow. | 3.00 | Each | 409.00 | 200.00 | 600.00 | 400.00 | 1200.00 | 550.00 | 1650.00 | 700.00 | 2100.00 | 170.00 | 510.00 | 275.00 | 825.00 | 510.00 | FAIRDEAL ASSOCIATES
129.00 | 80mm dia Flange with rubber sheet and nut bolts. | 3.00 | Pair | 765.00 | 600.00 | 1800.00 | 720.00 | 2160.00 | 900.00 | 2700.00 | 1200.00 | 3600.00 | 590.00 | 1770.00 | 525.00 | 1575.00 | 1575.00 | VOID FIRE CONSULTANTS
130.00 | Supply & fixing of 150mm dia 4Ft. Long G.I. /M.D. Header assembly with support of 3" X 3" X 5 mm M.S. angle iron frame and clamp. | 1.00 | Job | 7437.00 | 5000.00 | 5000.00 | 7000.00 | 7000.00 | 11000.00 | 11000.00 | 3500.00 | 3500.00 | 2800.00 | 2800.00 | 5870.00 | 5870.00 | 2800.00 | FAIRDEAL ASSOCIATES
131.00 | Supply & fixing of following accessories:-
132.00 | 3" G.I. Socket. | 3.00 | Each | 471.00 | 450.00 | 1350.00 | 350.00 | 1050.00 | 650.00 | 1950.00 | 500.00 | 1500.00 | 325.00 | 975.00 | 250.00 | 750.00 | 750.00 | VOID FIRE CONSULTANTS
133.00 | 1/2" G.I. Socket. | 1.00 | Each | 25.00 | 200.00 | 200.00 | 150.00 | 150.00 | 100.00 | 100.00 | 100.00 | 100.00 | 28.00 | 28.00 | 73.00 | 73.00 | 28.00 | FAIRDEAL ASSOCIATES
134.00 | 2" G.I. Socket. | 1.00 | Each | 206.00 | 300.00 | 300.00 | 200.00 | 200.00 | 300.00 | 300.00 | 300.00 | 300.00 | 235.00 | 235.00 | 220.00 | 220.00 | 200.00 | CENTRE TAP ENGINEERING
135.00 | Supply & fixing of Pressure Meter alongwith Fullway (GM) Valve, Niple, Bush etc as required. | 1.00 | Item | 2069.00 | 1500.00 | 1500.00 | 1900.00 | 1900.00 | 4000.00 | 4000.00 | 10000.00 | 10000.00 | 3800.00 | 3800.00 | 1305.00 | 1305.00 | 1305.00 | VOID FIRE CONSULTANTS
136.00 | Supply & fixing of 10mm dia PVC insulated Steel Rope alongwith necessary 'U' bolts for lifting /lowering the Pump Motor Sets in the Sump as required. | 30.00 | Metre | 150.00 | 200.00 | 6000.00 | 140.00 | 4200.00 | 250.00 | 7500.00 | 150.00 | 4500.00 | 115.00 | 3450.00 | 1985.00 | 59550.00 | 3450.00 | FAIRDEAL ASSOCIATES
137.00 | Supply & fixing of PVC insulated 3 core copper flat cable of 4 Sq.mm. for 5 HP Submersible Pump Motor Sets. | 50.00 | Metre | 200.00 | 250.00 | 12500.00 | 180.00 | 9000.00 | 300.00 | 15000.00 | 300.00 | 15000.00 | 360.00 | 18000.00 | 750.00 | 37500.00 | 9000.00 | CENTRE TAP ENGINEERING
138.00 | Supply & fixing of End Socket as above. | 2.00 | Set | 121.00 | 200.00 | 400.00 | 115.00 | 230.00 | 150.00 | 300.00 | 1000.00 | 2000.00 | 65.00 | 130.00 | 1460.00 | 2920.00 | 130.00 | FAIRDEAL ASSOCIATES
139.00 | SITC of water pump Qubical type 250mm deep wall mounted control panel body made out of 2mm thick CRCA sheet ,totally enclosed, IP 42, floor/wall mounted with channel base frame, dust and vermin proof, indoor, compartmentalised, suitable for operation on 3 phase and neutral, 415 V, 50Hz AC system, making interlocking arrangement between incomers breakers, including control wiring with 2.5 sq mm size wires/cable and control MCBs of 2A rating, interconnection, duly powder coated painting etc. board of 14 SWA CRCA (CPRI approved) sheet having 100 Amp Copper Bus Bar (4 Nos.) Digital type Amp/Volt Meter, Sliding fuse with R-Y-B Indication Lamp , should be 7 tank process etc. including supply & installation of following switchgears,metering instruments and accessories as per specifications.
140.00 | Following electrical accessories should be arranged in the above panel board:
141.00 | INCOMER
142.00 | 2 Nos. 63 Amp,25 KA (Ics= 100% Icu) four pole Moulded Case Circuit Breaker with Spreader Link (As in concern)
143.00 | BUS-COUPLER
144.00 | 1 Nos. 63 Amp,35 KA,(Ics=100% Icu) four pole Moulded Case Circuit Breaker with spreader link (As in concern) with built in microprocessor based release unit with adjustable setting.Electrical & Mechanical Interlocking provision to be provided between 2 Incomers & Bus-Coupler.
145.00 | Instrument
146.00 | Digital Ammeter & Voltmeter, Class 1 for 3 phase as per specifications. - 2 Nos each. 3 Sets of RYB phase indicating lamps controlled by 2 amp MCB (Line Side) and ON/OFF LED indicator
147.00 | Bus Bar
148.00 | 100 Amp TPN busbars of high conductivity Copper
149.00 | Outgoing
150.00 | a) 5 HP DOL, 3 phase Starter, indicating lamp with MCBs for `ON'/OFF,`TRIP' status of motor including control wiring as per specifications - 3 nos.
151.00 | b) 32 Amp 4 Pole MCB=4 Nos.
152.00 | c) 32 Amp 2 Pole MCB.=2 Nos.
153.00 | Motor-Pump set Dry run preventer - For all the Pumps. | 1.00 | Set | 190500.00 | 55000.00 | 55000.00 | 170000.00 | 170000.00 | 225000.00 | 225000.00 | 100000.00 | 100000.00 | 77500.00 | 77500.00 | 350000.00 | 350000.00 | 55000.00 | M/S JAYSHWAL ENTERPRISES
154.00 | Painting of the existing delivery pipe line for water transfer system and accessories with approved quality paints over two coat of anti corrosive red oxide. | 1.00 | Job | 1068.00 | 100000.00 | 100000.00 | 1000.00 | 1000.00 | 1200.00 | 1200.00 | 50000.00 | 50000.00 | 6800.00 | 6800.00 | 87600.00 | 87600.00 | 1000.00 | CENTRE TAP ENGINEERING
155.00 | Supply of Aqueous Film Forming Foam (AFFF) at 6% concentrate used in MFT as fire suppressant to extinguish flammable fires. | 700.00 | Ltr. | 110.00 | 105.00 | 73500.00 | 100.00 | 70000.00 | 120.00 | 84000.00 | 150.00 | 105000.00 | 850.00 | 595000.00 | 104.00 | 72800.00 | 70000.00 | CENTRE TAP ENGINEERING
156.00 | Supply and fixing of fire safety related signs glow in dark PU polymer Board with backside adhesive tape having multicolour graphics printing with superior lamination for durable performance which are as follows.
157.00 | Emergency Escape Route Plan having size 36” x 48” | 6.00 | Lot | 8640.00 | 6000.00 | 36000.00 | 8000.00 | 48000.00 | 10000.00 | 60000.00 | 2000.00 | 12000.00 | 7150.00 | 42900.00 | 2675.00 | 16050.00 | 12000.00 | J.K.DEFENCE FIRE ENGG. SERVICES
158.00 | Emergency Escape Route Plan having size 24” x 36” | 8.00 | Lot | 4320.00 | 5000.00 | 40000.00 | 4000.00 | 32000.00 | 4500.00 | 36000.00 | 1500.00 | 12000.00 | 4225.00 | 33800.00 | 4876.00 | 39008.00 | 12000.00 | J.K.DEFENCE FIRE ENGG. SERVICES
159.00 | Glow in Dark Photoluminescent double sided board with Chans, ring & hooks 6” X 16” | 10.00 | Lot | 768.00 | 3500.00 | 35000.00 | 700.00 | 7000.00 | 1000.00 | 10000.00 | 1000.00 | 10000.00 | 780.00 | 7800.00 | 1090.00 | 10900.00 | 7000.00 | CENTRE TAP ENGINEERING
160.00 | Glow in Dark Photoluminescent double sided board with Chans, ring & hooks 12” X 36” | 4.00 | Lot | 3456.00 | 4000.00 | 16000.00 | 3200.00 | 12800.00 | 3800.00 | 15200.00 | 2500.00 | 10000.00 | 2860.00 | 11440.00 | 4718.00 | 18872.00 | 10000.00 | J.K.DEFENCE FIRE ENGG. SERVICES
161.00 | Glow in Dark Photoluminescent double sided board with Chans, ring & hooks 6” X 6” | 20.00 | Lot | 288.00 | 3000.00 | 60000.00 | 250.00 | 5000.00 | 400.00 | 8000.00 | 1000.00 | 20000.00 | 350.00 | 7000.00 | 810.00 | 16200.00 | 5000.00 | CENTRE TAP ENGINEERING
162.00 | Glow in Dark Photoluminescent double sided board with Chans, ring & hooks 12” X 12” | 10.00 | Lot | 1152.00 | 4000.00 | 40000.00 | 1000.00 | 10000.00 | 1250.00 | 12500.00 | 1500.00 | 15000.00 | 1200.00 | 12000.00 | 1670.00 | 16700.00 | 10000.00 | CENTRE TAP ENGINEERING
163.00 | Glow in Dark Photoluminescent single sided board with Chans, ring & hooks – 6” x 16 “ | 8.00 | Lot | 480.00 | 3500.00 | 28000.00 | 400.00 | 3200.00 | 650.00 | 5200.00 | 1800.00 | 14400.00 | 950.00 | 7600.00 | 1190.00 | 9520.00 | 3200.00 | CENTRE TAP ENGINEERING
164.00 | Glow in Dark Photoluminescent single sided board with Chans, ring & hooks – 12” x 36 “ | 6.00 | Lot | 2160.00 | 4000.00 | 24000.00 | 2000.00 | 12000.00 | 3300.00 | 19800.00 | 2200.00 | 13200.00 | 2950.00 | 17700.00 | 2330.00 | 13980.00 | 12000.00 | CENTRE TAP ENGINEERING
165.00 | Glow in Dark Photoluminescent single sided board with Chans, ring & hooks – 6” x 6 “ | 12.00 | Lot | 180.00 | 3000.00 | 36000.00 | 180.00 | 2160.00 | 300.00 | 3600.00 | 1000.00 | 12000.00 | 600.00 | 7200.00 | 810.00 | 9720.00 | 2160.00 | CENTRE TAP ENGINEERING
166.00 | Glow in Dark Photoluminescent single sided board with Chans, ring & hooks – 12” x 12 “ | 8.00 | Lot | 720.00 | 4000.00 | 32000.00 | 650.00 | 5200.00 | 850.00 | 6800.00 | 1500.00 | 12000.00 | 1400.00 | 11200.00 | 940.00 | 7520.00 | 5200.00 | CENTRE TAP ENGINEERING
167.00 | Glow in Dark Photoluminescent Lift Safety (FD30) having size 12"X12" | 5.00 | Lot | 576.00 | 4000.00 | 20000.00 | 500.00 | 2500.00 | 850.00 | 4250.00 | 1800.00 | 9000.00 | 1500.00 | 7500.00 | 940.00 | 4700.00 | 2500.00 | CENTRE TAP ENGINEERING
168.00 | Glow in Dark Photoluminescent Self Adhesive tapes & edges Markers – 3”x 10 mtr. Roll | 7.00 | Lot | 2430.00 | 7000.00 | 49000.00 | 2250.00 | 15750.00 | 3000.00 | 21000.00 | 4000.00 | 28000.00 | 1350.00 | 9450.00 | 3650.00 | 25550.00 | 9450.00 | FAIRDEAL ASSOCIATES
169.00 | Glow in Dark Photoluminescent Self Adhesive tapes & edges Markers – 4”x 10 mtr. Roll | 5.00 | Lot | 3240.00 | 7500.00 | 37500.00 | 3000.00 | 15000.00 | 3500.00 | 17500.00 | 5500.00 | 27500.00 | 1950.00 | 9750.00 | 4850.00 | 24250.00 | 9750.00 | FAIRDEAL ASSOCIATES
170.00 | Emergency Exit lighting System celing suspended unit acrylic itched type self contained rechargeable emergency exit sign system powered by non maintainable LEDs having size of the Facia 12"x6". | 10.00 | Lot | 3960.00 | 12500.00 | 125000.00 | 3700.00 | 37000.00 | 4500.00 | 45000.00 | 6500.00 | 65000.00 | 3000.00 | 30000.00 | 4380.00 | 43800.00 | 30000.00 | FAIRDEAL ASSOCIATES
171.00 | Glow in dark shock resuscitation chart – WE JUMBO 11, WE JUMBO 12 & WE JUMBO 13 having size 24"x36" | 4.00 | Lot | 3456.00 | 25000.00 | 100000.00 | 3200.00 | 12800.00 | 4500.00 | 18000.00 | 2500.00 | 10000.00 | 2500.00 | 10000.00 | 4870.00 | 19480.00 | 10000.00 | J.K.DEFENCE FIRE ENGG. SERVICES, FAIRDEAL ASSOCIATES
172.00 | Glow in dark Information Sign Board – FHS 12 size 36"x48" | 16.00 | Lot | 2965.00 | 3000.00 | 48000.00 | 2800.00 | 44800.00 | 3500.00 | 56000.00 | 2500.00 | 40000.00 | 7800.00 | 124800.00 | 9606.00 | 153696.00 | 40000.00 | J.K.DEFENCE FIRE ENGG. SERVICES
173.00 | Glow in dark Information Sign Board – FHS 12 size 48"x72" | 10.00 | Lot | 3953.00 | 4500.00 | 45000.00 | 3500.00 | 35000.00 | 5000.00 | 50000.00 | 3000.00 | 30000.00 | 8500.00 | 85000.00 | 20000.00 | 200000.00 | 30000.00 | J.K.DEFENCE FIRE ENGG. SERVICES
174.00 | Supply of stainless steel portable twin type trolly for carrying different type (ABC/DCP/Co2) type fire extinguisher. | 10.00 | Each | 12427.00 | 12000.00 | 120000.00 | 11700.00 | 117000.00 | 16000.00 | 160000.00 | 12000.00 | 120000.00 | 2600.00 | 26000.00 | 18250.00 | 182500.00 | 26000.00 | FAIRDEAL ASSOCIATES
175.00 | Supply of stainless steel portable trolly for carrying different type (ABC/DCP/Co2) type fire extinguisher. | 25.00 | Each | 7460.00 | 12000.00 | 300000.00 | 7000.00 | 175000.00 | 10000.00 | 250000.00 | 7500.00 | 187500.00 | 2600.00 | 65000.00 | 18250.00 | 456250.00 | 65000.00 | FAIRDEAL ASSOCIATES
| Total in Figures |  |  |  |  | 14790207.00 |  | 14566621.50 |  | 16618520.00 |  | 14978675.00 |  | 11580034.00 |  | 14487128.50
Lowest Amount Quoted BY: FAIRDEAL ASSOCIATES(11580034.00)

## BOQ Summary
BOQ Summary Details Tender Title: Provision of Fire Fighting System and augmentation / re-orientation of water supply system at Bagdogra Airport. Tender ID: 2025_AAI_232514_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | FAIRDEAL ASSOCIATES (BID ID -848919) | 11580034.00 | L1
| 2 | VOID FIRE CONSULTANTS (BID ID -847182) | 14487128.50 | L2
| 3 | CENTRE TAP ENGINEERING (BID ID -847216) | 14566621.50 | L3
| 4 | M/S JAYSHWAL ENTERPRISES (BID ID -845724) | 14790207.00 | L4
| 5 | J.K.DEFENCE FIRE ENGG. SERVICES (BID ID -846909) | 14978675.00 | L5
| 6 | Modern Agencies (BID ID -847247) | 16618520.00 | L6