## BoQ1
Government eProcurement System Created By: RAVI KUMAR VANKUDOTHU Created Date/Time: 21-May-2025 03:54 PM Tender Title: SITC OF 11/33 KV Transformer for the Integration of Existing 1MWp Solar power plant with the upcoming 33KV Power Supply System at Rajahmundry Airport Tender ID: 2025_AAI_232927_1
Tender Inviting Authority: SENIOR MANAGER (ENGG-ELECT), AIRPORTS AUTHORITY OF INDIA, RAJAHMUNDRY AIRPORT, RAJAHMUNDRY
Name of Work:Construction of New Domestic Terminal Building and Miscellaneous Works at Rajahmundry Airport, Sub-Head: SITC OF 11/33 Kv Transformer for the Integration of Existing 1MWp Solar power plant with the upcoming 33KV Power Supply System.
Tender ID No: 2025_AAI_232927_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | DOSHI ELECTRIC ENGG. CO. (GSTN-24AAEFD3355K1ZI) BID ID -848518 |  | SARASWAT ENGINEERING SERVICES (GSTN-27AAZFS6239C1ZO) BID ID -848667 |  | Awasthi Electric Works (GSTN-09ABAPA1866D1Z5) BID ID -849227 |  | Power Star (GSTN-NA) BID ID -848117
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | SITC of Transformer SITC of Transformer Supply, Installation, Testing and Commissioning of 1250 kVA, 11kV/33KV 3 Ph, 50 Hz, ONAN cooled, vector Dd0/DY11 Transformer connected Delta on HV side and Delta/Star on LV side as per site requirement with Off Load Tapp Changer in steps of +/- 2.5%, +5% & -10%, with radiator cooling fins, Conservator tank, bucholtz relay, winding temperature & oil temperature alarm and trip, mercury switch contacts, first fill of oil, HV cable box suitable for termination of HT XLPE cable and complete with all standard fittings and accessories etc as required complete and as per specifications attached in all respects as required and necessary control cabling for alarm, tripping & indication with 2.5 mm2 armoured copper cable as required. Voltage Ratio: 11/33 kV Type of Winding: Copper Fittings: Standard fittings as per IS:2026/77. | 1.00 | No. |  | 2300000.00 | 2300000.00 | 1884786.00 | 1884786.00 | 2165000.00 | 2165000.00 | 1382400.00 | 1382400.00 | 1382400.00 | Power Star
2.00 | HT CABLES AND CABLING Supply of stranded compact circular aluminium conductor, conductors screen with extruded semi conducting compound, XLPE insulated, insulation screening with extruded semi conducting compound in combination with copper tape, cores laid up, innersheath of PVC, galvanised steel flat strip armoured, and overall PVC sheathed cable of size 3 Core X 240 Sqmm confirming to IS 7098 (part-II)2011 as required with up to date amendments. | 30.00 | Meter |  | 2000.00 | 60000.00 | 3572.00 | 107160.00 | 3150.00 | 94500.00 | 2220.00 | 66600.00 | 60000.00 | DOSHI ELECTRIC ENGG. CO.
3.00 | Laying of one number PVC insulated and PVC sheathed I XLPE power cable of 11 kV grade of size above 120 sq. mm and upto 400 sq. mm direct in ground including excavation, sand cushioning,protective covering and refilling the trench etc. as required. | 150.00 | Meter |  | 400.00 | 60000.00 | 755.00 | 113250.00 | 450.00 | 67500.00 | 1900.00 | 285000.00 | 60000.00 | DOSHI ELECTRIC ENGG. CO.
4.00 | Laying of one number PVC insulated and PVC sheathed I XLPE power cable of 33 kV grade of size above 120 sq. mm and upto 400 sq. mm in the existing masonry open duct as required. | 30.00 | Meter |  | 100.00 | 3000.00 | 172.00 | 5160.00 | 80.00 | 2400.00 | 5000.00 | 150000.00 | 2400.00 | Awasthi Electric Works
5.00 | supplying and making indoor cable end termination with heat shrinkable jointing kit complete with all accessories including lugs suitable for size of 3 core 300 sq. mm XLPE aluminium conductor cable of 11 kV grade as required: | 2.00 | Set |  | 7650.00 | 15300.00 | 6063.00 | 12126.00 | 12000.00 | 24000.00 | 2000.00 | 4000.00 | 4000.00 | Power Star
6.00 | supplying and making indoor cable end termination with heat shrinkable jointing kit complete with all accessories including lugs suitable for size of 3 core 240 sq. mm XLPE aluminium conductor cable of 33 kV grade as required: | 2.00 | Set |  | 9000.00 | 18000.00 | 12378.00 | 24756.00 | 16000.00 | 32000.00 | 6000.00 | 12000.00 | 12000.00 | Power Star
7.00 | Earthing Earthing with Copper earth plate 600mm x 600mm x 3 mm thick including accessories, and providing 300x300x450(H) mm RCC earth pit chamber suitable to receive 6mm thick MS chequered plate with handle,strengthening & compaction of soil below the earth pit chamber including providing suitable ratio PCC, providing & laying positional cement concrete (1:2:4) of depth 100mm surrounding the earth pit chamber covering surface area of 1 Sqmtr,including providing and fixing of reducer water funnel with wire mesh arrangement for watering etc. with charcoal/coke and salt as required. | 4.00 | Set |  | 18000.00 | 72000.00 | 24514.00 | 98056.00 | 20000.00 | 80000.00 | 100000.00 | 400000.00 | 72000.00 | DOSHI ELECTRIC ENGG. CO.
8.00 | Supplying and laying 25 mm X 5 mm copper strip at 0.50 metre below ground as strip earth electrode, including connection/ terminating with nut, bolt, spring, washer etc. as required. (Jointing shall be done by overlapping and with 2 Sets of brass nut bolt & spring washer spaced at 50mm) | 16.00 | meters |  | 1100.00 | 17600.00 | 1488.00 | 23808.00 | 1350.00 | 21600.00 | 6250.00 | 100000.00 | 17600.00 | DOSHI ELECTRIC ENGG. CO.
9.00 | Providing· and fixing 25 mm X 5 mm· Copper strip in 40 mm dia G.l. pipe from earth electrode including connection with G.l. nut, bolt, spring, washer excavation and refilling etc. as required. | 24.00 | meters |  | 1500.00 | 36000.00 | 2101.00 | 50424.00 | 1650.00 | 39600.00 | 6250.00 | 150000.00 | 36000.00 | DOSHI ELECTRIC ENGG. CO.
10.00 | Providing and fixing 25 mm X 5 mm copper. strip on surface or in recess in Existing G.I pipe/Hume Pipe/ Open Trench for connections etc. as required | 40.00 | meters |  | 1000.00 | 40000.00 | 1371.00 | 54840.00 | 1250.00 | 50000.00 | 6250.00 | 250000.00 | 40000.00 | DOSHI ELECTRIC ENGG. CO.
| Total in Figures |  |  |  |  | 2621900.00 |  | 2374366.00 |  | 2576600.00 |  | 2800000.00
Lowest Amount Quoted BY: SARASWAT ENGINEERING SERVICES(2374366.00)

## BOQ Summary
BOQ Summary Details Tender Title: SITC OF 11/33 KV Transformer for the Integration of Existing 1MWp Solar power plant with the upcoming 33KV Power Supply System at Rajahmundry Airport Tender ID: 2025_AAI_232927_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | SARASWAT ENGINEERING SERVICES (BID ID -848667) | 2374366.00 | L1
| 2 | Awasthi Electric Works (BID ID -849227) | 2576600.00 | L2
| 3 | DOSHI ELECTRIC ENGG. CO. (BID ID -848518) | 2621900.00 | L3
| 4 | Power Star (BID ID -848117) | 2800000.00 | L4