## BoQ1
Government eProcurement System Created By: KUMAR RIJENDRA Created Date/Time: 22-May-2025 01:13 PM Tender Title: Reconfiguration of existing terminal building B M Airport Ranchi. SH- Fire Alarm and Fire Fighting system. Tender ID: 2025_AAI_233035_1
Tender Inviting Authority: SM (E-E), AAI, B.M.Airport, Ranchi
Name of Work: Reconfiguration of existing terminal building B M Airport Ranchi. SH:- Fire Alarm and Fire Fighting system.
Contract No: 2025_AAI_233035_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | VOID FIRE CONSULTANTS (GSTN-NA) BID ID -849168
[5 empty] | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Designing of Fire detection and alarm system, wet riser and sprinkler System for the reconfiguration of Terminal building including preparation and submission of shop drawings, as-built drawings submission of NOC from state fire deptartment / regulatory authority etc. as per latest IS and NBC standards. | 1.00 | Job | 51510.00 | 50000.00 | 50000.00 | 50000.00 | VOID FIRE CONSULTANTS
2.00 | Supplying, installation, testing and commissioning of two loop micro processor based intelligent addressable fire alarm panel, central processing unit with the following loop modules and capable of supporting not less than 240 devices (including detectors) and minimum 120 detectors per loop and loop length up to 2 km, network communication card, minimum 320 character graphics/ LCD display with touch screen or other keypad and minimum 4000 events history log in the non volatile memory (EPROM), power supply unit (230 ± 5% V, 50 hz), 48 hrs back-up with 24 volt sealed maintenance free batteries with automatic charger. The panel shall have facility to connect printer to printout log and facility to have seamless integration with analog/digital voice evacuation system (which is part of the schedule of work under SH: PA System) and shall be complete with all accessories .The panel shall be compatible for BMS system with open protocol BACnet/ Modbus over IP complete as per specification etc as required. | 1.00 | Job | 141910.00 | 300000.00 | 300000.00 | 300000.00 | VOID FIRE CONSULTANTS
3.00 | Supply, Installation, Testing & commissioning of UL / EN listed intelligent addressable multi criteria detector with inbuilt fault isolator / isolator base with visible LED suitable for 2 wires loop connection, complete with plug into common separate base & housing complete with connections etc. and to be fixed below / above false ceiling roof and concealed space with necessary support complete as required and as per direction of Engineer in charge. | 78.00 | Nos. | 2843.00 | 2550.00 | 198900.00 | 198900.00 | VOID FIRE CONSULTANTS
4.00 | Supply, Installation, Testing & commissioning of UL / EN listed intelligent addressable Manual call station suitable for semi flush mounting, IP 54, with inbuilt fault isolator / isolator module including the word Fire appearing on the front with connections etc. complete as required and as per direction of Engineer in charge. | 5.00 | Nos. | 6655.00 | 3902.00 | 19510.00 | 19510.00 | VOID FIRE CONSULTANTS
5.00 | Supply, installation, testing and commissioning of UL / EN listed addressable Hooter-cum-strobe with inbuilt fault isolator / isolator module with adjustable sound level complete with termination etc.and to be fixed at wall/ surface etc. complete as required and as per direction of Engineer in charge. | 5.00 | Nos. | 3606.00 | 5393.00 | 26965.00 | 26965.00 | VOID FIRE CONSULTANTS
6.00 | Supplying, installation, testing & commissioning of UL / EN listed Response Indicator i/c Mounting Boxes installed on surface/ recessed having two LED complete with all connections with termination/ connection etc.and to be fixed at wall/ surface etc. complete as required and as per direction of Engineer in charge. | 32.00 | Nos. | 113.00 | 367.00 | 11744.00 | 11744.00 | VOID FIRE CONSULTANTS
7.00 | Providing, installation, testing & commissioning of UL / EN listed addressable Monitor Module (input module) complete with connection/ interconnection etc complete as required and as per direction of Engineer in charge. | 5.00 | Nos. | 2668.00 | 3270.00 | 16350.00 | 16350.00 | VOID FIRE CONSULTANTS
8.00 | Providing, installation, testing & commissioning of UL / EN listed addressable Control Module / Relay Module (output module) complete with connection/ interconnection etc complete as required and as per direction of Engineer in charge. | 5.00 | Nos. | 3142.00 | 3270.00 | 16350.00 | 16350.00 | VOID FIRE CONSULTANTS
9.00 | Supplying of 2Cx1.5 sqmm fire survival armoured cable, 600/1000V rated with annealed copper conductor having glass mica fire barrier tape covered by XLPE Insulation and LSZH inner bedding, steel wire armouring & LSZH outer sheath etc complete as required and as per direction of Engineer in charge. | 3000.00 | Mtrs. | 196.00 | 230.00 | 690000.00 | 690000.00 | VOID FIRE CONSULTANTS
10.00 | Laying of 2Cx1.5 sqmm fire survival armoured cable, 600/1000V rated in the existing surface / wall with suitable GI saddle complete as required and as per direction of Engineer in charge. | 3000.00 | Mtrs. | 52.00 | 46.00 | 138000.00 | 138000.00 | VOID FIRE CONSULTANTS
11.00 | Supply and fixing of metal junction box for mounting of detectors / devices complete with connections etc. as required and as per direction of Engineer in charge. | 78.00 | Nos. | 185.00 | 122.00 | 9516.00 | 9516.00 | VOID FIRE CONSULTANTS
12.00 | Providing, fixing, testing & commissioning of 15mm dia size suitable for sustaining the seat & water hammer effect, quartzoid bulb type sprinklers (UL, FM approved) of rating 68 degree centigrade with required accessories :
12.01 | Side wall Sprinkler | 5.00 | Each | 515.00 | 474.00 | 2370.00 | 2370.00 | VOID FIRE CONSULTANTS
12.02 | Horizontal side wall sprinkler | 10.00 | Each | 515.00 | 390.00 | 3900.00 | 3900.00 | VOID FIRE CONSULTANTS
12.03 | Concealed sprinkler | 50.00 | Each | 515.00 | 995.00 | 49750.00 | 49750.00 | VOID FIRE CONSULTANTS
12.04 | Upright Sprinkler | 50.00 | Each | 402.00 | 390.00 | 19500.00 | 19500.00 | VOID FIRE CONSULTANTS
13.00 | Supplying, installation, testing & commissioning of sprinkler flexible pipe (UL Listed) of stainless steel complete with 15 NPT on reducer thread with maximum working pressure of 175 PSI test pressure of 875 PSI (Burst) with branch line (Inlet) 25mm NPT male thread to sprinkler head (Outlet) 15mm NPT female thread with reducer, nipple, 2 side brackets, center bracket, stockbar of following sizes complete as required. a)1200 mm | 50.00 | Set | 1494.00 | 864.00 | 43200.00 | 43200.00 | VOID FIRE CONSULTANTS
14.00 | Providing, laying, testing & commissioning of 'C' class heavy duty MS pipe conforming to IS 3589/IS 1239 including Welding, fittings like elbows, tees, flanges, tapers, nuts bolts, gaskets etc. and fixing the pipe on the wall/ceiling with suitable clamp/support frame and painting with two or more coats of synthetic enamel paint of required shade complete as required:
14.01 | 25 mm dia | 200.00 | Mtrs. | 587.00 | 380.00 | 76000.00 | 76000.00 | VOID FIRE CONSULTANTS
14.02 | 32 mm dia | 100.00 | Mtrs. | 690.00 | 496.00 | 49600.00 | 49600.00 | VOID FIRE CONSULTANTS
14.03 | 40 mm dia | 100.00 | Mtrs. | 793.00 | 727.00 | 72700.00 | 72700.00 | VOID FIRE CONSULTANTS
14.04 | 50 mm dia | 150.00 | Mtrs. | 1020.00 | 780.00 | 117000.00 | 117000.00 | VOID FIRE CONSULTANTS
14.05 | 65 mm dia | 150.00 | Mtrs. | 1174.00 | 996.00 | 149400.00 | 149400.00 | VOID FIRE CONSULTANTS
14.06 | 80 mm dia | 250.00 | Mtrs. | 1411.00 | 1102.00 | 275500.00 | 275500.00 | VOID FIRE CONSULTANTS
14.07 | 100 mm dia | 220.00 | Mtrs. | 1926.00 | 1570.00 | 345400.00 | 345400.00 | VOID FIRE CONSULTANTS
14.08 | 150 mm dia | 870.00 | Mtrs. | 2823.00 | 2355.00 | 2048850.00 | 2048850.00 | VOID FIRE CONSULTANTS
15.00 | Supplying, fixing, testing and commissioning of butterfly valve of PN 1.6 rating with bronze/gunmetal seat duly ISI marked complete with nuts, bolts, washers, gaskets conforming to IS 13095 of following sizes as required :
15.01 | 80 mm dia | 10.00 | Nos. | 3997.00 | 3666.00 | 36660.00 | 36660.00 | VOID FIRE CONSULTANTS
15.02 | 100 mm dia | 10.00 | Nos. | 5347.00 | 4833.00 | 48330.00 | 48330.00 | VOID FIRE CONSULTANTS
15.03 | 150 mm dia | 5.00 | Nos. | 9231.00 | 6932.00 | 34660.00 | 34660.00 | VOID FIRE CONSULTANTS
16.00 | Providing, installation, testing and commissioning of CI dual plate non return valve PN 16 of following sizes confirming to complete with rubber gasket, GI bolt, nuts,washers etc. as required.
16.01 | 100 mm dia | 3.00 | Nos. | 10302.00 | 5050.00 | 15150.00 | 15150.00 | VOID FIRE CONSULTANTS
16.02 | 150 mm dia | 3.00 | Nos. | 15453.00 | 8268.00 | 24804.00 | 24804.00 | VOID FIRE CONSULTANTS
17.00 | Providing & fixing of Stainless Steel double flange suction " Y" type strainer fabricated out of minimum 1.2 mm thick Stainless Steel sheet with 3 mm dia. perforation holes including nuts, bolts and 3 mm thick rubber insertion complete & tested to 16 Kg/Sq.cm pressure complete as required and as per enclosed specification. 150 mm dia. | 4.00 | Nos. | 21140.00 | 14936.00 | 59744.00 | 59744.00 | VOID FIRE CONSULTANTS
18.00 | Providing & fixing of 25mm dia. gunmetal air release valve with all fittings and forged ball valve on header complete as required and as per enclosed specification. | 4.00 | Nos. | 3606.00 | 1071.00 | 4284.00 | 4284.00 | VOID FIRE CONSULTANTS
19.00 | Providing & fixing of installation control valve (Sprinkler Alarm Valve) of Cast iron body and bronze working parts comprising of water motor alarm, bronze seat clapper and clapper arm, hydraulically driven mechanical gong bell to sound continuous alarm when the Wet riser/Sprinkler system activates, pressure gauges, emergency releases ,strainer, pressure switch, cock valve complete with drain valve and bypass, test control box,ball valves, flanges, orifice plate, fittings, gasket etc.suitable for 150 mm diameter pipe size complete as required as per enclosed specification. | 1.00 | Nos. | 49079.00 | 56600.00 | 56600.00 | 56600.00 | VOID FIRE CONSULTANTS
20.00 | Supplying and fixing single headed internal hydrant valve with instantaneous Gunmetal/Stainless Steel coupling of 63 mm dia with cast iron wheel ISI marked conforming to IS 5290 (Type -A) with blank Gunmetal/Stainless Steel cap and chain as required :Single headed.Gunmetal | 4.00 | Nos. | 10302.00 | 12087.00 | 48348.00 | 48348.00 | VOID FIRE CONSULTANTS
21.00 | Supplying & fixing 63 mm dia gun metal short branch pipe with 20 mm nominal internal diameter size nozzle conforming to IS 903 suitable for instantaneous connection to interconnect hose pipe coupling as required :Gun metal | 4.00 | Nos. | 3091.00 | 3366.00 | 13464.00 | 13464.00 | VOID FIRE CONSULTANTS
22.00 | Supplying and fixing 63 mm dia, 15 m long RRL hose pipe with 63 mm dia male and female couplings duly bound with GI wire, rivets etc. conforming to IS 636 (type-A) as required :Gun Metal | 8.00 | Nos. | 10302.00 | 5585.00 | 44680.00 | 44680.00 | VOID FIRE CONSULTANTS
23.00 | Supplying and fixing of Double door MS hose cabinet of size not less than 0.9 x 0.6 x 0.5 mtr made out of MS sheet 2mm thick suitable to accommodate hydrant with valve, 2 nos 15mtr. long hose pipe, 1 no. branch pipe, etc having central opening and 6 mm thick glazed glass doors (02 nos) suitably marked on the outside with the letter"FIRE" i/c necessary locking arrangement, mounting legs / concrete pedestal and duly painted with one coat of primer and two coats of synthetic enamel paint of post office red shade complete as required. | 4.00 | Nos. | 6696.00 | 10710.00 | 42840.00 | 42840.00 | VOID FIRE CONSULTANTS
24.00 | Supply, installation , testing and commissioning of pressure gauge of 150 mm dia with syphon tubing, mounting accessories,0-21 kg/ sq.cm range with 15 mm dia stop cock valve, piping etc as required. | 4.00 | Nos. | 1494.00 | 2127.00 | 8508.00 | 8508.00 | VOID FIRE CONSULTANTS
25.00 | Demolishing cement concrete manually/ by mechanical means including disposal of material within 50 metres lead as per direction of Engineer - in - charge. | 10.00 | Cum | 1030.00 | 2295.00 | 22950.00 | 22950.00 | VOID FIRE CONSULTANTS
26.00 | Cutting of existing MS pipe (upto 150 mm dia) for testing and connecting temporary dummy joint in the existing fire hydrant line various location at terminal building and rejointing MS pipe with the help of Welding, fittings like elbows, tees, flanges, tapers, nuts bolts, gaskets etc. as required and as per direction of Engineer in charge. | 5.00 | Job | 2060.00 | 23715.00 | 118575.00 | 118575.00 | VOID FIRE CONSULTANTS
27.00 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering - All work up to plinth level: 1:2:4 (1 Cement : 2 coarse sand (zone-III) derived from natural sources : 4 graded stone aggregate 20 mm nominal size derived from natural sources) | 10.00 | Cum | 1545.00 | 11169.00 | 111690.00 | 111690.00 | VOID FIRE CONSULTANTS
28.00 | Dismantaling the existing MS pipe ( upto 150 mm dia) & stored at AAI store as per direction of EIC. | 50.00 | Mtrs. | 618.00 | 398.00 | 19900.00 | 19900.00 | VOID FIRE CONSULTANTS
29.00 | Providing and fixing reinforced neoprene rubber vibration eliminators/expansion joints (to provide relief from stresses at pipe flanges) suitable for upto 20 kg/cm2 pressure, complete as per specification.
29.01 | 150mm dia. | 2.00 | Each | 9952.00 | 15600.00 | 31200.00 | 31200.00 | VOID FIRE CONSULTANTS
29.02 | 100mm dia. | 2.00 | Each | 7685.00 | 12500.00 | 25000.00 | 25000.00 | VOID FIRE CONSULTANTS
| Total in Figures |  |  |  |  | 5497892.00
Lowest Amount Quoted BY: VOID FIRE CONSULTANTS(5497892.00)

## BOQ Summary
BOQ Summary Details Tender Title: Reconfiguration of existing terminal building B M Airport Ranchi. SH- Fire Alarm and Fire Fighting system. Tender ID: 2025_AAI_233035_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | VOID FIRE CONSULTANTS (BID ID -849168) | 5497892.00 | L1