## BoQ1
Government eProcurement System Created By: RISHI RAJ BAGRE Created Date/Time: 11-Jun-2025 02:08 PM Tender Title: Replacement Of Apron Flood Light Old LT Feeder Panel and Provision of Airfield Lighting Control and Monitoring System ALCMS at Dehradun Airport Tender ID: 2025_AAI_234100_1
Tender Inviting Authority: Assistant General Manager (Engg.-Elect.), AAI, Dehradun Airport.
Name of Work: Replacement Of Apron flood light Old LT Feeder Panel & Provision of Airfield Lighting Control & Monitoring System (ALCMS) at Dehradun airport.
Contract No:
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | NASU SYSTEMS (GSTN-27ABAPS2566G1ZK) BID ID -852184 |  | Techno Electricals (GSTN-24AAGFT9086M1ZG) BID ID -856734 |  | SAURABH ENTERPRISES (GSTN-NA) BID ID -856646
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
0.00 | Electrical Works
1.00 | Supply, Installation, Testing & commissioning(SITC) of cubicle type totally enclosed free standing, dust & vermin proof and water proof (IP-55) outdoor double door type feeder pillar (openable on front & back) of suitable size suitable for 415 V, 3 Phase, 4 wire 50 Hz AC supply system fabricated out of 2mm thick CRCA sheet duly powder coated of approved shade,3mm thick detachable gland plates at bottom including angle iron frame work at bottom with legs of minimum 600 mm height made out of 75x75x5 mm MS angle iron including all civil works like excavation, PCC, brick work pedestal, plastering, refilling etc including dismentling of existing panel as required. The control wiring shall be of minimum 2.5 sq mm size FRLS , PVC insulated and feeder pillar shall have the following switch gears as per the approved drawing. INCOMER 2 Nos-160A,25KA, 4 pole motorized MCCB ( Ics=Icu=100%) with thermal release & adjustable O/L setting 0.8-1.0xln and RYB, ON,OFF & trip indicator with 2A control MCB. Each incommer shall be provided with Digital Ammeter & Voltmeter i/c selector switch for phase selection. BUSCOUPLER 1 No-160A,25KA, 4 pole motorized MCCB( Ics=Icu=100%) with auxillary contact (NO/NC) for auto ON/OFF operation and ON & Trip indicator with control MCB Busbar 1 Set of 160 Amp(Minimum) TPN busbars of high conductivity electrolytic grade aluminium with heat shrinkable colour sleeves & DMC/SMC supports Outgoing 2 Nos-160A,25KA, 4 pole MCCB( Ics=Icu=100%) with thermal release & adjustable O/L setting 0.8-1.0xln and ON,OFF & trip indicator with 2A control MCB 2 sets.-16A 4P, 10KA MCB, 24Hrs astronomical time switch & 4 pole contactor with O/L protection and ON/Trip indication with 2 A protection SP o/g MCB for 5nos aviation light. 10 nos- 32 Amp, 4P, 10KA MCB with 32A TP power contactor operating on 230 VAC coil having O/L relay and 2NO/2NC aux.contacts for the automatic switching of luminaries with illuminated push buttons for local ON/OFF operation & selector switch for Local/ Remote operation. Other Accessories 1. Each motorized MCCB shall be provided with TNC switch. 2. O/G MCCB shall be provided with extended rotory handle & 3. There shall be electrical & mechanical interlocking between incommers & bus coupler with Local & Remote operation selctor switch. 4. 50x6 mm AL common Earth & any other accessories etc as required. 5. Incomming of 3.5x185 sqmm and outgoing cables of size 4x25sq mm connectors/ terminations. 6. Control wiring shall be done with minimum 2.5 sqmm copper FRLS flexible wire. 7. Space heaters with suitable control & protion system shall be provided and any other item as required to complete the job. 8. Control logic for operation of breakers shall be finallized while approval of SLD/GAD . | 2.00 | Job | 0.00 | 250000.00 | 500000.00 | 275000.00 | 550000.00 | 490000.00 | 980000.00 | 500000.00 | NASU SYSTEMS
2.00 | Supply, Installation, Testing & Commissioning of indoor type LT Panel cubicle type, made out of 2 mm thick CRCA sheet and 3 mm thick gland plate with top/bottom cable entry as per site requirement, 100x50 x5 mm suitable MS channels frame in the bottom/ legs for grouting etc totally enclosed IP 42, free standing, floor mounting, dust and vermin proof, indoor, compartmentalized with concealed hinged lockable doors, suitable for operation on 3 phase, 415 V, 50Hz AC system with TPN busbars including internal control wiring with minimum 2.5 sqmm size FRLS PVC insulated flexible wires/cable, interconnection, duly powder coated painting etc. as per technical specifications including following switchgears, metering instruments and accessories in the Panel as per the approved drawing. 1) Incommer & Outgoing : 160A 4 P 35KA MCCB( Ics=Icu=100%) with thermal-megnetic release and RYB , ON,OFF, trip indicator with 2A control MCB. Incomer shall be provided with digital multifunction, suitable rating CT & 3 ph. Voltmeter control MCB per phase - 02 nos 2) ATS: 160A, 4P, 415 V Automatic Transfer switch with manual override facility- 02 nos. 3) Other Accessories: 1) Control wiring , suitable TPN Busbar , Auto/ Manual Selctor switch, Bypass arrangement & control logic as per approved SLD. 2) Suitable cable connectors, phase spreader, extended rotory handle etc and any other item required to complet the job. 3) Control logic for operation of breakers shall be finallized while approval of SLD/GAD . | 1.00 | Job | 0.00 | 150000.00 | 150000.00 | 200000.00 | 200000.00 | 450000.00 | 450000.00 | 150000.00 | NASU SYSTEMS
3.00 | Supplying, Installation, Testing & Commissioning of 20 KVA on-line UPS,IGBT based Hi Frequency PWM (Pulse Width Modulation) level 3, conforming to IEC EN 62040-3 standards with three phase AC input voltage 380 V to 480 V, 50 Hz+5% and three phase AC output voltage 415 V + 1%, 50Hz+0.25 Hz, with 30 Minutes battery backup using SMF (Sealed Maintainence Free) batteries with batteries stand including uninyvin copper conductor flexible cable of suitable size from Battery bank to UPS along with suitable capacity DC MCCB for battery isolation. It shall be housed in suitable rugged enclosure aesthetically finished duly Pre treated and powder coated. Digital Metering, Monitoring, Protection, Features & performance parameters shall be as per OEM & tender specifications. | 2.00 | Job | 0.00 | 400000.00 | 800000.00 | 750000.00 | 1500000.00 | 500000.00 | 1000000.00 | 800000.00 | NASU SYSTEMS
4.00 | Supply & laying (in GI flexible conduit) of 1X6 Sq. mm, 1.1KV grade, FRLSH PVC insulated, copper conductor flexible cable conforming to IS:694 with up to date ammendments for interconnection from I/p panel to UPS and UPS to O/p panel including terminations as required. | 100.00 | Mtr | 0.00 | 150.00 | 15000.00 | 325.00 | 32500.00 | 110.00 | 11000.00 | 11000.00 | SAURABH ENTERPRISES
5.00 | Supply of following Size. XLPE insulated, PVC sheathed, Aluminum/copper conductor armoured power cable of 1.1 KV grade conforming to IS:7098 Part-I with upto date amendment etc. complete as required.
5.10 | 2 core x 1.5 sq. mm (stranded copper conductor) | 200.00 | Mtr | 0.00 | 64.00 | 12800.00 | 275.00 | 55000.00 | 125.00 | 25000.00 | 12800.00 | NASU SYSTEMS
5.20 | 4 core x 25 sq. mm ( Aluminum conductor) | 500.00 | Mtr | 0.00 | 178.00 | 89000.00 | 289.00 | 144500.00 | 225.00 | 112500.00 | 89000.00 | NASU SYSTEMS
6.00 | Supplying of 50 mm size DWC HDPE pipe of AAI Approved make and ISI marked complete as required. | 400.00 | Mtr | 0.00 | 98.00 | 39200.00 | 85.00 | 34000.00 | 150.00 | 60000.00 | 34000.00 | Techno Electricals
7.00 | Laying of 50 mm size DWC HDPE pipe ISI marked along with all accessories like socket, bend, couplers etc. conforming to IS 14930, Part II complete with fitting and cutting, jointing etc.direct in ground (75 cm below ground level) including excavation and refilling the trench but excluding sand cushioning and protective covering etc., complete as required. | 300.00 | Mtr | 0.00 | 30.00 | 9000.00 | 175.00 | 52500.00 | 150.00 | 45000.00 | 9000.00 | NASU SYSTEMS
8.00 | Supplying and making end termination with brass compression gland and Copper/Aluminum lugs for following size of PVC insulated and PVC sheathed / XLPE cable of 1.1 kV grade as required.
8.10 | 3.5 x 240 sq.mm ( Aluminum conductor) | 10.00 | Job | 0.00 | 500.00 | 5000.00 | 900.00 | 9000.00 | 1000.00 | 10000.00 | 5000.00 | NASU SYSTEMS
8.20 | 4 x 25 sq.mm ( Aluminum conductor) | 25.00 | Job | 0.00 | 500.00 | 12500.00 | 550.00 | 13750.00 | 700.00 | 17500.00 | 12500.00 | NASU SYSTEMS
8.30 | 2 core 1.5 sq.mm (stranded copper) | 2.00 | Job | 0.00 | 500.00 | 1000.00 | 550.00 | 1100.00 | 500.00 | 1000.00 | 1000.00 | NASU SYSTEMS, SAURABH ENTERPRISES
9.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/ HUME/ METAL/PVC pipe as required
9.10 | Upto 35 sq. mm | 400.00 | Mtr | 0.00 | 30.00 | 12000.00 | 20.00 | 8000.00 | 50.00 | 20000.00 | 8000.00 | Techno Electricals
9.20 | above 185 sq. mm upto 400 sq mm | 20.00 | Mtr | 0.00 | 30.00 | 600.00 | 65.00 | 1300.00 | 100.00 | 2000.00 | 600.00 | NASU SYSTEMS
10.00 | Earthing with Maintenance free Earthing System. The Rod shall be copper bonded low carbon high tensile steel with 17.2 mm dia. and 10 feet length , UL Listed with molecularly bonded with min. 250 microns coating of 99.90% pure electrolytic grade Copper and tested by CPRI capable of bearing fault current of 25 kA for 1 second with SS 304 Clamp , along with earth enhancement compound in a sealed bag of minimum 30 kg (10 kg Bag x 3) (95% carbon based compound, resistivity is less than 0.12 ohm meter) with Poly Plastic Pit Cover 300x300x195 mm with load Bearing Capacity 5000 kg. ( Job includes Supply, Installation, Testing and Commissioning) | 6.00 | Job | 0.00 | 15000.00 | 90000.00 | 8000.00 | 48000.00 | 15000.00 | 90000.00 | 48000.00 | Techno Electricals
11.00 | Supplying and laying 25 mm X 5 mm copper strip at 0.50 metre below ground as strip earth electrode, including connection/ terminating with nut, bolt, spring, washer etc. as required. (Jointing shall be done by overlapping and with 2 sets of brass nut bolt & spring washer spaced at 50mm) | 30.00 | Mtr | 0.00 | 2800.00 | 84000.00 | 1255.00 | 37650.00 | 1500.00 | 45000.00 | 37650.00 | Techno Electricals
12.00 | Supplying and laying 25 mm X 5 mm G.I strip at 0.50 metre below ground as strip earth electrode, including connection/ terminating with G.I. nut, bolt, spring, washer etc. as required. (Jointing shall be done by overlapping and with 2 sets of G.I. nut bolt & spring washer spaced at 50mm) | 25.00 | Mtr | 0.00 | 1200.00 | 30000.00 | 1255.00 | 31375.00 | 200.00 | 5000.00 | 5000.00 | SAURABH ENTERPRISES
13.00 | Providing and fixing 25 mm X 5 mm copper strip on surface or in recess for connections etc. as required. | 60.00 | Mtr | 0.00 | 2500.00 | 150000.00 | 1255.00 | 75300.00 | 1500.00 | 90000.00 | 75300.00 | Techno Electricals
14.00 | Supply, installation, testing and commissioning of PC/PLC based Touch- Screen LCD type remote control panel cum display unit (Airfield Lighting Control and Monitoring System,ALCMS), type L 890'BB" as per the requirements of FAA Advisory Circular No. AC 150/5345-56B (current edition) and additional circular/ mechanisms/ interfaces at control tower suitable for remote operation of constant current regulators of GLF Circuits, Apron Flood Lights, Landing T and Wind cones etc.and necessary soft integration of existing GLF UPS with ALCMS for monitoring & data logging of UPS status including all hardware's, software's, licenses & other items as required for successful operation of the system inline with the scope of work details of equipments,equipment specifications,performance criteria as conforming to the tender specifications. Two vault processor shall be provided both running in parallel for redundancy in opertaions. The ALCMS shall include industrial type, latest configuration of Computers and IT active & passive devices and on ATC side there shall be two Touch screens( HMI) of minimum size 21.5” and one 32” display unit along with installation arrangement at the existing console at ATC including required modifications and on CCR side there shall be one 32” display unit. On/Off, 5 positions brightness control for CCR controlled GLF circuits, Mimic display system(Monitor units), termination of power/ interfacing cables(OFC/Control ) of following air field lighting systems: a) Rwy Ckt-1 &2 - (30 kW) - 02 nos + 01 Spare b) Apron edge lights & Taxi-A &D (7.5KW) - 01 no.+ 01 spare c) Apron edge lights & Link Taxi-B ( 4KW) - 01 no. d) NTRO Taxi -C( 4 KW ) - 01 no.+ 01 spare e) SAPL Approach-RWY 08 (4 KW) - 01 no. (Expendable for Cat-I approach- 2nos CCRs) f) PAPI Rwy -08 (7.5 KW) -01 no+ 01 Spare. g) Guard Lights (4KW) -01 no. h) Beacons Lights -01 no.+ 01 Spare i) Landing H -01 no. j) WDI (Lights) - 02 nos k) AFL masts lights -11 nos.+ 6 Spare l) Crash bell -01 no m) Siren -01 no n) Fire Approach, Taxi-C, B and Emergency Exit Runway-08 Road Holding Traffic Light- 04 nos. | 1.00 | Job | 0.00 | 1500000.00 | 1500000.00 | 1550000.00 | 1550000.00 | 909888.00 | 909888.00 | 909888.00 | SAURABH ENTERPRISES
15.00 | Supply& laying of 6 core,single mode 9/125 unitube armoured Optical fiber cable as per the IEC/ITU & other relevant standards i/c buffer tube, water swellable yarns, di-electric material, ripcod, steel tap armoured, PE jacket etc complete as required as per site requirement. | 100.00 | Mtr | 0.00 | 80.00 | 8000.00 | 100.00 | 10000.00 | 150.00 | 15000.00 | 8000.00 | NASU SYSTEMS
| Total in Figures |  |  |  |  | 3508100.00 |  | 4353975.00 |  | 3888888.00
Lowest Amount Quoted BY: NASU SYSTEMS(3508100.00)

## BOQ Summary
BOQ Summary Details Tender Title: Replacement Of Apron Flood Light Old LT Feeder Panel and Provision of Airfield Lighting Control and Monitoring System ALCMS at Dehradun Airport Tender ID: 2025_AAI_234100_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | NASU SYSTEMS (BID ID -852184) | 3508100.00 | L1
| 2 | SAURABH ENTERPRISES (BID ID -856646) | 3888888.00 | L2
| 3 | Techno Electricals (BID ID -856734) | 4353975.00 | L3