## BoQ1
Government eProcurement System Created By: VIVEKANAND PRASAD MORIL Created Date/Time: 23-Jun-2025 03:59 PM Tender Title: Provision of lighting wiring and miscellaneous work for Power House Building at Amritsar Airport Tender ID: 2025_AAI_234254_1
Tender Inviting Authority: <Asstt. GM Engg (Elect), Airports Authority of India, Sri Guru Ram Dass Jee, International Airport, Amritsar - 143101>
Name of Work: <Provision of lighting, wiring and miscellaneous work for Power House Building at Amritsar Airport.>
Tender ID: <2025_AAI_234254_1>
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Manish Electricals (GSTN-23ABLPM9012E1ZW) BID ID -853354 |  | Awasthi Electric Works (GSTN-09ABAPA1866D1Z5) BID ID -853606 |  | Anil Kumar Sharma (GSTN-01AIWPS0647K1ZU) BID ID -853607 |  | GVD ENGINEERS & CONTRACTOR (GSTN-NA) BID ID -852652
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply and fixing of fire retardant electrically insulated synthetic mat of class C, 2 mm thick suitable for 11KV AC grade and 240V DC system meeting requirements of IS 15652:2006 tested for breakdown strength, tensile/elongation, aging properties, insulation resistance, effect to acid, alkaline, diesel, transformer oil & leakage current test, fire test etc. having minimum width of 1000 mm ± 20 mm along with all allied materials such as Pu-resin, Chemi bound, special PVC adhesive, liquid primer etc. | 71.00 | Mtr |  | 1250.00 | 88750.00 | 1350.00 | 95850.00 | 800.00 | 56800.00 | 650.00 | 46150.00 | 46150.00 | GVD ENGINEERS & CONTRACTOR
2.00 | Supply and fixing of fire retardant electrically insulated synthetic mat of class A, 2mm thick suitable for all voltages not exceeding 3.3 KV AC and 240V DC system meeting requirements of IS 15652:2006 tested for breakdown strength, tensile/elongation, aging properties, insulation resistance, effect to acid, alkaline, diesel, transformer oil & leakage current test, fire test etc. having minimum width of 1000 mm ±20 mm along with all allied materials such as Pu-resin, Chemi bound, special PVC adhesive, liquid primer etc. in what so ever quantity required to complete the job as per site conditions and as per instructions from Engineer-in-Charge. | 175.00 | Mtr |  | 1500.00 | 262500.00 | 1250.00 | 218750.00 | 1000.00 | 175000.00 | 450.00 | 78750.00 | 78750.00 | GVD ENGINEERS & CONTRACTOR
3.00 | Providing of set of 4 Nos. 9.5 Litre capacity GI bucket painted in post office red colour with prior coat of red oxide paint and written with white paint FIRE and mounted on MS angle iron frame with bracket of appropriate size & capacity i/c filling sand etc. (MS angle iron size 40mm X 40mm X5mm, length 4.6 metre) | 4.00 | EA |  | 3350.00 | 13400.00 | 3200.00 | 12800.00 | 3000.00 | 12000.00 | 8200.00 | 32800.00 | 12000.00 | Anil Kumar Sharma
4.00 | Supply of following sizes of Copper Power Cables,multi stranded conductor, XLPE Insulated, Armoured ,PVC innersheathed,1100V grade as per IS 7098(Part 1) 1988.
4.10 | 3Core X 1.5 Sqmm | 300.00 | Mtr |  | 200.00 | 60000.00 | 120.00 | 36000.00 | 150.00 | 45000.00 | 150.00 | 45000.00 | 36000.00 | Awasthi Electric Works
4.20 | 3Core X 2.5 Sqmm | 200.00 | Mtr |  | 350.00 | 70000.00 | 160.00 | 32000.00 | 290.00 | 58000.00 | 205.00 | 41000.00 | 32000.00 | Awasthi Electric Works
4.30 | 4Core X 4 Sqm | 450.00 | Mtr |  | 550.00 | 247500.00 | 270.00 | 121500.00 | 400.00 | 180000.00 | 360.00 | 162000.00 | 121500.00 | Awasthi Electric Works
4.40 | 4 Core X 6 Sqm | 350.00 | Mtr |  | 700.00 | 245000.00 | 400.00 | 140000.00 | 580.00 | 203000.00 | 460.00 | 161000.00 | 140000.00 | Awasthi Electric Works
5.00 | Supply of 600mm x 600mm recess Mounted LED fixture with high efficiency PMMA diffuser complete with driver and accessories having lumen output not less than 3600 Lumens with luminaire efficacy not less than 100 Lumens / watt, CCT from 3000K to 6500K, suitable for indoor applications complete as per techhncial specificaitons (Similar to Havells make CAT No. VENUSNEO2X2PLR36WLED830POS or equivalent as per list of Approved make). | 100.00 | EA |  | 6210.00 | 621000.00 | 1250.00 | 125000.00 | 3000.00 | 300000.00 | 2250.00 | 225000.00 | 125000.00 | Awasthi Electric Works
6.00 | Supply of LED fitting with LED tube light rating of 20 Watt with heat dissipation capability to create optimum light uniformity with minimum glare. It has a system level lumen output not less than 2000 lumens with luminaire efficacy of not less than 100 lm/W. CCT from 3000K to 6500K, suitable for indoor applications complete as per technical specifications. (Similar to Havells CAT No. ENDURALINEARPROBS20WLED865SPCSSIND or equivalent as per list of Approved make). | 160.00 | EA |  | 1200.00 | 192000.00 | 350.00 | 56000.00 | 500.00 | 80000.00 | 550.00 | 88000.00 | 56000.00 | Awasthi Electric Works
7.00 | Supply of suspended type Industrial bay LED light (70 Watt) comprising of LEDs of approved make with Constant current output driver, It has a system level lumen output not less thanlumens with luminaire efficacy of not less than 100 lm/W, CCT from 3000K to 6500K , suitable for indoor applications complete as per technical specifications. (Similar to Havells CAT No. GAZELLAHBP80WLED857PBOPC or equivalent as per list of Approved make). | 18.00 | EA |  | 7500.00 | 135000.00 | 3500.00 | 63000.00 | 5000.00 | 90000.00 | 6300.00 | 113400.00 | 63000.00 | Awasthi Electric Works
8.00 | Supply of 45 W LED road lighting lumanarie consisting of single piece, integral, grey powder coated high pressure die-cast alminium housing, conecting strip, including power driver should having surge protection upto 8KV complete as required suitable for operation on 230V, 50 Hz AC supply. (Havells ENDURASUNBEAMSL45WLED757SASYTOPC (OR) EQUIVALENT as per list of Approved make). | 20.00 | EA |  | 4340.00 | 86800.00 | 1500.00 | 30000.00 | 3000.00 | 60000.00 | 4300.00 | 86000.00 | 30000.00 | Awasthi Electric Works
9.00 | Supplyof LED decorative post top luminaire (35 Watt)consisting of a high-pressure powder coated die-cast aluminium housing suitable for vertical mounting on decorative pole (BOQ item no. 10) having system lumen output not less than 3500 lumens and system efficacy of not less than 100 lumens per watt ,complete with driver and all accessories suitable for outdoor applications completeasper technical specifications. (Similar to Havells CAT No.VICTORIAPT35WLED757PSYMTOTG or equivalent). | 30.00 | EA |  | 24300.00 | 729000.00 | 6500.00 | 195000.00 | 15000.00 | 450000.00 | 7600.00 | 228000.00 | 195000.00 | Awasthi Electric Works
10.00 | Supply of decorative electric light poles, height 2.7 mtr to 3.00 mtr, constructed from mild steel or aluminum, finishes powder coating or hot-dip galvanization, shapes round or polygonal designs. with suitable bracket for installation of post top luminairet suitable for wind velocity as per IS 875 (but not less than 50 m/sec.), fabricated out of 3 mm MS plate in single section, suitable for installation on a precast foundation with supply of 4 nos. of foundation bolt & anchor plate, rigid flange plate (200x200x12mm min.) welded with the base of pole for fixing on foundation bolts complete as reqd. for structural stability as specified, weather proof and vandal resistant door flush with the exterior surface containing a terminal plate of 5 mm thick backlite sheet with 32 Amp heavy duty connector for loop in loop out cable terminations suitable for upto two numbers 4 core 6 Sq.mm cables & 10A DP MCB for each fixture connections, earthing bolts for continuous earth connection complete as required & as specified.( Suitable for BOQ item no. 9) | 30.00 | EA |  | 15000.00 | 450000.00 | 13500.00 | 405000.00 | 10000.00 | 300000.00 | 22500.00 | 675000.00 | 300000.00 | Anil Kumar Sharma
11.00 | Supply of Single arm standared bracket not less than 500 mm+500 mm with suitable length Each and made of 40 mm dia pipe having suitable nipple of size 32mm dia GI pipe to hold the fittings with tilt angle including in built arrangement for incoming cable termination with 20A 4P connector. complete as required as per EIC for the following Heights. | 20.00 | EA |  | 1500.00 | 30000.00 | 3000.00 | 60000.00 | 1000.00 | 20000.00 | 3300.00 | 66000.00 | 20000.00 | Anil Kumar Sharma
12.00 | Erection of decorative electric light pole with all accessories in reinforced cement concrete 1:3:6 (1 cement : 3 coarse sand : 6 graded stone aggregate 40 mm nominal size) foundation including excavation and refilling including positioning of template & foundation bolts (supplied with pole to match with pole base plate) & providing and fixing of DWC HDPE pipe of size 50 mm dia (2 pieces of min. 0.75 m length) in the foundation for loop-in-loop-out of the cable to the pole complete as required and as specified. (Suitable for BOQ item no. 10) | 30.00 | EA |  | 5000.00 | 150000.00 | 4500.00 | 135000.00 | 3000.00 | 90000.00 | 2000.00 | 60000.00 | 60000.00 | GVD ENGINEERS & CONTRACTOR
13.00 | Installation, testing and commissioning of decorative Post Top light fitting with all accessories on existing decorative Post Top light pole of 2.7 to 3 mtr height with bracket, including supplying and drawing of 3core 1.5 sq.mm. PVC insulated PVC sheathed flexible copper conductor cable from loop-in-loop-out box upto the individual post top light fitting(s), connection etc. complete as required & as specified. | 30.00 | EA |  | 1000.00 | 30000.00 | 250.00 | 7500.00 | 200.00 | 6000.00 | 1100.00 | 33000.00 | 6000.00 | Anil Kumar Sharma
14.00 | Installation of the Single arm standard bracket for street light on roof of building fixing with nut bolt, clamp etc suitable support on wall as required. | 20.00 | EA |  | 250.00 | 5000.00 | 200.00 | 4000.00 | 50.00 | 1000.00 | 800.00 | 16000.00 | 1000.00 | Anil Kumar Sharma
15.00 | Installation, testing and commissioning of pre-wired, fluorescent fitting / compact fluorescent fitting of all types, complete with all accessories and tube etc. directly on ceiling/ wall, including connection with 1.5 sq. mm FRLS PVC insulated, copper conductor, single core cable and earthing etc. as required. | 258.00 | EA |  | 225.00 | 58050.00 | 150.00 | 38700.00 | 50.00 | 12900.00 | 700.00 | 180600.00 | 12900.00 | Anil Kumar Sharma
16.00 | Finishing with Epoxy paint ( two or more coats) at all locations prepared and applied as per manufacturers specifications including appropriate priming coat, preparation of surface, etc. complete on the steel work .Colour of paint shall be decided by the EIC. | 1650.00 | Sqmtr |  | 345.00 | 569250.00 | 260.00 | 429000.00 | 250.00 | 412500.00 | 440.00 | 726000.00 | 412500.00 | Anil Kumar Sharma
17.00 | Lettering with Black Japan paint or other approved colour of approved brand and manufacturer. | 15000.00 | Per letter per cm height |  | 12.00 | 180000.00 | 4.00 | 60000.00 | 5.00 | 75000.00 | 12.00 | 180000.00 | 60000.00 | Awasthi Electric Works
18.00 | Supply, installation, testing and commissioning of double skin construction fan (For Heat Exhaust) sections suitable for outdoor duty. The unit shall be complete with belt driven double inlet double width, backward curved centrifugal fan, squirrel cage induction motor, vibration isolators, canvass connections, belt drive, pulley mounted on motor and fan shaft, belt guard mounted within the housing, The motor shall be suitable for operation on 3 Phase, 415 +/- 10% V, 50 Hz AC supply. Motor shall confirm to IE3 series of energy efficient motors with IP55 degree of protection. Motor rating 5.5 KW | 3.00 | Nos |  | 125000.00 | 375000.00 | 65000.00 | 195000.00 | 100000.00 | 300000.00 | 195000.00 | 585000.00 | 195000.00 | Awasthi Electric Works
19.00 | Supply, installation, balancing and commissioning of fabricated at site GSS sheet metal rectangular/round ducting complete with neoprene rubber gaskets, elbows, splitter dampers, vanes, hangers, supports etc. as per approved drawings and specifications of following sheet thickness complete as required. i) Thickness 0.8mm Sheet | 325.00 | Sqmtr |  | 1500.00 | 487500.00 | 2700.00 | 877500.00 | 1000.00 | 325000.00 | 1340.00 | 435500.00 | 325000.00 | Anil Kumar Sharma
20.00 | Supplying and fixing following way, single pole and neutral, sheet steel, MCB distribution board, 240 V, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCB/RCCB/Isolator)
20.10 | 12 Way ,Double door | 2.00 | EA |  | 3250.00 | 6500.00 | 1600.00 | 3200.00 | 2500.00 | 5000.00 | 8400.00 | 16800.00 | 3200.00 | Awasthi Electric Works
21.00 | Supplying and fixing following way, horizontal type three pole and neutral, sheet steel, MCB distribution board, 415 V, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCB/RCCB/Isolator)
21.10 | 8 way (4+24), double door | 1.00 | EA |  | 5000.00 | 5000.00 | 4200.00 | 4200.00 | 4350.00 | 4350.00 | 12500.00 | 12500.00 | 4200.00 | Awasthi Electric Works
22.00 | Supplying and fixing of following sizes of PVC conduit along with accessories in surface/recess including painting in case of surface conduit, or cutting the wall and making good the same in case of recessed conduit as required.
22.10 | 25 mm Dia Conduit | 750.00 | Mtr |  | 200.00 | 150000.00 | 235.00 | 176250.00 | 150.00 | 112500.00 | 62.00 | 46500.00 | 46500.00 | GVD ENGINEERS & CONTRACTOR
22.20 | 25 mm Junction 2 way | 120.00 | EA |  | 35.00 | 4200.00 | 75.00 | 9000.00 | 20.00 | 2400.00 | 120.00 | 14400.00 | 2400.00 | Anil Kumar Sharma
22.30 | 25 mm Junctin 4 Way | 30.00 | EA |  | 40.00 | 1200.00 | 75.00 | 2250.00 | 20.00 | 600.00 | 150.00 | 4500.00 | 600.00 | Anil Kumar Sharma
22.40 | 32 mm Dia Conduit | 60.00 | Mtr |  | 250.00 | 15000.00 | 300.00 | 18000.00 | 180.00 | 10800.00 | 82.00 | 4920.00 | 4920.00 | GVD ENGINEERS & CONTRACTOR
23.00 | Supplying and fixing following size/ modules, GI box along with modular base & cover plate for modular switches in recess etc as required.
23.10 | 8 Module (125mmX125mm) | 3.00 | EA |  | 600.00 | 1800.00 | 435.00 | 1305.00 | 400.00 | 1200.00 | 950.00 | 2850.00 | 1200.00 | Anil Kumar Sharma
24.00 | Wiring for group controlled (looped) light point (without independent switch etc.) with 1.5 sq. mm FRLS PVC insulated copper conductor single core cable in surface/ recessed steel conduit, and earthing the point with 1.5 sq. mm FRLS PVC insulated copper conductor single core cable etc. as required. | 25.00 | Point |  | 1130.00 | 28250.00 | 875.00 | 21875.00 | 800.00 | 20000.00 | 2100.00 | 52500.00 | 20000.00 | Anil Kumar Sharma
25.00 | Supplying and fixing 5 A to 32 A rating, 240/415 V, 10 kA, "C" curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required.
25.10 | 6A | 12.00 | EA |  | 250.00 | 3000.00 | 200.00 | 2400.00 | 150.00 | 1800.00 | 210.00 | 2520.00 | 1800.00 | Anil Kumar Sharma
25.20 | 16A | 20.00 | EA |  | 300.00 | 6000.00 | 200.00 | 4000.00 | 150.00 | 3000.00 | 245.00 | 4900.00 | 3000.00 | Anil Kumar Sharma
25.30 | 25 A | 4.00 | EA |  | 340.00 | 1360.00 | 200.00 | 800.00 | 150.00 | 600.00 | 275.00 | 1100.00 | 600.00 | Anil Kumar Sharma
26.00 | Supplying and fixing following rating, double pole, 240 V, isolator in the existing MCB DB complete with connections, testing and commissioning etc. as required.
26.10 | 32 A | 2.00 | EA |  | 850.00 | 1700.00 | 350.00 | 700.00 | 500.00 | 1000.00 | 6300.00 | 12600.00 | 700.00 | Awasthi Electric Works
27.00 | Supplying and fixing following rating, four pole, 415 V, isolator in the existing MCB DB complete with connections, testing and commissioning etc. as required.
27.10 | 32 A | 1.00 | EA |  | 1500.00 | 1500.00 | 750.00 | 750.00 | 1000.00 | 1000.00 | 6600.00 | 6600.00 | 750.00 | Awasthi Electric Works
28.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing masonry open duct as required.
28.10 | Up to 35 Sqmm | 75.00 | EA |  | 40.00 | 3000.00 | 25.00 | 1875.00 | 10.00 | 750.00 | 450.00 | 33750.00 | 750.00 | Anil Kumar Sharma
29.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on wall surface as required.
29.10 | Upto 35 sq. mm (clamped with 1mm thick saddle) | 425.00 | Mtr |  | 100.00 | 42500.00 | 80.00 | 34000.00 | 60.00 | 25500.00 | 200.00 | 85000.00 | 25500.00 | Anil Kumar Sharma
30.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size direct in ground including excavation, sand cushioning, protective covering and refilling the trench etc as required. a) Up to 35 sq. mm | 45.00 | Mtr |  | 300.00 | 13500.00 | 350.00 | 15750.00 | 200.00 | 9000.00 | 90.00 | 4050.00 | 4050.00 | GVD ENGINEERS & CONTRACTOR
31.00 | Supplying and fixing following modular switch/ socket on the existing modular plate & switch box including connections but excluding modular plate etc. as required.
31.10 | 5/6 amps switch | 20.00 | EA |  | 175.00 | 3500.00 | 95.00 | 1900.00 | 100.00 | 2000.00 | 430.00 | 8600.00 | 1900.00 | Awasthi Electric Works
31.20 | 15/16 amp switch | 5.00 | EA |  | 265.00 | 1325.00 | 185.00 | 925.00 | 150.00 | 750.00 | 630.00 | 3150.00 | 750.00 | Anil Kumar Sharma
32.00 | Providing and fixing following rating and breaking capacity and pole MCCB in existing cubicle panel board including drilling holes in cubicle panel, making connections, etc. as required.
32.10 | 100 Amp, 18KA, TPMCCB (Similar to 100 A ABB Tmax MCCB) | 1.00 | EA |  | 5430.00 | 5430.00 | 8500.00 | 8500.00 | 4200.00 | 4200.00 | 8300.00 | 8300.00 | 4200.00 | Anil Kumar Sharma
33.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
33.10 | 4C X 4 Sqmm | 4.00 | EA |  | 250.00 | 1000.00 | 200.00 | 800.00 | 100.00 | 400.00 | 550.00 | 2200.00 | 400.00 | Anil Kumar Sharma
33.20 | 4C X 6 Sqmm | 4.00 | EA |  | 300.00 | 1200.00 | 200.00 | 800.00 | 100.00 | 400.00 | 650.00 | 2600.00 | 400.00 | Anil Kumar Sharma
34.00 | Wiring for circuit/ submain wiring along with earth wire with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface/ recessed steel conduit as required
34.10 | 2 X 1.5 sq. mm + 1 X 1.5 sq. mm earth wire | 40.00 | Mtr |  | 250.00 | 10000.00 | 290.00 | 11600.00 | 180.00 | 7200.00 | 260.00 | 10400.00 | 7200.00 | Anil Kumar Sharma
34.20 | 2 X 2.5 sq. mm + 1 X 2.5 sq. mm earth wire | 60.00 | Mtr |  | 340.00 | 20400.00 | 325.00 | 19500.00 | 275.00 | 16500.00 | 300.00 | 18000.00 | 16500.00 | Anil Kumar Sharma
35.00 | Note: 1. Rate quoted shall be inclusive of any taxes, duties, Cess, fee, royalty charges etc. levied under any statute but exclusive of GST. Goods & Services Tax (GST) shall be paid to the contractor for any taxable supply/ services/works against a valid tax invoice as per terms and conditions of the contract.
| Total in Figures |  |  |  |  | 5413115.00 |  | 3677980.00 |  | 3483150.00 |  | 4622940.00
Lowest Amount Quoted BY: Anil Kumar Sharma(3483150.00)

## BOQ Summary
BOQ Summary Details Tender Title: Provision of lighting wiring and miscellaneous work for Power House Building at Amritsar Airport Tender ID: 2025_AAI_234254_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Anil Kumar Sharma (BID ID -853607) | 3483150.00 | L1
| 2 | Awasthi Electric Works (BID ID -853606) | 3677980.00 | L2
| 3 | GVD ENGINEERS & CONTRACTOR (BID ID -852652) | 4622940.00 | L3
| 4 | Manish Electricals (BID ID -853354) | 5413115.00 | L4