## BoQ1
Government eProcurement System Created By: RISHI RAJ BAGRE Created Date/Time: 20-Jun-2025 04:43 PM Tender Title: Provision of Fire Suppression System for critical CNS and Electrical installations at Dehradun Airport Tender ID: 2025_AAI_235601_1
Tender Inviting Authority: Assistant General Manager (Engg.-Elect.), AAI, Dehradun Airport.
Name of Work: Provision of Fire suppression system for critical CNS & Electrical installations at Dehradun Airport.
Contract No:
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Modern Agencies (GSTN-04AAWFM7893FIZL) BID ID -853438 |  | Nexus Fire And Security Systems (GSTN-07AAKFN7125K1ZY) BID ID -853977 |  | PYROGUARD ENGINEERS PRIVATE LIMITED (GSTN-07AACCP9466E1Z7) BID ID -859284 |  | CENTRE TAP ENGINEERING (GSTN-24AGPPP8172K1ZP) BID ID -859742 |  | Kalpataru Industries (GSTN-NA) BID ID -859846
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Design, Supply,Installation ,Testing & commissioing of Gas Suppression System including fire gas (FK-5-1-12) of 4.5% concentration, flooding system comprising of the following as per NFPA 2001 & Upto date amendments standards consisting of Cylinder PESO Approved, complete with UL / VDS / PESO Approved valve assembly and arrangement for supervisory switch connection for monitoring cylinder pressure,a pressure guage with a safety burst disc ,electronic control head / Solenoid, pressure operated control, head, flexible hose, strap, NRV, Pressure Switch and a safety cap, required nos of Nozzles (UL / VDS listed), Piping, Manifold etc. complete as required. Gas. Design & drawings of clean agent /gas suppression ( Total flooding) system (FK-5-1-12) of 4.5% concentration in compliance to NFPA 2001 & Upto date amendments including design of Cylinder capaity, volume of Gas, Nos. of Nozzles, piping design and pressure calculations using certified (PESO/BIS/UL/VDS) design software suitable for seamless steel cylinder for the rooms with following dimensions duly vetted by manufacturer (OEM) shall be submitted prior to starting of the works. Note: RV: Room Void, CV- Ceiling void & m3- cubic mtrs
1.10 | UPS room -1 +Server room (RV-22 m3 & CV-5 m3) | 1.00 | Job | 0.00 | 8000.00 | 8000.00 | 8000.00 | 8000.00 | 2000.00 | 2000.00 | 20000.00 | 20000.00 | 50000.00 | 50000.00 | 2000.00 | PYROGUARD ENGINEERS PRIVATE LIMITED
1.20 | Automation room (RV-58 m3 & CV-14 m3) | 1.00 | Job | 0.00 | 8000.00 | 8000.00 | 8000.00 | 8000.00 | 2000.00 | 2000.00 | 20000.00 | 20000.00 | 50000.00 | 50000.00 | 2000.00 | PYROGUARD ENGINEERS PRIVATE LIMITED
1.30 | Equipment room-1 RV-54 m3 & CV-13 m3) | 1.00 | Job | 0.00 | 8000.00 | 8000.00 | 7000.00 | 7000.00 | 2000.00 | 2000.00 | 20000.00 | 20000.00 | 50000.00 | 50000.00 | 2000.00 | PYROGUARD ENGINEERS PRIVATE LIMITED
1.40 | Equipment room-2 (RV-64 m3 & CV-15 m3) | 1.00 | Job | 0.00 | 8000.00 | 8000.00 | 7000.00 | 7000.00 | 2000.00 | 2000.00 | 20000.00 | 20000.00 | 50000.00 | 50000.00 | 2000.00 | PYROGUARD ENGINEERS PRIVATE LIMITED
1.50 | UPS room -2 +Battery room (RV-28 m3 & CV-7m3) | 1.00 | Job | 0.00 | 8000.00 | 8000.00 | 8000.00 | 8000.00 | 2000.00 | 2000.00 | 20000.00 | 20000.00 | 50000.00 | 50000.00 | 2000.00 | PYROGUARD ENGINEERS PRIVATE LIMITED
1.60 | UPS room-3 (RV-23 m3 ) | 1.00 | Job | 0.00 | 8000.00 | 8000.00 | 7000.00 | 7000.00 | 2000.00 | 2000.00 | 20000.00 | 20000.00 | 50000.00 | 50000.00 | 2000.00 | PYROGUARD ENGINEERS PRIVATE LIMITED
2.00 | SITC of UL & PESO approved Seamless storage 80L cylinder of Novac 1230 agent complete with valve assembly, pressure switch with safety burst disk & safety cap and other standard accessories including suitable size mounting Straps (2 nos. of straps for each cylinder) . | 4.00 | Each | 0.00 | 105000.00 | 420000.00 | 88000.00 | 352000.00 | 106930.00 | 427720.00 | 100000.00 | 400000.00 | 85000.00 | 340000.00 | 340000.00 | Kalpataru Industries
3.00 | SITC of UL & PESO approved Seamless storage 34 L cylinder of Novac 1231 agent complete with valve assembly , pressure switch with safety burst disk & safety cap and other standard accessories including suitable size mounting Strap (2 nos. of straps for each cylinder) . | 2.00 | Each | 0.00 | 88000.00 | 176000.00 | 59000.00 | 118000.00 | 83120.00 | 166240.00 | 80000.00 | 160000.00 | 70000.00 | 140000.00 | 118000.00 | Nexus Fire And Security Systems
4.00 | Supply, filling & handing over of clean, odourless, colour less, UL listed and suitable for fire class - A, B & C fire suppression agent (FK-5-1-12 fire suppresion fluid) for item no 1.2 & 1.3. etc. complete as per tender specification, as per site requirment & as per direction of Engineer Incharge.(Gas shall be UL Listed and Chromatography Report is required) | 275.00 | Kg | 0.00 | 2200.00 | 605000.00 | 1250.00 | 343750.00 | 1550.00 | 426250.00 | 3000.00 | 825000.00 | 2050.00 | 563750.00 | 343750.00 | Nexus Fire And Security Systems
5.00 | Supply, Installation, Testing & Commissioning of following UL listed accessories of master cylinder suitable to the cylinders as per item no-1.1 & 1.2 complete as per tender specification, as per site requirment: 1. Electrically cum Manual acctuator to operate the gas manually from the cylinder with all accessories 2. Pneumatic actuator valve - For triggering the cylinder assembly as per system requirement 3. Flexible Discharge Hose of Suitable size with approporiate pressure rating made of Braided reinforce rubber Hose fitted with Carbon steel fittings 4. Pressure gauge. | 6.00 | Each | 0.00 | 135000.00 | 810000.00 | 44530.00 | 267180.00 | 41070.00 | 246420.00 | 50000.00 | 300000.00 | 46500.00 | 279000.00 | 246420.00 | PYROGUARD ENGINEERS PRIVATE LIMITED
6.00 | Supply , installation,Testing & commissioing of Manifold supervisory switch for indication of discharge of system complete as required. | 6.00 | Job | 0.00 | 18000.00 | 108000.00 | 2700.00 | 16200.00 | 100.00 | 600.00 | 10000.00 | 60000.00 | 11500.00 | 69000.00 | 600.00 | PYROGUARD ENGINEERS PRIVATE LIMITED
7.00 | Supply , installation,Testing & commissioing of MS seamless Piping conforming to ASTM A-106 Schedule-40 complete with all fittings as per flow calculations for the specific hazard volume and stand to hold,position & support the manifold and piping properly with MS suspended supports, clamps anchor fastners including painting with one coat of red oxide/yellow zinc cromate and 2 coats of enamel paint ( post office red) and cutting/ chases / holes in ceiling/wall and making good the same as required.
7.10 | UPS room -1 +Server room (RV-22 m3 & CV-5 m3) | 1.00 | Lot | 0.00 | 85000.00 | 85000.00 | 35000.00 | 35000.00 | 14000.00 | 14000.00 | 20000.00 | 20000.00 | 28774.00 | 28774.00 | 14000.00 | PYROGUARD ENGINEERS PRIVATE LIMITED
7.20 | Automation room (RV-58 m3 & CV-14 m3) | 1.00 | Lot | 0.00 | 80000.00 | 80000.00 | 35000.00 | 35000.00 | 28000.00 | 28000.00 | 20000.00 | 20000.00 | 76388.00 | 76388.00 | 20000.00 | CENTRE TAP ENGINEERING
7.30 | Equipment room-1 RV-54 m3 & CV-13 m3) | 1.00 | Lot | 0.00 | 80000.00 | 80000.00 | 35000.00 | 35000.00 | 28000.00 | 28000.00 | 20000.00 | 20000.00 | 71867.00 | 71867.00 | 20000.00 | CENTRE TAP ENGINEERING
7.40 | Equipment room-2 (RV-64 m3 & CV-15 m3) | 1.00 | Lot | 0.00 | 85000.00 | 85000.00 | 35000.00 | 35000.00 | 28000.00 | 28000.00 | 20000.00 | 20000.00 | 83738.00 | 83738.00 | 20000.00 | CENTRE TAP ENGINEERING
7.50 | UPS room -2 +Battery room (RV-28 m3 & CV-7m3) | 1.00 | Lot | 0.00 | 60000.00 | 60000.00 | 35000.00 | 35000.00 | 14000.00 | 14000.00 | 20000.00 | 20000.00 | 36456.00 | 36456.00 | 14000.00 | PYROGUARD ENGINEERS PRIVATE LIMITED
7.60 | UPS room-3 (RV-23 m3 ) | 1.00 | Lot | 0.00 | 60000.00 | 60000.00 | 25000.00 | 25000.00 | 14000.00 | 14000.00 | 20000.00 | 20000.00 | 24255.00 | 24255.00 | 14000.00 | PYROGUARD ENGINEERS PRIVATE LIMITED
8.00 | Supply, Installation, Testing & Commissioning of Discharge nozzles designed to provide the proper flow and distribution of gas for total flood of hazard area at - 360 degrees or as per design & site requirment. | 18.00 | Each | 0.00 | 6500.00 | 117000.00 | 5450.00 | 98100.00 | 5500.00 | 99000.00 | 1500.00 | 27000.00 | 6050.00 | 108900.00 | 27000.00 | CENTRE TAP ENGINEERING
9.00 | SITC of microprocessor based dual function Detection cum Gas/Agent Release Panel fully compliant with PESO/UL/BIS/VDS/EN listed & NFPA-72 having minimum 4 detection & minimum 2 nos release circuits (RAC) with programable function. Panel shall have minimum 16x2 character LCD Display suitable to operate on 120-220V /50Hz AC power supply with standby(battery) backup 24V DC supply with builtin charger along with audio visual indication of status/warnings. Other Features comprising of following: i) All zones configuration as Alarm /Supervisory zone. ii) Notifiation Appliance circuits iii)Programmable relays for fire/Fault/supervisory /gas released. iv) Auto /Manual Modes v) Walk test vi) Programable RAC with count down timer vii) Event history Logging viii) All field wiring circuits supervision. ix) Auto dialer interfacing compatibility. | 4.00 | Job | 0.00 | 29000.00 | 116000.00 | 26750.00 | 107000.00 | 24180.00 | 96720.00 | 20000.00 | 80000.00 | 24500.00 | 98000.00 | 80000.00 | CENTRE TAP ENGINEERING
10.00 | Supply & installation of LPCB certified/complient Manual Abort Stations Semi Flush Mounting Re-settable (Non-Breaking Glass), Supplied with Special Reset Tool including integration with gas release panel | 6.00 | Each | 0.00 | 5000.00 | 30000.00 | 2500.00 | 15000.00 | 3840.00 | 23040.00 | 3000.00 | 18000.00 | 3550.00 | 21300.00 | 15000.00 | Nexus Fire And Security Systems
11.00 | Supply & installation of LPCB certified/complient Manual Release Stations Semi Flush Mounting Re-settable (Non-Breaking Glass), Supplied with Special Reset Tool including integration with gas release panel | 6.00 | Each | 0.00 | 5000.00 | 30000.00 | 2500.00 | 15000.00 | 3840.00 | 23040.00 | 3000.00 | 18000.00 | 3550.00 | 21300.00 | 15000.00 | Nexus Fire And Security Systems
12.00 | Supplying, installation , testing and commissioning of conventional photoelectric type Smoke detector, conforming to UL/LPCB/FMI/EN-54, with all accessories viz : indicator, base, base box etc. to be installed on ceiling / false ceiling etc. complete as per site requirment | 32.00 | Each | 0.00 | 2500.00 | 80000.00 | 1300.00 | 41600.00 | 980.00 | 31360.00 | 2000.00 | 64000.00 | 1450.00 | 46400.00 | 31360.00 | PYROGUARD ENGINEERS PRIVATE LIMITED
13.00 | Supply , Installation & comissioning of Hooter cum strobe confirming to UL/LPCB/EN-54. | 16.00 | Each | 0.00 | 4000.00 | 64000.00 | 2800.00 | 44800.00 | 3620.00 | 57920.00 | 4500.00 | 72000.00 | 3750.00 | 60000.00 | 44800.00 | Nexus Fire And Security Systems
14.00 | Supply , Installation & comissioning of Response indicator as required | 20.00 | Each | 0.00 | 700.00 | 14000.00 | 110.00 | 2200.00 | 100.00 | 2000.00 | 500.00 | 10000.00 | 115.00 | 2300.00 | 2000.00 | PYROGUARD ENGINEERS PRIVATE LIMITED
15.00 | Supply and laying of 2 core x 1.5 sqmm, 1.1 KV grade, stranded copper conductor, XLPE insulated with fire-rated glass mica tape, LSZH outer sheathed, Armoured Fire Survival Cable confirming to BS 7846:2015, Fire Resistance as per BS 8434-2:2003, RED in Colour, laid on surface with GI saddle Complete with GI Junction Box, lugs, cable compression glands, cable tags and Ferruling. | 700.00 | Mtrs | 0.00 | 125.00 | 87500.00 | 160.00 | 112000.00 | 200.00 | 140000.00 | 250.00 | 175000.00 | 165.00 | 115500.00 | 87500.00 | Modern Agencies
16.00 | Following capacity Seamless storage cylinder of Novac 1230 agent complete with all necessary fire suppression agent (FK-5-1-12 fire suppresion fluid) including , fittings, valve assembly, pressure gauge and other standard accessories as required approved by LPCB/UL/VDS/FM:
16.10 | 1 Kg Capacity | 3.00 | Each | 0.00 | 48000.00 | 144000.00 | 17500.00 | 52500.00 | 18960.00 | 56880.00 | 10000.00 | 30000.00 | 38760.00 | 116280.00 | 30000.00 | CENTRE TAP ENGINEERING
16.20 | 2 Kg Capacity | 2.00 | Each | 0.00 | 60000.00 | 120000.00 | 25000.00 | 50000.00 | 21350.00 | 42700.00 | 15000.00 | 30000.00 | 41064.00 | 82128.00 | 30000.00 | CENTRE TAP ENGINEERING
17.00 | Supply, installation, testing & commissioning of FireTraceTube (Heat detection tube) for automatic fire detection and suppression system made by special modified Polyamide (PA), Color Red RAL300, High grade quality, Inner diameter 4mm, OuterDiameter 6 MM, bursting temperature-195oC UL approved as per UL 521- STANDARD FOR HEAT DETECTORS FOR FIRE PROTECTIVE SIGNALING SYSTEMS. | 100.00 | Mtrs | 0.00 | 1200.00 | 120000.00 | 675.00 | 67500.00 | 840.00 | 84000.00 | 1500.00 | 150000.00 | 750.00 | 75000.00 | 67500.00 | Nexus Fire And Security Systems
18.00 | Supply, installation, testing & commissioning of FireTrace End of Line adapter with Pressure gauge for Automatic fire suppression tube used for fitting at the end of the tube for pressurizing and re-pressurising the tube used for fitting at the end of the tube for pressurizing and re pressurizing the tube includes check Valve, Pressure Gauge and fitting to connect to sensor tubing. Tube connection 6mm. | 5.00 | Each | 0.00 | 3500.00 | 17500.00 | 3350.00 | 16750.00 | 3720.00 | 18600.00 | 2000.00 | 10000.00 | 2450.00 | 12250.00 | 10000.00 | CENTRE TAP ENGINEERING
19.00 | Supply, installation, testing & commissionong of FireTrace Pressure Switch ( UL Listed) to monitor Pressure drop in the tube, switch point 5 Bars. | 5.00 | Each | 0.00 | 10500.00 | 52500.00 | 4500.00 | 22500.00 | 9480.00 | 47400.00 | 3000.00 | 15000.00 | 4550.00 | 22750.00 | 15000.00 | CENTRE TAP ENGINEERING
20.00 | Supply, installation, testing & commissioning of FireTrace T Connection, Brass, Nickle plated, for 4x6 mm Sensor Tube, quick and easy disassembly using special tool, External Diameter tube 6mm. | 5.00 | Each | 0.00 | 1500.00 | 7500.00 | 1500.00 | 7500.00 | 1210.00 | 6050.00 | 2000.00 | 10000.00 | 1100.00 | 5500.00 | 5500.00 | Kalpataru Industries
21.00 | Supply, installation, testing & commissioning of FireTrace End of Line Plug for Automatic fire suppression tube used for fitting at the tube end to terminate the point. Fitting made by brass nickel plated material. | 5.00 | Each | 0.00 | 1500.00 | 7500.00 | 700.00 | 3500.00 | 1540.00 | 7700.00 | 2000.00 | 10000.00 | 1020.00 | 5100.00 | 3500.00 | Nexus Fire And Security Systems
22.00 | Supply, installation, testing & commissioning of MASTER CONTROL UNIT. | 5.00 | Each | 0.00 | 15000.00 | 75000.00 | 3900.00 | 19500.00 | 7000.00 | 35000.00 | 10000.00 | 50000.00 | 8150.00 | 40750.00 | 19500.00 | Nexus Fire And Security Systems
| Total in Figures |  |  |  |  | 3699500.00 |  | 2017580.00 |  | 2176640.00 |  | 2754000.00 |  | 2846686.00
Lowest Amount Quoted BY: Nexus Fire And Security Systems(2017580.00)

## BOQ Summary
BOQ Summary Details Tender Title: Provision of Fire Suppression System for critical CNS and Electrical installations at Dehradun Airport Tender ID: 2025_AAI_235601_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Nexus Fire And Security Systems (BID ID -853977) | 2017580.00 | L1
| 2 | PYROGUARD ENGINEERS PRIVATE LIMITED (BID ID -859284) | 2176640.00 | L2
| 3 | CENTRE TAP ENGINEERING (BID ID -859742) | 2754000.00 | L3
| 4 | Kalpataru Industries (BID ID -859846) | 2846686.00 | L4
| 5 | Modern Agencies (BID ID -853438) | 3699500.00 | L5