## BoQ1
Government eProcurement System Created By: RAVI KUMAR VANKUDOTHU Created Date/Time: 30-Jun-2025 04:27 PM Tender Title: Installation of DVOR at Rajahmundry Airport, Sub Head Electrical Works Tender ID: 2025_AAI_235776_1
Tender Inviting Authority: SENIOR MANAGER (ENGG-ELECT), AIRPORTS AUTHORITY OF INDIA, RAJAHMUNDRY AIRPORT, RAJAHMUNDRY
Name of Work:Installation of DVOR at Rajahmundry Airport, Sub-Head: Electrical Works.
Tender ID No: 2025_AAI_235776_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | DOSHI ELECTRIC ENGG. CO. (GSTN-24AAEFD3355K1ZI) BID ID -859290 |  | Manish Electricals (GSTN-23ABLPM9012E1ZW) BID ID -865093
[5 empty] | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | DVOR Indoor Panel Design, fabrication, assembling, supply, installation, testing and commissioning of cubicle type LT panels, free floor standing/wall mounted as per site condition suitable for 415V , 3 phase, 4 wire 50 Hz AC supply system fabricated in compartmentised design from CRCA sheet steel of 2 mm thick, IP 42, 3 mm thick for gland plates i/c cleaning and finishing complete 7 tank process for powder coating in approved shade, extendable type TPN aluminium alloy busbars of high condectivity, DMC/SMC busbar supports, entire panel shall have a common copper earthbar of size 20mm X 3 mm at the rear with 2 Nos. earth studs, solid connection from main busbar to switchgears with require size of aluminium busbar & control wiring with 2.5(CT)/1.5(PT) sqmm FRLS insulated copper conductor cable, cable alleys, cable gland plates i/c accessrories as per specification and providing switchgears, metering instruments etc. for following to the panel. Note: Extended Bus Bars with sufficient clearance shall be provided for Incommer section of MCCBs to receive 3.5C x 95Sqmm. Armoured Aluminium Cable. Incomer: a) 100 A, 36 KA, 04 Pole Thermal magnetic release MCCB (Ics=100%Icu) having O/L, S/C fault Protection with with front operated rotary handle - 02 Nos. b) 100 A, 04 Pole , Automatic transfer Swicth with controller having Auto/Manual mode selection with operated handle - 01 Nos. c) 100 A, 04 Pole, HRC fuse with links - 01 Set d) 100 A, 36 KA, 04 Pole Microprocessor Based releases MCCB (Ics=100%Icu) having O/L, S/C, E/F fault Protection with with front operated rotary handle - 02 Nos. e) TPN SPD, type-2, Uc = 275 V, Imax = 40 KA ( 8/20µs) with isolating MCB & indicators - 02 Set f) Digital Power Data logger for current, voltage, PF, Frequency, Power etc. with inbuilt memory for storage of atleast 3 days record - 01 Set. g) LED indication Lamps ( R,Y,B) with SP MCBs protection - 04 Set. h) Digital Multifunction meter, 3 phase, 5A, class -1 with Cast resin CTs( 100/5) - 02 Set. i) ON, OFF &Trip indication lamps (LED type) - 04 Set Bus Coupler: 100 A, 36 KA, 04 Pole Thermal magnetic release MCCB (Ics=100%Icu) having O/L and S/C fault Protection with with front operated rotary handle - 01 no. (Mechanically interlocked with Incomers) 100 A, 4 P, Aluminium Bus bar, with Fiber glass insulated support & Heat shrinkable color coded insulation sleeves etc. Out goings: a) 63 A, 25 KA, 04 Pole Thermal magnetic release MCCB (Ics=100%Icu) having O/L and S/C fault Protection with with front operated rotary handle - 02 Nos. b) 40 A, 25 KA, 04 Pole Thermal magnetic release MCCB (Ics=100%Icu) having O/L and S/C fault Protection with with front operated rotary handle - 04 Nos. c) TPN SPD, type-2, Uc = 275 V, Imax = 40 KA ( 8/20µs) with isolating MCB & indicators - 02 Nos. d) ON, OFF &TRIP indication lamps (LED type) - 06 Sets | 1.00 | Job |  | 375000.00 | 375000.00 | 390000.00 | 390000.00 | 375000.00 | DOSHI ELECTRIC ENGG. CO.
2.00 | Supply of following size XLPE insulated PVC sheathed aluminium conductor armoured power cable of 1.1KV grade confirming to IS 7098 (PART-I) with upto date amendments as required. 4C X 25 Sq.mm | 200.00 | Mtrs |  | 250.00 | 50000.00 | 300.00 | 60000.00 | 50000.00 | DOSHI ELECTRIC ENGG. CO.
3.00 | Supplying and making end termination with brass compression gland and aluminum lugs for following size of PVC insulated and PVC sheathed/XLPE aluminum conductor cable of 1.1 KV grade as required. 3.5C X 240 Sq.mm | 4.00 | Set |  | 2000.00 | 8000.00 | 2500.00 | 10000.00 | 8000.00 | DOSHI ELECTRIC ENGG. CO.
4.00 | Supply, installation, testing and commissioning of conventional type Fire detection & alarm control panel having minimum of 2 zones for connecting multi sensor detectors, manual call points, Hooters etc suitable for operation on 220 Volts, 50 Hz AC power supply, LED indicators to indicate fire and normal operation & power supply status, push button for accept and Reset, maintenance free batteries with minimum 1 hour backup on alarm mode & 8 hours on normal operation mode with battery charger etc., shall be complete as required. Panel shall have necessary provision for connecting and functioning with auto dialer etc as required. | 1.00 | Each |  | 95000.00 | 95000.00 | 19000.00 | 19000.00 | 19000.00 | Manish Electricals
5.00 | Supply, installation, testing and commissioning of auto dialer with all necessary accessories including connections, modules if any required for integrating with Conventional Fire Alarm Panels etc. complete as required. | 1.00 | Each |  | 19000.00 | 19000.00 | 19000.00 | 19000.00 | 19000.00 | DOSHI ELECTRIC ENGG. CO., Manish Electricals
6.00 | Supply, installation, testing and commissioning of weather proof conventional type manual call point (UL Listed) complete with all accessories including connections etc. complete as required. | 2.00 | Each |  | 15200.00 | 30400.00 | 1200.00 | 2400.00 | 2400.00 | Manish Electricals
7.00 | Supply, installation, testing and commissioning of weather proof conventional type Hooter cum strobe with base plate etc. complete as required. | 2.00 | Each |  | 5700.00 | 11400.00 | 3000.00 | 6000.00 | 6000.00 | Manish Electricals
8.00 | Supply, installation, testing and commissioning of conventional type Photoelectric Multi Sensor smoke detectors (UL Listed) along with mounting base with unique optical sensing chamber, visible LED's, complete with all accessories including connections etc. as required. | 18.00 | Each |  | 2850.00 | 51300.00 | 2000.00 | 36000.00 | 36000.00 | Manish Electricals
9.00 | Supplying and fixing of 20 mm steel conduit along with all fittings and accessories in surface/recess including painting using red colour incase of surface conduit, or cutting the wall and making good the same in case of recessed conduit etc. complete as required. | 70.00 | Mtrs |  | 95.00 | 6650.00 | 200.00 | 14000.00 | 6650.00 | DOSHI ELECTRIC ENGG. CO.
10.00 | Supplying and drawing of 2 X 1.5 Sqmm FRLS insulated copper conductor single core cable in the existing surface/ recessed steel conduit/flexible conduit, including terminations etc. complete as required. | 80.00 | Mtrs |  | 55.00 | 4400.00 | 150.00 | 12000.00 | 4400.00 | DOSHI ELECTRIC ENGG. CO.
11.00 | Supply of 1.5 Ton, 5 star rating Split Air conditioner of wall mounting inverter type consisting of non-ductable single type room evaporator unit (copper coil) with cordless remote control and one number outdoor condensing unit comprising of compressor and Refrigerant R32/ R 410A, suitable for operation on 230V, 50Hz. AC supply i/c supply of all accessories i.e. copper refrigerant pipe, insulation, interconnecting cable, drain pipe, full charge of refrigerant etc., complete as required. | 6.00 | Each |  | 47500.00 | 285000.00 | 43000.00 | 258000.00 | 258000.00 | Manish Electricals
12.00 | Installation, testing and commissioning of the 1.5 Ton split air conditioner of high wall mounting type including fixing the condenser unit on existing raising stand and fixing of evaporator unit including providing and making inter connections between evaporator unit and condenser unit up to a length of 3 mtrs etc. complete as required. | 6.00 | Job |  | 3800.00 | 22800.00 | 2000.00 | 12000.00 | 12000.00 | Manish Electricals
13.00 | Supply and fixing of following for interconnections between evaporator unit and condensing unit (extra length) for 1.5 ton Ac, as required as per OEM. i. 1/4"dia copper pipe with insulation or as per OEM. ii. 1/2" copper pipe with insulation or as per OEM. iii. 2 x 2.5 sq. mm + 2.5 sq.mm copper conductor cable or as per OEM.. iv. Rigid PVC pipe / PVC Trunking of suitable size for covering the refrigerant line for above. | 18.00 | Mtrs |  | 2500.00 | 45000.00 | 2100.00 | 37800.00 | 37800.00 | Manish Electricals
14.00 | Providing and laying of 25 mm UPVC drain pipe for 1.5 TR split type A.C units with necessary saddles complete etc. as required. | 24.00 | Mtrs |  | 190.00 | 4560.00 | 200.00 | 4800.00 | 4560.00 | DOSHI ELECTRIC ENGG. CO.
15.00 | Supply, Installation, testing and commissioning of 4 KVA voltage stabilizer, electronic type, wall mountable to give constant output of 230V for wide input range of 150 V to 285 V with time delay, high/low cut off, zero correction technology, output voltage correction mains turn on delay etc. complete as required. | 6.00 | Each |  | 3800.00 | 22800.00 | 4000.00 | 24000.00 | 22800.00 | DOSHI ELECTRIC ENGG. CO.
16.00 | Supply and Installation of MS stand with powder coated/Concrete Pedestral suitable to receive 1.5/2TR outdoor unit of Split AC Units etc. complete as required. | 6.00 | Each |  | 1900.00 | 11400.00 | 900.00 | 5400.00 | 5400.00 | Manish Electricals
17.00 | SITC of Digital Dynamic AC Timers latest micro controller based technology with Auto/manual facility for cyclic operation of 02 Nos. suitable upto 2 Ton split Air Conditioners each of any make, Digital display of On/Off status, Parameters of AC's, Heavy Duty Relays & connectors etc. complete as required. | 6.00 | Each |  | 8550.00 | 51300.00 | 7500.00 | 45000.00 | 45000.00 | Manish Electricals
18.00 | Earthing with G.I. earth plate 600mm x 600mm x 6 mm thick, including accessories, and providing 300x300x450(H) mm RCC earth pit chamber suitable to receive 6mm thick MS chequered plate with handle,strengthening & compaction of soil below the earth pit chamber including providing suitable ratio PCC, providing & laying positional cement concrete (1:2:4) of depth 100mm surrounding the earth pit chamber covering surface area of 01 Sqmtr, including providing and fixing of reducer water funnel with wire mesh arrangement for watering etc. with charcoal/coke and salt as required. | 2.00 | Sets |  | 7600.00 | 15200.00 | 9500.00 | 19000.00 | 15200.00 | DOSHI ELECTRIC ENGG. CO.
19.00 | Earthing with Copper earth plate 600mm x 600mm x 3 mm thick including accessories, and providing 300x300x450(H) mm RCC earth pit chamber suitable to receive 6mm thick MS chequered plate with handle,strengthening & compaction of soil below the earth pit chamber including providing suitable ratio PCC, providing & laying positional cement concrete (1:2:4) of depth 100mm surrounding the earth pit chamber covering surface area of 1 Sqmtr,including providing and fixing of reducer water funnel with wire mesh arrangement for watering etc. with charcoal/coke and salt as required. | 2.00 | Sets |  | 15200.00 | 30400.00 | 15200.00 | 30400.00 | 30400.00 | DOSHI ELECTRIC ENGG. CO., Manish Electricals
20.00 | Providing and fixing 6 SWG dia G.I. wire on surface or in recess for loop earthing along with existing surface/ recessed conduit/HDPE Pipe/ cable as required | 30.00 | Mtrs |  | 25.00 | 750.00 | 60.00 | 1800.00 | 750.00 | DOSHI ELECTRIC ENGG. CO.
21.00 | Supplying and laying 25 mm X 5 mm copper strip at 0.50 metre below ground as strip earth electrode, including connection/ terminating with nut, bolt, spring, washer etc. as required. (Jointing shall be done by overlapping and with 2 Sets of brass nut bolt & spring washer spaced at 50mm) | 10.00 | Mtr |  | 1040.00 | 10400.00 | 1200.00 | 12000.00 | 10400.00 | DOSHI ELECTRIC ENGG. CO.
22.00 | Supplying and laying 25 mm X 5 mm G.I strip at 0.50 metre below ground as strip earth electrode, including connection/ terminating with G.I. nut, bolt, spring, washer etc. as required. (Jointing shall be done by overlapping and with 2 Sets of G.I. nut bolt & spring washer spaced at 50mm) | 10.00 | Mtr |  | 190.00 | 1900.00 | 200.00 | 2000.00 | 1900.00 | DOSHI ELECTRIC ENGG. CO.
23.00 | Providing· and fixing 25 mm X 5 mm· Copper strip in 40 mm dia G.l. pipe from earth electrode including connection with G.l. nut, bolt, spring, washer excavation and refilling etc. as required. | 12.00 | Mtr |  | 1425.00 | 17100.00 | 2000.00 | 24000.00 | 17100.00 | DOSHI ELECTRIC ENGG. CO.
24.00 | Providing· and fixing 25 mm X 5 mm· G.l. strip in 40 mm dia G.l. pipe from earth electrode including connection with G.l. nut, bolt, spring, washer excavation and refilling etc. as required. | 14.00 | Mtr |  | 570.00 | 7980.00 | 900.00 | 12600.00 | 7980.00 | DOSHI ELECTRIC ENGG. CO.
25.00 | Providing and fixing 25 mm X 5 mm copper. strip on surface or in recess in Existing G.I pipe/Hume Pipe/ Open Trench for connections etc. as required | 12.00 | Mtr |  | 950.00 | 11400.00 | 1000.00 | 12000.00 | 11400.00 | DOSHI ELECTRIC ENGG. CO.
26.00 | Providing and fixing 25 mm X 5 mm G.I strip on surface or in recess in Existing G.I pipe for connections etc. as required | 12.00 | Mtr |  | 140.00 | 1680.00 | 250.00 | 3000.00 | 1680.00 | DOSHI ELECTRIC ENGG. CO.
27.00 | Supplying and fixing of nominal 2 mm thick PVC synthetic,electric insulated mats along with suitable adhesive/chemibond, having breakdown strength of 30 KV, no adverse effect of mineral oil, high insulation resistance (Minimum 10,000 M Ω on wet condition with 5 KV meggar) i/c providing water proofing of floor, (chipping of floor if required) sealing of all joints etc., as required. | 5.00 | Sq. mtr |  | 570.00 | 2850.00 | 900.00 | 4500.00 | 2850.00 | DOSHI ELECTRIC ENGG. CO.
28.00 | Supply ,installation, testing, commissioning of 4" dia submersible borewell type pump of 60 LPM discharge (minimum) at 88 mtr head, multi stage, Noryl impeller suitable for 150 mm borewell with 2 HP motor suitable for operation on 230V, Single phase power supply etc, complete as required. (Make: Kirloskar KS4C-2016 or its equivalent from list of AAI approved makes) | 1.00 | Each |  | 25000.00 | 25000.00 | 29000.00 | 29000.00 | 25000.00 | DOSHI ELECTRIC ENGG. CO.
29.00 | Supply of minimum of 300 lumens capacity compact portable lantern type, plastic housing with plastic diffuser LED emergency lamps having minimum of 04 hours backup rechargable battery including charging wire, operating of 230V, 50HZ A.C supply,etc as required.(Model No. BAJAJ ELX 16 LED or equivalent) | 4.00 | Each |  | 2500.00 | 10000.00 | 2500.00 | 10000.00 | 10000.00 | DOSHI ELECTRIC ENGG. CO., Manish Electricals
| Total in Figures |  |  |  |  | 1228670.00 |  | 1115700.00
Lowest Amount Quoted BY: Manish Electricals(1115700.00)

## BOQ Summary
BOQ Summary Details Tender Title: Installation of DVOR at Rajahmundry Airport, Sub Head Electrical Works Tender ID: 2025_AAI_235776_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Manish Electricals (BID ID -865093) | 1115700.00 | L1
| 2 | DOSHI ELECTRIC ENGG. CO. (BID ID -859290) | 1228670.00 | L2