## BoQ1
Government eProcurement System Created By: MEHBUB AHMED Created Date/Time: 16-Jul-2025 11:53 AM Tender Title: Provision of 250 KVA DG set and associated miscellaneous works at AAI residential colony, Guwahati Airport Tender ID: 2025_AAI_236460_1
Tender Inviting Authority: AGM(E-E), RHQ NER, GUWAHATI AIRPORT
Name of Work: Provision of 250 KVA DG set and associated miscellaneous works at AAI residential colony, Guwahati Airport
Tender ID: 2025_AAI_236460_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Awasthi Electric Works (GSTN-09ABAPA1866D1Z5) BID ID -863998 |  | FUJI TECHNICAL SERVICES PVT. LTD. (GSTN-27AAACF1784F1ZQ) BID ID -863877 |  | S chowdhury and Company (GSTN-NA) BID ID -864066 |  | Shiva Enterprises (GSTN-NA) BID ID -864154 |  | Virtus Techno (GSTN-NA) BID ID -863875 |  | VOID FIRE CONSULTANTS (GSTN-NA) BID ID -862701
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | SH:1- DG Set
1.01 | Providing, Installation, Testing and Commissioning of ‘Silent Type’ Diesel Generating set along with having Prime Power Rating of 250kVA, 415 volts at 1500 RPM, 0.8 lagging power factor at 415V suitable for 50 Hz, 3 phase system & for 0.85 Load Factor CPCB4+ complaint as ammended upto date and consisting of the followings: (a)Diesel Engine : Diesel engine of 4 stroke water cooled, electric start, of suitable BHP at 1500 RPM suitable for above output of alternator at 40 Degree C, 50% RH & at 1000 Meter MSL and conforming to BS 5514, BS 649, IS 10000 ammended upto date, capable of taking 10% over loading for one hour after 12 hours of continuous operation. The engine will be fitted complete with all the required accessories. (b)Engine mounted Instrument Panel fitted with and having digital display for following : (i) Start-stop switch with key.(ii) Water temperature indication.(iii) Lubrication oil pressure indication.(iv) Lubrication oil temperature indication.(v) RPM indication.(vi) Over speed indication.(vii) Low lub. Oil trip indication.(viii) Engine Hours indication. ix) Battery charging indication. (c)Alternator: Synchronous alternator rated at 250kVA, 415 volts at 1500 RPM, 3 phase 50 Hz, AC supply with 0.8 lagging power factor at 40 Degree C, 50% RH & at 1000 Meter MSL. The alternator shall be having SPDP enclosure, brushless, continuous duty, self-excited and self regulated through AVR conforming to IS:4722/BS 2613 suitable for tropical conditions and with class- F/H insulation. (d)Base Frame & Foundation : Both the engine and alternator shall be mounted on suitable base frame made of MS channel with necessary reinforcement which shall be installed on suitable cement concrete foundation and vibration isolation arrangement as per recommendations of manufacturer. (e)Fuel Tank : Daily fuel service tank fabricated out of 3mm thick MS sheet complete with al standard accessories and fuel piping between fuel tank and diesel engine with MS 'C' class pipes of suitable dia complete with valves, air vent tap, drain plug, level indicator & accessories as requires. (f) Exhaust System : Dry exhaust manifold with residential type exhaust silencer, catalytic convertor and alongwith required length of heavy duty MS exhaust pipings duly insulated and claded as per Technical specifications.. (g)Starting System : 24V DC starting system comprising of starter motors, voltage regulator and arrangement for initial excitation complete with suitable no's of batteries (25 plates, 180 Amp. Hour capacity lead acid type) as required as per specifications. (h)Acoustics and weather proof enclosure with arrangement for fresh air intake for cooling of the engine & alternator, extraction, discharging hot air in to the atmosphere as per the specifications and standard design of manufacturer. | 1.00 | JOB | 100.00 | 2345000.00 | 2345000.00 | 3374800.00 | 3374800.00 | 2350000.00 | 2350000.00 | 2150000.00 | 2150000.00 | 3060000.00 | 3060000.00 | 2510000.00 | 2510000.00 | 2150000.00 | Shiva Enterprises
1.02 | Supply, installation, testing & commissioning of Calibrated HSD buffer/service tank, rectangular MS (IS:226) construction with 990 liters capacity complete with flanged inlet & outlet, overflow, drain, vent, mechanical level indicator, 450mm dia Access hole on top with cover, flame arrestor. Tank will be made out of 3mm MS sheet and will be provided with structural support to keep tank base at (2000mm) above FFL with access ladder arrangement, painting etc. complete as required. | 1.00 | JOB | 100.00 | 60000.00 | 60000.00 | 181720.00 | 181720.00 | 360000.00 | 360000.00 | 15000.00 | 15000.00 | 54000.00 | 54000.00 | 240000.00 | 240000.00 | 15000.00 | Shiva Enterprises
1.03 | Supplying, installation, testing & comissioning of MS pipes of heavy class ERW piping (Class-C) conforming to IS 1239 of following sizes and materials cut to required lengths and installed with necessary bends, supports and clamps, anti-vibration mounting, etc but excluding valves, strainers and gauges etc. adequately supported on rigid supports / concealed on floor, painting with two coats of synthetic enamel paint after primer coat etc. complete as required. Size 25 mm | 20.00 | MTR | 10.00 | 455.00 | 9100.00 | 2531.10 | 50622.00 | 6500.00 | 130000.00 | 4000.00 | 80000.00 | 540.00 | 10800.00 | 450.00 | 9000.00 | 9000.00 | VOID FIRE CONSULTANTS
1.04 | Supply , installation, testing & comissioning of following sizes of Ball Valve of brass body, PN-16 rating, Teflon sealing, stainless steel handle, screwed ends etc complete as required. Size 25 mm | 1.00 | EACH | 10.00 | 1500.00 | 1500.00 | 5192.00 | 5192.00 | 1250.00 | 1250.00 | 3800.00 | 3800.00 | 900.00 | 900.00 | 1650.00 | 1650.00 | 900.00 | Virtus Techno
1.05 | Providing, Fixing, Testing and Commissioning of HSD Oil Y-strainer of 50mm dia, CI body, SS strainer, flanged ends etc complete as required. Size 25 mm dia | 1.00 | EACH | 10.00 | 3800.00 | 3800.00 | 16225.00 | 16225.00 | 3800.00 | 3800.00 | 2500.00 | 2500.00 | 2220.00 | 2220.00 | 4500.00 | 4500.00 | 2220.00 | Virtus Techno
1.06 | Supplying and fixing of exhaust gas piping of dia. 150 mm for 250 KVA rating D.G. Set welded black MS, 'B' Class pipe conforming to IS:3589 cut to required lengths and installed with necessary bends, supports and clamps, anti-vibration mountings, the work include necessary cladding of exhaust pipe work using wiremesh, 50 mm thick Loosely bound resin(LBR)mattress / mineral wool/ Rockwool, density not less than 150kg/m and aluminium cladding (0.6mm thick min.) complete portion complete as required as per specifications. | 12.00 | MTR | 10.00 | 5500.00 | 66000.00 | 25960.00 | 311520.00 | 3500.00 | 42000.00 | 7200.00 | 86400.00 | 7800.00 | 93600.00 | 11000.00 | 132000.00 | 42000.00 | S chowdhury and Company
1.07 | Supply, installation, fabrication of MS frame structural work for supproting existing exahuast gas pipe of dia 150 mm mentioned at item no.- 6 complete as required | 100.00 | KG | 10.00 | 250.00 | 25000.00 | 181.72 | 18172.00 | 360.00 | 36000.00 | 125.00 | 12500.00 | 60.00 | 6000.00 | 150.00 | 15000.00 | 6000.00 | Virtus Techno
1.08 | Supply and installation of SS Flexible Bellows, 6" dia. (150 mm NB), complete with counter flanges, heat resitant gaskets, nuts-bolts-washers etc., complete as required. | 1.00 | EACH | 10.00 | 8000.00 | 8000.00 | 29205.00 | 29205.00 | 4500.00 | 4500.00 | 5000.00 | 5000.00 | 12600.00 | 12600.00 | 7700.00 | 7700.00 | 4500.00 | S chowdhury and Company
2.00 | SH:2- Panel and Wiring
2.01 | MAIN ESSENTIAL Cum AMF PANEL Design, manufacture supply, installation, testing and commissioning of Main LT Panel (PTTA type construction), cubicle & modular type, made of CRCA sheet of 2 mm thick for load bearing members, 1.6 mm thick for doors & 3 mm thick for gland plates, totally enclosure protection class IP 42 of cubical construction, free standing, floor mounting, dust and vermin proof, indoor, compartmentalised, including cleaning & finishing complete with 7 tank process, powder coated, painting, suitable for operation on 3 Phase and neutral, 415v, 50 Hz AC system with Al.busbars extensible on both sides, entire panel shall have a common GI earth bar of size 25mm x 5mm at the rear with 2 nos. earth stud, control wiring with 2.5 sq.mm. PVC insulated copper conductor, cable alloys, cable gland plates in two half, interconnections including supply & installation of following items i/c providing & installation of suitable PLC as required and as per technical specification: (a) INCOMERS (i) 400A, FP, ≥50 kA, ( ICS= 100% ICU) MCCB with microprocessor release having over load and short circuit, earth fault, Rotary handel, spreader link,phase barriers etc.- 4 nos . (ii) Digital reverse power relay- 4 nos (iii) FP 400 Amp Power Contactor- 4 nos (iv) Flush pattern digital Voltmeter(0-500 V), accuracy class 1, suitable range for 3 phase, 4 wire operation with LED display and built-in selector switch along with 3 nos. of 2 Amp SP MCBs.- 4 sets. (v) Flush pattern Digital Type Ammeter of suitable range (to measure 0-400A), for 3 phase 4 wire operation with LED display and selector switch with 3 numbers of class 1.0 accuracy, 15 VA burden & suitable range CTs.- 4 sets. (vi) Indication Lamps, LED type for R,Y,B and breaker 'ON' , 'OFF', 'TRIP' indications each with 2 Amp SP MCBs for protection.- 4 sets (vii) Intelligent multi function digital meter to read V,A,KVA, KW, KVAR, KWH, PF, Hz etc and LED display with 3 Nos CTs, 15 VA, class 1.0 and control circuit wiring with 2 Amp. SP MCBs.-4 sets. (b) BUS COUPLER (i) 1 No. 400A, FP,≥50 kA, ( ICS= 100% ICU) MCCB without release (ii) 1 Set Indication Lamps, LED type for 'ON' , 'OFF', 'TRIP' indications with 2 Amp SP MCBs, etc. as required. (c ) BUSBARS 1 set of high conductivity Aluminium bus bars of minimum 500 Amps capacity, TPN with heat shrinkable coloured sleeves and i/c DMC busbars supports at required intervals. (d) Accessories for Electrical & Mechanical Interlocking Electrical & mechanical interlocking arrangement as per drawing and specifications, etc. as required. (e) OUTGOINGS (i) 4 Nos. 200A, FP, 35 kA, ( ICS= 100% ICU) MCCB with Thermal Magnetic release having over load and short circuit, earth fault, Rotary handel, spreader link,phase barriers etc.. (ii) 2 Nos. 63A, FP, 25 kA, ( ICS= 100% ICU) MCCB with Thermal magnetic release having, over load and short circuit, Rotary handel, spreader link,phase barriers etc.. (iii) Flush pattern Digital Type Ammeter of suitable range (for each outgoing), for 3 phase 4 wire operation with LED display and selector switch with 3 numbers of class 1.0 accuracy, 15 VA burden & suitable range CTs.- 6 sets. B) COMPONENTS FOR AMF OPERATION OF DG SET - 02 SETS ( 1 SET FOR EACH DG SET) Each AMF section shall have the one set of following items: a) Relays, control contactors for neutral, Aux.Relays, Timers: i) 1 No. Microprocessor based AMF logic relay having UV and OV, Phase reversal, engine start relay ,engine cranking relay, Auto/Mannual/ test / service etc. ii) 1 Set of All other auxiliary relays, auxiliary / control contactors (12V/ 24V DC and 230V AC), timers, Three impulse unit , Master trip relay, etc of suitable rating and quantity as required to achieve AMF function as described in technical specifications. iii) 1 Set LED Indication lamps, Push buttons, window annunciation facia etc of required quantity as per technical specifications. iv) 1 No combined digital over current and earth fault relay b) Metering: i) 1 set of Digital AC Ammeter of suitable range with built-in selector switch, Cast Resin CTs & control MCBs ii) 1 set of Digital AC Voltmeter of suitable range with built-in selector switch & control MCBs iii) 1 no.Digital Frequency meter iv) 1 No.Digital Power factor meter v) 1 No. Digital DC Voltmeter vi) 1 No. Digital DC Ammeter c) Others i) 1 set of required quantity of suitable range and accuracy class of Cast Resin CTs for Metering & Protection ii) 1 set of required quantity and rating of HRC fuse/MCBs for control & protection circuits - 01 Set iii) 1 set of 24V DC battery charger comprising of transformer, rectifier unit & charge rate selector switch etc., - 01 Set. iv) 1 No. Hooter v) 1 Lot of Control wiring from DG set to AMF Panel vi) All other accessories & components required for proper operation of AMF logic and inter locking etc. Note- Ics = 100%Icu upto 430V for all MCCB. Rotary operating mechanism and terminal extension / spreaders shall be provided to all the MCCBs. | 1.00 | JOB | 10.00 | 1175000.00 | 1175000.00 | 713900.00 | 713900.00 | 885000.00 | 885000.00 | 1140000.00 | 1140000.00 | 905520.00 | 905520.00 | 405000.00 | 405000.00 | 405000.00 | VOID FIRE CONSULTANTS
2.02 | Supply of following sizes LT power cables of 1.1 KV grade aluminium conductor XLPE insulated and PVC sheathed armoured cable confirming to IS 7098 Part I-1988 with upto date amendment as required. Size-i) 3.5C x 240 sq. mm. | 100.00 | MTR | 10.00 | 1150.00 | 115000.00 | 1882.10 | 188210.00 | 1950.00 | 195000.00 | 1100.00 | 110000.00 | 1163.40 | 116340.00 | 2100.00 | 210000.00 | 110000.00 | Shiva Enterprises
2.03 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing masonry open duct as required. i) Above 95 sq. mm and upto 185 sq. mm | 50.00 | MTR | 10.00 | 70.00 | 3500.00 | 292.05 | 14602.50 | 100.00 | 5000.00 | 120.00 | 6000.00 | 132.00 | 6600.00 | 265.00 | 13250.00 | 3500.00 | Awasthi Electric Works
2.04 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing masonry open duct as required. ii) Above 185 sq. mm and upto 400 sq. mm | 100.00 | MTR | 10.00 | 100.00 | 10000.00 | 421.85 | 42185.00 | 100.00 | 10000.00 | 140.00 | 14000.00 | 180.00 | 18000.00 | 385.00 | 38500.00 | 10000.00 | Awasthi Electric Works, S chowdhury and Company
2.05 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 kV grade as required. i) 3½ X 240 sq. mm (62mm) | 4.00 | EACH | 10.00 | 1100.00 | 4400.00 | 5841.00 | 23364.00 | 930.00 | 3720.00 | 1100.00 | 4400.00 | 1440.00 | 5760.00 | 1309.00 | 5236.00 | 3720.00 | S chowdhury and Company
2.06 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 kV grade as required. ii) 3½ X 185 sq. mm (57mm) | 4.00 | EACH | 10.00 | 950.00 | 3800.00 | 3894.00 | 15576.00 | 900.00 | 3600.00 | 950.00 | 3800.00 | 1260.00 | 5040.00 | 1001.00 | 4004.00 | 3600.00 | S chowdhury and Company
2.07 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 kV grade as required. iii) 3½ X 50 sq. mm (35mm) | 2.00 | EACH | 10.00 | 450.00 | 900.00 | 2596.00 | 5192.00 | 830.00 | 1660.00 | 450.00 | 900.00 | 1020.00 | 2040.00 | 847.00 | 1694.00 | 900.00 | Awasthi Electric Works, Shiva Enterprises
2.08 | Supplying and making straight through joint with heat shrinkable kit including ferrules and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. i) 3½ X 185 sq. mm | 2.00 | EACH | 10.00 | 3850.00 | 7700.00 | 5192.00 | 10384.00 | 3800.00 | 7600.00 | 2450.00 | 4900.00 | 1560.00 | 3120.00 | 2310.00 | 4620.00 | 3120.00 | Virtus Techno
2.09 | Supplying and making straight through joint with heat shrinkable kit including ferrules and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. ii) 3½ X 50 sq. mm | 1.00 | EACH | 10.00 | 3000.00 | 3000.00 | 3245.00 | 3245.00 | 2500.00 | 2500.00 | 1750.00 | 1750.00 | 1020.00 | 1020.00 | 1540.00 | 1540.00 | 1020.00 | Virtus Techno
3.00 | SH:3- Earthing
3.01 | Earthing with G.l. earth pipe 4.5 meter long, 40 mm dia including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe etc. with charcoal/coke and salt as required. | 2.00 | EACH | 10.00 | 10000.00 | 20000.00 | 6490.00 | 12980.00 | 18000.00 | 36000.00 | 7500.00 | 15000.00 | 7800.00 | 15600.00 | 6930.00 | 13860.00 | 12980.00 | FUJI TECHNICAL SERVICES PVT. LTD.
3.02 | Earthing with G.I. earth plate 600 mm X 600 mm X 6 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 meter long etc. with charcoal/ coke and salt as required. | 6.00 | EACH | 10.00 | 16000.00 | 96000.00 | 9735.00 | 58410.00 | 14000.00 | 84000.00 | 10000.00 | 60000.00 | 6240.00 | 37440.00 | 11550.00 | 69300.00 | 37440.00 | Virtus Techno
3.03 | Providing and fixing 25 mm X 5 mm G.I. strip in 40 mm dia G.I. pipe from earth electrode including connection with G.I. nut, bolt, spring, washer excavation and re-filling etc. as required. | 50.00 | MTR | 10.00 | 650.00 | 32500.00 | 778.80 | 38940.00 | 190.00 | 9500.00 | 250.00 | 12500.00 | 114.00 | 5700.00 | 700.00 | 35000.00 | 5700.00 | Virtus Techno
3.04 | Providing and fixing 25 mm X 5 mm G.I. strip on surface or in recess for connections etc. as required. | 70.00 | MTR | 10.00 | 210.00 | 14700.00 | 519.20 | 36344.00 | 190.00 | 13300.00 | 180.00 | 12600.00 | 114.00 | 7980.00 | 210.00 | 14700.00 | 7980.00 | Virtus Techno
3.05 | Earthing with copper earth plate 600 mm X 600 mm X 3 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 meter long etc. with charcoal/ coke and salt as required. | 4.00 | EACH | 10.00 | 22000.00 | 88000.00 | 19470.00 | 77880.00 | 10000.00 | 40000.00 | 18500.00 | 74000.00 | 14640.00 | 58560.00 | 16170.00 | 64680.00 | 40000.00 | S chowdhury and Company
3.06 | Providing and fixing 25 mm X 5 mm copper strip in 40 mm dia G.I. pipe from earth electrode including connection with brass nut, bolt, spring, washer excavation and re-filling etc. as required. | 30.00 | MTR | 10.00 | 1650.00 | 49500.00 | 4218.50 | 126555.00 | 1650.00 | 49500.00 | 1550.00 | 46500.00 | 1242.00 | 37260.00 | 1986.00 | 59580.00 | 37260.00 | Virtus Techno
3.07 | Providing and fixing 25 mm X 5 mm copper strip on surface or in recess for connections etc. as required | 60.00 | MTR | 10.00 | 1300.00 | 78000.00 | 3569.50 | 214170.00 | 1650.00 | 99000.00 | 1150.00 | 69000.00 | 1242.00 | 74520.00 | 1500.00 | 90000.00 | 69000.00 | Shiva Enterprises
3.08 | Supplying and laying 6 SWG G.I. wire on surface or in recess for loop earthing as required. | 50.00 | MTR | 10.00 | 30.00 | 1500.00 | 116.82 | 5841.00 | 120.00 | 6000.00 | 20.00 | 1000.00 | 30.00 | 1500.00 | 50.00 | 2500.00 | 1000.00 | Shiva Enterprises
3.09 | Dismantling of existing AME panel, Wall mounting panel of all types and sizes from its location i/c removal of cable termination, shifting and handing over to AAI store/dismantled yard upto a distance not more than 250 mtrs as directed by EIC. | 2.00 | JOB | 10.00 | 5000.00 | 10000.00 | 44132.00 | 88264.00 | 10000.00 | 20000.00 | 12000.00 | 24000.00 | 78000.00 | 156000.00 | 21000.00 | 42000.00 | 10000.00 | Awasthi Electric Works
| Total in Figures |  |  |  |  | 4231900.00 |  | 5663498.50 |  | 4398930.00 |  | 3955550.00 |  | 4698120.00 |  | 3995314.00
Lowest Amount Quoted BY: Shiva Enterprises(3955550.00)

## BOQ Summary
BOQ Summary Details Tender Title: Provision of 250 KVA DG set and associated miscellaneous works at AAI residential colony, Guwahati Airport Tender ID: 2025_AAI_236460_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Shiva Enterprises (BID ID -864154) | 3955550.00 | L1
| 2 | VOID FIRE CONSULTANTS (BID ID -862701) | 3995314.00 | L2
| 3 | Awasthi Electric Works (BID ID -863998) | 4231900.00 | L3
| 4 | S chowdhury and Company (BID ID -864066) | 4398930.00 | L4
| 5 | Virtus Techno (BID ID -863875) | 4698120.00 | L5
| 6 | FUJI TECHNICAL SERVICES PVT. LTD. (BID ID -863877) | 5663498.50 | L6