## BoQ1
Government eProcurement System Created By: Sateesh Kr Kanaujiya Created Date/Time: 09-Jul-2025 04:49 PM Tender Title: Design, Supply, Installation, Testing and Commissioning of 18 KW Roof Top Solar Plant at Aurangabad Airport Tender ID: 2025_AAI_237796_1
Tender Inviting Authority: Senior Manager (Engg.-Electrical), Airports Authority of India, Aurangabad Airport, Aurangabad- 431007.
Name of Work: Design, Supply, Installation, Testing and commissioning of 18 KW Roof Top Solar Plant at Aurangabad Airport.
Contract No: 2025_AAI_ 237796 _1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | POOJA BUILDCON CONSTRUCTION (GSTN-06AAWFP9068M1Z4) BID ID -867369 |  | NEW BALAJI ENTERPRISES (GSTN-NA) BID ID -867129
[5 empty] | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Design, Supply, Installation, Testing and Commissioning of ongrid Solar Photovoltaic Power Plant conforming to MNRE specifications as amended, consisting of Mono Crystalline silicon solar cells, net metering facility, necessary protections, earthing, mounted on Aluminium/GI structure of suitable strength with following components complete as required:- a) Solar Photovoltaic Module of capacity 540 Wp or above, manufactured in India, conforming to IS 14286/IEC 61215, IS/IEC 61730-Part-1, IS/IEC 61730-Part-2. Solar Photovoltaic Module conversion efficiency shall not be less than 16.5%. PV modules used in solar power plants/ systems must be warranted for their output peak watt capacity, which should not be less than 90% at the end of 10 years and 80% at the end of 25 years. b) Power Conditioning Unit (PCU) of 350-800 V DC Input voltage range and 400 V AC, three phase, 4 wire, 50Hz +/- 2.5 Hz, output voltage suitable to generate AC Power with efficiency not less than 97%, total harmonic distortion less than 3% and suitable for ambient temperature from 0 to 50 degree C. The PCU shall adjust the voltage and frequency level to suit the Grid Voltage Frequency. c) Data Monitoring System (SCADA), Solarradiation & environment monitoring system complete with accessories. d) Fixing of Array junction box & Main junction box with IP 65 protection and termination arrangement for incoming and outgoing cable along with glands, lugs and other accessories etc. as required. e) Lightning and surge voltage protection. f) Connections & Interconnections by supplying & fixing required size XLPE insulated copper conductor 1.1 kV grade armoured power and DC cables between solar modules, main power cable to grid supply to PCU unit along with supplying & fixing of necessary channel/conduit lugs and other accessories etc. as required. g) DLP for the installation will be 02 years. h)Carrying out Glint/Glare Analysis for safe flight operations, shadow analysis, clearance/approval from DISCOM, CEA and other statuatory agencies, transportaions & insuarnce of materials etc and all other items/ acessories/ services which are required for sucessfull commissioning of Solar Power plant complete as required as per technical specifications & terms & conditions of the contract. | 18.00 | KWp |  | 47166.00 | 848988.00 | 50000.00 | 900000.00 | 848988.00 | POOJA BUILDCON CONSTRUCTION
| Total in Figures |  |  |  |  | 848988.00 |  | 900000.00
Lowest Amount Quoted BY: POOJA BUILDCON CONSTRUCTION(848988.00)

## BOQ Summary
BOQ Summary Details Tender Title: Design, Supply, Installation, Testing and Commissioning of 18 KW Roof Top Solar Plant at Aurangabad Airport Tender ID: 2025_AAI_237796_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | POOJA BUILDCON CONSTRUCTION (BID ID -867369) | 848988.00 | L1
| 2 | NEW BALAJI ENTERPRISES (BID ID -867129) | 900000.00 | L2