## BoQ1
Government eProcurement System Created By: Narender Kumar Created Date/Time: 30-Jul-2025 10:46 AM Tender Title: Misc. Electrical works at Safdarjung Airport, New Delhi. Tender ID: 2025_AAI_238100_1
Tender Inviting Authority: Sr. Mgr., Airports Authority of India, Safdarjung Airport, New Delhi-110003.
Name of Work: Misc. Electrical works at Safdarjung Airport, New Delhi.
Contract No: AAI/SAP/Engg.(E)/Facade/2025-26
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | SANGEETA ELECTRICALS (GSTN-NA) BID ID -868925 |  | SYNERGY LIGHTING SOLUTIONS (GSTN-NA) BID ID -868887
[5 empty] | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply, Installation, testing and commissioning of MONO Linear wallwasher LED Light made of aluminium extrusion, exterior-rated linear luminaire (1000mm), Input Power 36W, Rated input supply of Input Voltage 24V DC, Luminaire luminous flux Minimum range 2160Lm. IP protection rating : IP67. The luminaire should have multiple beam angle: 10°, 20, 40, 60°, 10X20° (as per site requirement) complete as required. Manufacturer should submit proper BIS certificate. | 28.00 | Nos. | 100.00 | 20285.00 | 567980.00 | 19500.00 | 546000.00 | 546000.00 | SYNERGY LIGHTING SOLUTIONS
2.00 | Supply, Installation, testing and commissioning of RGBW linear wallwasher LED Light , made of aluminium extrusion, exterior-rated linear luminaire (1000mm), Product input Power 24 Watt , Product should be equipped with inbuilt DMX 512 decoder with Same Ingress protection of Product for individual addressing and programming , Rated input supply of Input Voltage 24V DC, Luminaire luminous flux Minimum range 960Lm. IP protection rating : IP67. The luminaire should have multiple beam angle: 10°, 20, 40, 60°, 10X20° (as per site requirement) complete as required. Manufacturer should submit proper BIS certificate. | 60.00 | Nos. | 100.00 | 20971.00 | 1258260.00 | 20000.00 | 1200000.00 | 1200000.00 | SYNERGY LIGHTING SOLUTIONS
3.00 | Supply, Installation, testing and commissioning of MONO Linear wallwasher LED Light made of aluminium extrusion, exterior-rated linear luminaire (1000mm), Input Power 24W, Rated input supply of Input Voltage 24V DC, Luminaire luminous flux Minimum range 1440Lm. IP protection rating : IP67. The luminaire should have multiple beam angle: 10°, 20, 40, 60°, 10X20° (as per site requirement) complete as required. Manufacturer should submit proper BIS certificate. | 60.00 | Nos. | 10.00 | 19828.00 | 1189680.00 | 19200.00 | 1152000.00 | 1152000.00 | SYNERGY LIGHTING SOLUTIONS
4.00 | Supply, Installation, testing and commissioning of RGBW linear wallwasher LED Light made of aluminium extrusion, exterior-rated linear luminaire (1000mm), Input Power 15W, Product should be equipped with inbuilt DMX 512 decoder with Same Ingress protection of Product for individual addressing and programming, Rated input supply of Input Voltage 24V DC, Luminaire luminous flux Minimum range 600Lm. IP protection rating : IP67. The luminaire should have multiple beam angle: 10°, 20, 40, 60°, 10X20° (as per site requirement) complete as required. Manufacturer should submit proper BIS certificate. | 97.00 | Nos. | 10.00 | 19485.00 | 1890045.00 | 18900.00 | 1833300.00 | 1833300.00 | SYNERGY LIGHTING SOLUTIONS
5.00 | Supply, Installation, testing and commissioning of RGBW linear wallwasher LED Light made of aluminium extrusion, exterior-rated linear luminaire (1000mm), Input Power 18W, Product should be equipped with inbuilt DMX 512 decoder with Same Ingress protection of Product for individual addressing and programming Rated input supply of Input Voltage 24V DC, Luminaire luminous flux Minimum range 720Lm. IP protection rating : IP67. The luminaire should have multiple beam angle: 10°, 20, 40, 60°, 10X20° (as per site requirement) complete as required. Manufacturer should submit proper BIS certificate. | 55.00 | Nos. | 10.00 | 19600.00 | 1078000.00 | 19040.00 | 1047200.00 | 1047200.00 | SYNERGY LIGHTING SOLUTIONS
6.00 | Supply, Installation, testing and commissioning of LED linear flexible fully diffused module strip made of Silicon with RGBW LEDs, 15Watts per mtr, Product should be programmable with inbuilt decoder, CRI > 80(for white), 600lumens per mtr. The entire led should be IP67 protected with sealed ends customized as per the various site requirement . Strip to be supplied with Aluminium channel. Manufacturer should submit proper BIS certificate. | 86.00 | Mtr. | 10.00 | 4485.00 | 385710.00 | 4240.00 | 364640.00 | 364640.00 | SYNERGY LIGHTING SOLUTIONS
7.00 | Supply, Installation, testing and commissioning of IP67 rated LED Driver for luminaries with Constant Voltage Output 24V DC. Power consumption should be 200W. BIS approved with the same make. | 50.00 | Nos. | 10.00 | 5942.00 | 297100.00 | 5620.00 | 281000.00 | 281000.00 | SYNERGY LIGHTING SOLUTIONS
8.00 | Supply, Installation, testing and commissioning of 120W image projector gobo light with IP65 rated with forced cooling system. Gobo should have input voltage- 100-240V AC. Product should be equipped with high power LED with efficacy 100Lm/W. Products lens coated with broadband green film and made of high temperature resistant schott glass. Body of the product made of Aluminium housing with adjustable lens mechanism. Manufacturer should submit proper BIS certificate. | 2.00 | Nos. | 10.00 | 154000.00 | 308000.00 | 185000.00 | 370000.00 | 308000.00 | SANGEETA ELECTRICALS
9.00 | Supply, Installation, testing and commissioning of 5M tubular Pole suitable for mounting of Image projector, Pole made up of MS pipe of 114.3 mm ( OD ) diameter, 3.6 mm thickness and MS Base plate of 225 x 225 x 12 mm and a top plate bracket with dimension of 250 x 250 x 10 mm thick, suitable for mounting one number of projector /GOBO. The post fabricated pole with bracket shall be Hot dip galvanized, minimum 60 micron from inside and outside as per IS 4759/ IS 2629, Pole & bracket with PU paint shall have 3 layer coating of minimum DFT level is 60 Microns. The pole fabricated using MIG welding process. The service door shall be provided at bottom section of pole to accommodate a built in connection box. (With MCB, Connectors) with 4nos of M16X450 long 'J' type EN 8 grade foundation bolts along with common template. | 2.00 | Nos. | 10.00 | 31120.00 | 62240.00 | 32140.00 | 64280.00 | 62240.00 | SANGEETA ELECTRICALS
10.00 | Supply, Installation, testing and commissioning of BIS approved 100W RGBW Square shaped Post top light based on DMX512 technology, design and aesthetic appearance providing a high IP 65 for tough environmental conditions, along with beautiful screwless design complimenting the geometry of the area with heritage touch. Product should be equipped with DMX 512 decoder with same ingress protection. It should consists of pressure die cast aluminum heat sink for effective thermal management, sturdiness & excellent corrosion resistant. Suitable for mounting on pole with OD of 76mm. Clear PC/ PMMA diffuser is used for high lumen, glare free light output, 360° light emission. Powered by BIS certified, built-in, potted electronic LED driver in ABS/ Metal housing with APFC (SMPS based constant current supply) with lower THD, Output Short / Open Circuit protection, Over Voltage protection, Surge Voltage protection 4.0 kV (CM & DM) & other safety test as per IS 15885 Part-2/Sec 13. | 26.00 | Nos. | 10.00 | 57142.00 | 1485692.00 | 54050.00 | 1405300.00 | 1405300.00 | SYNERGY LIGHTING SOLUTIONS
11.00 | Supply, Installation, testing and commissioning of Poly-Steel 3M Post Top Marine Class decorative FRP , 3M pole made from marine-grade fiberglass with UV-stabilized Class-1 polyester composites and 750 GSM glass fiber reinforcement. The inner frame consists of a hot dip galvanized 60 mm OD mild steel pipe (B Class) as per IS: 1161 or IS: 1239 standards, with a base plate conforming to IS 2062:2011, galvanized to average 65 microns post-fabrication for enhanced structural strength against high wind speeds. The poles feature a selfcolored, textured surface finish with scratch-resistant aliphatic grade UV-stabilized PU paint. Suitable for mounting with M14mm x 90mm anchor fasteners (SS 304 grade), This includes an access door at the base for MCB and power cable connections, supporting up to 4Cx16 sq. mm cables. The pole shall be suitable to mount Post top luminaire of 63 ID pipe. | 26.00 | Nos. | 10.00 | 56280.00 | 1463280.00 | 55260.00 | 1436760.00 | 1436760.00 | SYNERGY LIGHTING SOLUTIONS
12.00 | Supply, Installation, testing and commissioning of Signal Booster/Splitter with 8-Way output for spreading and amplyfing the DMX Data signals in multiple directions, Input-220-240V AC. BIS approved with the same make. | 5.00 | Nos. | 10.00 | 24000.00 | 120000.00 | 18500.00 | 92500.00 | 92500.00 | SYNERGY LIGHTING SOLUTIONS
13.00 | Supply, Installation, Testing and Commissioning of BIS approved DMX 512 Controller for the system including all other accessories. Controller should have Input Power 5-5.5V DC 0.6A and Output Protocol DMX512 with 4 universe. 2 universe should work in Stand Alone Mode and 2 universe should work in live mode with laptop/ tablet/computer. The universe should be expandable from 2 to 4 DMX512 universes. DMX controller should have network controllability feature to control the scene remotely through LAN and triggered via UDP packets on port 2430. Its must have Connections Type C USB, XLR3. There should be provision for Memory microSD card. Device should have Intuitive backlit keyboard with 10 presets and also have provision of keypad on device for changing scene manually from device. Device should be capable to work on Extended triggering possibilities (TCA) & also have a Smart Upgrade Technology (SUT). It is an IP 20 unit and has an Operating Temperature of 0°C to 50°C. OS Requirements for the controller is Mac OS X 10,8-10,12, Windows 7/8/10 64bit Standards ROHS, EMC, BIS approved with the same make | 1.00 | Nos. | 10.00 | 150000.00 | 150000.00 | 194590.00 | 194590.00 | 150000.00 | SANGEETA ELECTRICALS
14.00 | Supply, Installation, testing and commissioning of DMX Special cable DMX cable (single pair) having one 22AWG pair stranded (7x30) tinned copper conductors, Datalene (FHDPE) insulation, twisted pairs, overall Beldfoil shield (100% coverage) plus tinned copper braid, PVC jacket Cable. | 1850.00 | Mtr. | 10.00 | 200.00 | 370000.00 | 275.00 | 508750.00 | 370000.00 | SANGEETA ELECTRICALS
15.00 | Programming, Testing, Troubleshooting and synchronization of DMX control system.The addressing of fixtures with the multiple scenes (atleast 20 Themes) as per instruction of engineer in charge. | 1.00 | Job | 10.00 | 100000.00 | 100000.00 | 50000.00 | 50000.00 | 50000.00 | SYNERGY LIGHTING SOLUTIONS
16.00 | Supply, Installation, testing and commissioning of enclosure for Power Supply, Splitter, DMX Controller : Plain sides, grey cover, Degree of protection: IP 66/ IP 67, Impact strenght: IK 08, Material, base: Fiberglass reinforced polycarbonate, Material, cover: Polycarbonate, Material, cover screws: Polyamide, Material, gasket: Polyurethane, Colour: RAL 7035 | 33.00 | Nos. | 10.00 | 8857.00 | 292281.00 | 8370.00 | 276210.00 | 276210.00 | SYNERGY LIGHTING SOLUTIONS
17.00 | Supply, Installation, testing and commissioning of Poly-Steel 3.8M Single arm Marine Class decorative FRP Pole , 3.8 M pole made from marine-grade fiberglass with UV-stabilized Class-1 polyester composites and 750 GSM glass fiber reinforcement. The inner frame consists of a hot dip galvanized 60 mm OD mild steel pipe (B Class) as per IS: 1161 or IS: 1239 standards, with a base plate conforming to IS 2062:2011, galvanized to average 65 microns post-fabrication for enhanced structural strength against high wind speeds. The poles feature a selfcolored, textured surface finish with scratch-resistant aliphatic grade UV-stabilized PU paint. Suitable for mounting with M14mm x 90mm anchor fasteners (SS 304 grade), This include an access door at the base for MCB and power cable connections, supporting up to 4Cx16 sq. mm cables. The pole shall be suitable to mount Post top luminaire of 63 ID pipe. | 10.00 | Nos. | 10.00 | 62831.00 | 628310.00 | 62140.00 | 621400.00 | 621400.00 | SYNERGY LIGHTING SOLUTIONS
18.00 | Supply, Installation, testing and commissioning of 45 W LED drop down light fixture made up of aluminum housing optical grade clear injection moulded PC diffuser, High pressure die cast aluminum heat sink, IP 66, IK 08 of impact resistance diffuser protection, CCT 5700K / 3000 K, CRI >70. | 10.00 | Nos. | 10.00 | 15085.00 | 150850.00 | 14270.00 | 142700.00 | 142700.00 | SYNERGY LIGHTING SOLUTIONS
19.00 | SITC of Wall/ Floor mounted CPRI tested Timer Based Light Control Panel (Feeder Pillar) with rated Al. Bus Bar suitable for 415V, 3 phase, 4 wire, 50 Hz, power supply distribution system. The panel shall be double door conforming to IP 54. The painting process shall conform to relevant IS code for out door application. I/C: 63A FP MCB - 1 No. + Indication Lamp + 63A FP CONTACTOR (AC-1 duty) + A/M Selector switch + Time switch including making connection, etc. as required O/G : 20A FP MCB - 5 Nos. Complete Set of Feeder Pillar as above | 1.00 | Set | 10.00 | 100000.00 | 100000.00 | 110000.00 | 110000.00 | 100000.00 | SANGEETA ELECTRICALS
20.00 | Supply of following sizes of 1.1kv grade multicore Aluminium conductor XLPE insulated PVC sheathed armoured cable (as per IS : 7098:1988 with upto date amendments) complete as requried as per specifications.
20.01 | 4C x 25 Sqmm Al. LT XLPE Cable | 150.00 | Mtr | 10.00 | 490.00 | 73500.00 | 465.00 | 69750.00 | 69750.00 | SYNERGY LIGHTING SOLUTIONS
20.02 | 4C x 10 Sqmm Al. LT XLPE Cable | 700.00 | Mtr | 10.00 | 350.00 | 245000.00 | 330.00 | 231000.00 | 231000.00 | SYNERGY LIGHTING SOLUTIONS
21.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/ HUME/ METAL/ HDPE pipe as required.
21.01 | Upto 35 sq. mm | 600.00 | Mtr | 10.00 | 57.00 | 34200.00 | 55.00 | 33000.00 | 33000.00 | SYNERGY LIGHTING SOLUTIONS
22.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on cable tray as required.
22.01 | Upto 35 sq. mm (clamped with 1mm thick saddle) | 200.00 | Mtr | 10.00 | 114.00 | 22800.00 | 110.00 | 22000.00 | 22000.00 | SYNERGY LIGHTING SOLUTIONS
23.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on wall surface as required.
23.01 | Upto 35 sq. mm (clamped with 1mm thick saddle) | 50.00 | Mtr | 10.00 | 120.00 | 6000.00 | 110.00 | 5500.00 | 5500.00 | SYNERGY LIGHTING SOLUTIONS
24.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
24.01 | 4C X 10 sq. mm (25mm) | 2.00 | Each | 10.00 | 285.00 | 570.00 | 270.00 | 540.00 | 540.00 | SYNERGY LIGHTING SOLUTIONS
24.02 | 4C X 25 sq. mm (28mm) | 2.00 | Each | 10.00 | 428.00 | 856.00 | 405.00 | 810.00 | 810.00 | SYNERGY LIGHTING SOLUTIONS
24.03 | 3.5C X 35 sq. mm (32mm) | 1.00 | Each | 10.00 | 570.00 | 570.00 | 540.00 | 540.00 | 540.00 | SYNERGY LIGHTING SOLUTIONS
25.00 | Supply & laying of following sizes P.V.C. insulated & P.V.C. sheathed cable of 1.1 KV grade flexible copper conductor confirming to IS:694 in existing pipe/ conduit including making necessary connection, testing etc. as required.
25.01 | 5C x 4.0 Sqmm Copper Flexible Cable | 175.00 | Mtr | 10.00 | 651.00 | 113925.00 | 610.00 | 106750.00 | 106750.00 | SYNERGY LIGHTING SOLUTIONS
25.02 | 3C x 2.5 Sqmm Copper Flexible Cable | 75.00 | Mtr | 10.00 | 237.00 | 17775.00 | 225.00 | 16875.00 | 16875.00 | SYNERGY LIGHTING SOLUTIONS
25.03 | 2C x 1.5 Sqmm Copper Flexible Cable | 300.00 | Mtr | 10.00 | 104.00 | 31200.00 | 100.00 | 30000.00 | 30000.00 | SYNERGY LIGHTING SOLUTIONS
26.00 | Supplying and laying of following size DWC HDPE pipe ISI marked along with all accessories like socket, bend, couplers etc. conforming to IS 14930, Part II complete with fitting and cutting, jointing etc.direct in ground (75 cm below ground level) including excavation and refilling the trench but excluding sand cushioning and protective covering etc., complete as required.
26.01 | 63 mm dia (OD-63 mm & ID-51 mm nominal) | 800.00 | Mtr | 10.00 | 285.00 | 228000.00 | 160.00 | 128000.00 | 128000.00 | SYNERGY LIGHTING SOLUTIONS
27.00 | Supplying and fixing of following sizes of medium class PVC conduit along with accessories in surface/recess including cutting the wall and making good the same in case of recessed conduit as required.
27.01 | 20 mm | 400.00 | Mtr | 10.00 | 171.00 | 68400.00 | 100.00 | 40000.00 | 40000.00 | SYNERGY LIGHTING SOLUTIONS
27.02 | 25 mm | 300.00 | Mtr | 10.00 | 200.00 | 60000.00 | 120.00 | 36000.00 | 36000.00 | SYNERGY LIGHTING SOLUTIONS
28.00 | Supplying and fixing of following sizes of PVC flexible conduit along with accessories in surface/recess including cutting the wall and making good the same in case of recessed conduit as required.
28.01 | 20 mm | 300.00 | Mtr | 10.00 | 57.00 | 17100.00 | 50.00 | 15000.00 | 15000.00 | SYNERGY LIGHTING SOLUTIONS
28.02 | 25 mm | 300.00 | Mtr | 10.00 | 85.00 | 25500.00 | 70.00 | 21000.00 | 21000.00 | SYNERGY LIGHTING SOLUTIONS
29.00 | Junction Box & Accessories Supply & fixing of outdoor type cable Junction Box with terminals/ Connector IP65/66 suitable for Terminating/ Loop-in Loop-out of 4.0/2.5 sqmm Cu flexible cable including all acessories | 5.00 | Nos. | 10.00 | 4570.00 | 22850.00 | 4320.00 | 21600.00 | 21600.00 | SYNERGY LIGHTING SOLUTIONS
30.00 | Earthing with G.I. earth pipe 4.5 meter long, 40 mm dia including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe etc. (with charcoal/ coke and salt ) as required. | 4.00 | Set | 10.00 | 10000.00 | 40000.00 | 5500.00 | 22000.00 | 22000.00 | SYNERGY LIGHTING SOLUTIONS
31.00 | Providing and fixing 25 mm X 5 mm G.I. strip in 40 mm dia G.I. pipe from earth electrode including connection with G.I. nut, bolt, spring, washer excavation and re-filling etc. as required. | 20.00 | Mtr | 10.00 | 1142.00 | 22840.00 | 400.00 | 8000.00 | 8000.00 | SYNERGY LIGHTING SOLUTIONS
32.00 | Providing and laying in position 1:2:4 reinforced cement concrete foundation (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size) made out of M-20 grade concrete of size 350 mm (L) x 350 mm wide and 900 mm deep including excavation of earth, providing cutting, bending and placing in position, reinforcement of cold twisted bars of 12mm dia and suitable length - 04 nos. and reinforcement ring of cold twisted bar of 8mm dia and suitable length - 06 nos. (with suitable spacing) as required with positioning of foundation bolt set and providing 63 mm. diameter (O.D) DWC, HDPE Pipe for cable entry & exit etc complete as required. | 38.00 | Each | 10.00 | 5000.00 | 190000.00 | 7000.00 | 266000.00 | 190000.00 | SANGEETA ELECTRICALS
33.00 | Supply and laying of 63 mm dia (OD-63 mm & ID-51 mm nominal) DWC HDPE pipe ISI marked along with all accessories like socket, bend, couplers etc. conforming to IS 14930, Part II complete with fitting, cutting, jointing etc. through moling at a depth of 75 cms including excavation and refilling as required. | 20.00 | Mtr | 10.00 | 300.00 | 6000.00 | 160.00 | 3200.00 | 3200.00 | SYNERGY LIGHTING SOLUTIONS
34.00 | Feeder pillar SITC of outdoor cubicle type, totally enclosed, free standing, dust free, damp and vermin proof, floor mounted distribution feeder pillar of suitable size on cement concrete foundations on suitable MS angle base frame i/c grouting the stand with concrete mortar (As per standard or directed by EIC) nut bolts etc as required, conforming to IS 5039 & IP 54 and to withstand rough usage and weather. The panel shall be fabricated with 14 SWG M.S. sheet with suitable flat iron frame work complete with hinged door on front with locking arrangement, doors/covers for individual inside compartments, suitable angle/channels frame in the bottom, legs for grouting in foundation, painting etc. including supplying and fixing of following accessories and making inter connections, earth connection etc. as required. The feedar pillar shall comprising of followings: INCOMER 1 No.125 Amp, four pole Moulded Case Circuit Breaker (Ics = Icu = 20KA) with built in thermal magnetic release unit with O/L,S/C as per specification Incomer shall have one set of the following items: 0 - 500 Volt Digital voltmeter, 96 mm square flush pattern, with selector switch, and back up 2 Amp MCBs - 1 Set 1 No. Digital Ammeter (0-125Amp) with selector switch and one set of 3 nos. CTs of ratio 125/5A , Class I accuracy and 15 VA burden- 1set. 3 Nos.phase indicating LED lamps each with 2 amp back up MCB. BUSBARS TPN aluminium bus bars of minimum 200 Amps capacity with heat shrinkable coloured sleeves and i/c, SMC bus bars supports at required intervals complete for cross section, size supports & their spacing etc. for withstanding fault level of 20Ka for 1 sec. OUTGOING 63 Amps 4 pole, 10kA, C-curve MCB - 2 sets 32 Amps 4 pole, 10kA, C-curve MCB - 6 sets | 1.00 | Job | 10.00 | 200000.00 | 200000.00 | 148000.00 | 148000.00 | 148000.00 | SYNERGY LIGHTING SOLUTIONS
| Total in Figures |  |  |  |  | 13324514.00 |  | 12922195.00
Lowest Amount Quoted BY: SYNERGY LIGHTING SOLUTIONS(12922195.00)

## BOQ Summary
BOQ Summary Details Tender Title: Misc. Electrical works at Safdarjung Airport, New Delhi. Tender ID: 2025_AAI_238100_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | SYNERGY LIGHTING SOLUTIONS (BID ID -868887) | 12922195.00 | L1
| 2 | SANGEETA ELECTRICALS (BID ID -868925) | 13324514.00 | L2