## BoQ1
Government eProcurement System Created By: Dadan Singh Created Date/Time: 22-Jul-2025 04:53 PM Tender Title: Provision of STP for ATC Tower, New MSSR and New Fire Station at R. B. Airport, Bhopal. Tender ID: 2025_AAI_238591_1
Tender Inviting Authority: AGM(E-E), AAI, R.B. Airport, Bhopal
Name of Work: Provision of STP for ATC Tower, New MSSR & New Fire Station at R. B. Airport, Bhopal.
Contract No: AAI/BPL/ENGG(E)/NIT-05/2025-26
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | AQUAWHIZZ (GSTN-NA) BID ID -869988 |  | Max Tech Infra Projects Pvt Ltd (GSTN-NA) BID ID -869292 |  | greenagersenviro solutions and services pvt. ltd. (GSTN-NA) BID ID -870445 |  | Unistar environment and research labs pvt. ltd. (GSTN-NA) BID ID -871374
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Design, Supply, Installation, Testing & Commissioning of Membrane Bio Reactor (MBR), Sewage Water Treatment Plant of 10 KLD Capacity System. The unit should be suitable for all phases (loading, Aeration, rest, clear water extraction) Semi treated water from settling/ Sedimentation zone shall be tertiary treated using a pressure sand filter, Activated Carbon Filter (ACF) followed by UV filteration system. Plant must have fully automatic operation i/c PLC controller, alarm for CIP & mains failure. The system must have adequate retention times for all process including min. 8 Hrs. for Aeration. System must be designed to meet the outlet parameters given below:
1.01 | INLET EFFLUENT CHARACTERSTICS pH - 6.5 –8.0 BOD less than 350 mg/L S. Solids less than 400 mg/L COD less than 450 mg/L Oil & Grease - 40-50 mg / L DISCHARGE EFFLUENT CHARACTERSTICS AFTER UV TREATMENT pH - 7.0 – 8.0 BOD - Less than 10 mg/L S. Solids - Less than 10 mg/L COD - Less than 50 mg/L Oil & Grease - Less than 5 mg/L
1.02 | BAR SCREEN - COARSE Qty: 1 Job Pore Size: 12 mm MOC: SS 304 Operation: Manual BAR SCREEN - FINE Qty: Job Pore Size: 6 mm MOC: SS 304 Operation: Manual
1.03 | MBR FEED PUMPS (Raw Sewage Transfer Pump from EQT to Aeration) – P1 Qty: 2 Nos. (1W+1S) MOC: Cast Iron Type: Monoblock (Self priming) Seal: Mechanical Seal (Cartridge type) Flow Rate: 1.0 M³ / Hr Head Range: 10 - 12 Meter Motor Power: 1 HP Motor Efficiency, Phase / Volt: IE 3, Three Phase/ 415 Volt Insulation Class: F with IP 55 Enclosure ANOXIC MIXER (AGITATOR) Qty: 1 Job Rod Length: 1.2 Meter Long MOC: SS Stroke Speed: 50 - 60 RPM Motor Power: 0.5 HP Motor Efficiency, Phase/ Volt: IE 3, Three Phase/ 415 Volt
1.04 | COMMON BLOWER FOR EQT TANK, AERATION TANK AND MBR TANK – B1 Make: ABL / Aakash Qty: 2 Nos. (1W+1S) Air required for EQT: 5 Nm³ / Hr Air required for Aeration: 10 Nm³ / Hr Air required for MBR: 10 Nm³ / Hr Air required for SHT: 5 Nm³ / Hr Total Air required for Entire: 30 Nm³ / Hr Each Air Blower Capacity: 30 Nm³ / Hr Head of Blower: 0.4 Kg / cm2 Blower Motor Power: 1.0 HP Blowers Type: Twin lobe root blower Blower Motor Make: Crompton Motor Efficiency, Phase / Volt: IE 3, Three Phase/ 415 Volt
1.05 | MANUAL FINE SCREEN Qty: 1 Job Pore Size: 3 MM, Punched Hole Screen MOC: SS 304 Operation: Manual MBR - MEMBRANE SPECIFICATION Make: Imemflo Germany Qty: 1 Nos. Module Daily Flow: 10 M³ / Day Operation Time: 20 Hrs Design Flux: LMH Designed Membrane Area: 10 M³ Type of Membrane: HOLLOW FIBER Pore Size: 0.1 µ Area of Cassette: 0.8 M² No. of Cassettes per module: As per Design Deck: 01 Proposed Membrance Area: 10 M²
1.06 | Module Specifications: Model No.: IA 10 No. of Module: 01 No. Membrane area per module: 10M² Total Membrane per module: 10M² Air requires per cassette: 0.6 Nm³ / Hr Air requires per module: 10 Nm³ / Hr Length: 610 mm Width (Thickness): 45 mm Height: 1200 mm MOC of Membrane: PVDF MOC of frame: SS 304 MOC of air diffuser: PP
1.07 | RECIRCULATION ACTIVATED SLUDGE TRANSFER PUMPS – P2 Qty: 2 Nos. (1W+1S) MOC: Cast Iron Type: Self-Priming Coupled Seal: Mechanical Seal (Cartridge type) Flow Rate: 1.0 N³ / Hr Head Range: 10 - 12 Meter Motor Power: 0.5 HP Motor Efficiency, Phase/ Volt: IE 3, Three Phase/ 415 Volt Insulation Class: F with IP 55 Enclosure PERMEAT (MBR Treated) WATER SUCTION PUMPS – P3 Qty: 2 Nos. (1W+1S) MOC: Cast Iron Type: Self-Priming Coupled Seal: Mechanical Seal (Cartridge type) Flow Rate: 1.0 M³ / Hr Head Range: 10 - 12 Meter Motor Power: 1 HP Motor Efficiency, Phase/ Volt: IE 3, Three Phase/ 415 Volt Insulation Class: F with IP 55 Enclosure
1.08 | BACK PULSE PUMP/ CIP PUMPS – P4 Qty: 2 Nos. (1W+1S) MOC: SS Casing, SS Impeller & SS Shaft Type: Monoblock (non-submersible) Seal: Mechanical Seal (Cartridge type) Flow Rate: 1.0 M³ / Hr Head Range: 10 - 12 Meter Motor Power: 0.5 HP Motor Efficiency, Phase/ Volt: IE 3, Three Phase/ 415 Volt Insulation Class: F with IP 55 Enclosure DRAINAGE SUMP PUMPS – P5 Qty: 2 Nos. (1W+1S) MOC: SS Casing, SS Impeller & SS Shaft Type: Submersible Seal: Mechanical Seal (Cartridge type) Flow Rate: 3.0 M³ / Hr Head Range: 10 - 15 Meter Motor Power: 1 HP Motor Efficiency, Phase/ Volt: IE 3, Three Phase/ 415 Volt Insulation Class: F with IP 55 Enclosure
1.09 | BACK PULSE TANK (CIP TANK) Qty: 1 No. Tank MOC: LLDPE – 2000Ltr HYPO DOSING SYSTEM FOR MAINTENANCE CLEANING Dosing Pump Make: Milton Roy Qty (Pumps & Tank): 1 Job Dosing Pump Capacity: 0 - 6 LPH Pump Type: Diaphragm Motor Power: 0.25 kW Dosing Tank Capacity: 100 Liters Dosing Tank MOC: LLDPE
1.10 | CITRIC ACID DOSING SYSTEM FOR MAINTENANCE CLEANING Frequency: Once in year or as required Dosing Pump Make: Milton Roy Qty (Pumps & Tank): 1 Nos. Dosing Pump Capacity: 0 - 6 LPH Pump Type: Diaphragm Motor Power: 0.25 kW Dosing Tank Capacity: 100 Liters Dosing Tank MOC: LLDPE POLY ELECTROLYTE DOSING SYSTEM FOR Sludge Thickness Dosing Pump Make: Milton Roy Qty (Pumps & Tank): 1 Nos. Dosing Pump Capacity: 0 - 6 LPH Pump Type: Diaphragm Motor Power: 0.25 kW Dosing Tank Capacity: 100 Liters Dosing Tank MOC: LLDPE
1.11 | FILTER PRESS FEED PUMP SCREW TYPE – P6 Qty: 2 Nos. (1W+1S) Type: Screw Pump Pumping Fluid: Sludge Suction Head: Flooded Flow Rate: 1.0 M³ / Hr Head Range: 40 - 50 Meter MOC: CI Suction & Delivery Position: Top/ End Motor Power: 1.0 HP/ 0.75 kW Motor Efficiency, Phase/ Volt: IE 3, Three Phase/ 415 Volt WASTE ACTIVATED SLUDGE HANDLING – FILTER PRESS Make: Pharmatech Qty: 1 Nos. Type of filter press: Plate type Plate Dia x Height: 18” x 18” inch Max. Permissible Load: 500Ltr Make of Unit: PP Motor Power: 0.5 HP
1.12 | SEWAGE TREATMENT PLANT (MBR Technology 10 KLD Packaged Fully Automatic Operation) | 1.00 | Each |  | 1500000.00 | 1500000.00 | 1150000.00 | 1150000.00 | 1350000.00 | 1350000.00 | 1716000.00 | 1716000.00 | 1150000.00 | Max Tech Infra Projects Pvt Ltd
2.00 | Design, Supply, Installation, Testing & Commissioning of Membrane Bio Reactor (MBR), Sewage Water Treatment Plant of 5 KLD Capacity System. The unit should be suitable for all phases (loading, Aeration, rest, clear water extraction) Semi treated water from settling/ Sedimentation zone shall be tertiary treated using a pressure sand filter, Activated Carbon Filter (ACF) followed by UV filteration system. Plant must have fully automatic operation i/c PLC controller, alarm for CIP & mains failure. The system must have adequate retention times for all process including min. 8 Hrs. for Aeration. System must be designed to meet the outlet parameters given below:
2.01 | INLET EFFLUENT CHARACTERSTICS pH - 6.5 –8.0 BOD less than 350 mg/L S. Solids less than 400 mg/L COD less than 450 mg/L Oil & Grease - 40-50 mg / L DISCHARGE EFFLUENT CHARACTERSTICS AFTER UV TREATMENT pH - 7.0 – 8.0 BOD - Less than 10 mg/L S. Solids - Less than 10 mg/L COD - Less than 50 mg/L Oil & Grease - Less than 5 mg/L
2.02 | BAR SCREEN - COARSE Qty: 1 Job Pore Size: 12 mm MOC: SS 304 Operation: Manual BAR SCREEN - FINE Qty: Job Pore Size: 6 mm MOC: SS 304 Operation: Manual
2.03 | MBR FEED PUMPS (Raw Sewage Transfer Pump from EQT to Aeration) – P1 Qty: 2 Nos. (1W+1S) MOC: Cast Iron Type: Monoblock (Self priming) Seal: Mechanical Seal (Cartridge type) Flow Rate: 1.0 M³ / Hr Head Range: 10 - 12 Meter Motor Power: 1 HP Motor Efficiency, Phase / Volt: IE 3, Three Phase/ 415 Volt Insulation Class: F with IP 55 Enclosure ANOXIC MIXER (AGITATOR) Qty: 1 Job Rod Length: 1.2 Meter Long MOC: SS Stroke Speed: 50 - 60 RPM Motor Power: 0.5 HP Motor Efficiency, Phase/ Volt: IE 3, Three Phase/ 415 Volt
2.04 | COMMON BLOWER FOR EQT TANK, AERATION TANK AND MBR TANK – B1 Make: ABL / Aakash Qty: 2 Nos. (1W+1S) Air required for EQT: 5 Nm³ / Hr Air required for Aeration: 10 Nm³ / Hr Air required for MBR: 10 Nm³ / Hr Air required for SHT: 5 Nm³ / Hr Total Air required for Entire: 30 Nm³ / Hr Each Air Blower Capacity: 30 Nm³ / Hr Head of Blower: 0.4 Kg / cm2 Blower Motor Power: 1.0 HP Blowers Type: Twin lobe root blower Blower Motor Make: Crompton Motor Efficiency, Phase / Volt: IE 3, Three Phase/ 415 Volt
2.05 | MANUAL FINE SCREEN Qty: 1 Job Pore Size: 3 MM, Punched Hole Screen MOC: SS 304 Operation: Manual MBR - MEMBRANE SPECIFICATION Make: Imemflo Germany Qty: 1 Nos. Module Daily Flow: 10 M³ / Day Operation Time: 20 Hrs Design Flux: LMH Designed Membrane Area: 10 M³ Type of Membrane: HOLLOW FIBER Pore Size: 0.1 µ Area of Cassette: 0.8 M² No. of Cassettes per module: As per Design Deck: 01 Proposed Membrance Area: 10 M²
2.06 | Module Specifications: Model No.: IA 10 No. of Module: 01 No. Membrane area per module: 10M² Total Membrane per module: 10M² Air requires per cassette: 0.6 Nm³ / Hr Air requires per module: 10 Nm³ / Hr Length: 610 mm Width (Thickness): 45 mm Height: 1200 mm MOC of Membrane: PVDF MOC of frame: SS 304 MOC of air diffuser: PP
2.07 | RECIRCULATION ACTIVATED SLUDGE TRANSFER PUMPS – P2 Qty: 2 Nos. (1W+1S) MOC: Cast Iron Type: Self-Priming Coupled Seal: Mechanical Seal (Cartridge type) Flow Rate: 1.0 N³ / Hr Head Range: 10 - 12 Meter Motor Power: 0.5 HP Motor Efficiency, Phase/ Volt: IE 3, Three Phase/ 415 Volt Insulation Class: F with IP 55 Enclosure PERMEAT (MBR Treated) WATER SUCTION PUMPS – P3 Qty: 2 Nos. (1W+1S) MOC: Cast Iron Type: Self-Priming Coupled Seal: Mechanical Seal (Cartridge type) Flow Rate: 1.0 M³ / Hr Head Range: 10 - 12 Meter Motor Power: 1 HP Motor Efficiency, Phase/ Volt: IE 3, Three Phase/ 415 Volt Insulation Class: F with IP 55 Enclosure
2.08 | BACK PULSE PUMP/ CIP PUMPS – P4 Qty: 2 Nos. (1W+1S) MOC: SS Casing, SS Impeller & SS Shaft Type: Monoblock (non-submersible) Seal: Mechanical Seal (Cartridge type) Flow Rate: 1.0 M³ / Hr Head Range: 10 - 12 Meter Motor Power: 0.5 HP Motor Efficiency, Phase/ Volt: IE 3, Three Phase/ 415 Volt Insulation Class: F with IP 55 Enclosure DRAINAGE SUMP PUMPS – P5 Qty: 2 Nos. (1W+1S) MOC: SS Casing, SS Impeller & SS Shaft Type: Submersible Seal: Mechanical Seal (Cartridge type) Flow Rate: 3.0 M³ / Hr Head Range: 10 - 15 Meter Motor Power: 1 HP Motor Efficiency, Phase/ Volt: IE 3, Three Phase/ 415 Volt Insulation Class: F with IP 55 Enclosure
2.09 | BACK PULSE TANK (CIP TANK) Qty: 1 No. Tank MOC: LLDPE – 2000Ltr HYPO DOSING SYSTEM FOR MAINTENANCE CLEANING Dosing Pump Make: Milton Roy Qty (Pumps & Tank): 1 Job Dosing Pump Capacity: 0 - 6 LPH Pump Type: Diaphragm Motor Power: 0.25 kW Dosing Tank Capacity: 100 Liters Dosing Tank MOC: LLDPE
2.10 | CITRIC ACID DOSING SYSTEM FOR MAINTENANCE CLEANING Frequency: Once in year or as required Dosing Pump Make: Milton Roy Qty (Pumps & Tank): 1 Nos. Dosing Pump Capacity: 0 - 6 LPH Pump Type: Diaphragm Motor Power: 0.25 kW Dosing Tank Capacity: 100 Liters Dosing Tank MOC: LLDPE POLY ELECTROLYTE DOSING SYSTEM FOR Sludge Thickness Dosing Pump Make: Milton Roy Qty (Pumps & Tank): 1 Nos. Dosing Pump Capacity: 0 - 6 LPH Pump Type: Diaphragm Motor Power: 0.25 kW Dosing Tank Capacity: 100 Liters Dosing Tank MOC: LLDPE
2.11 | FILTER PRESS FEED PUMP SCREW TYPE – P6 Qty: 2 Nos. (1W+1S) Type: Screw Pump Pumping Fluid: Sludge Suction Head: Flooded Flow Rate: 1.0 M³ / Hr Head Range: 40 - 50 Meter MOC: CI Suction & Delivery Position: Top/ End Motor Power: 1.0 HP/ 0.75 kW Motor Efficiency, Phase/ Volt: IE 3, Three Phase/ 415 Volt WASTE ACTIVATED SLUDGE HANDLING – FILTER PRESS Make: Pharmatech Qty: 1 Nos. Type of filter press: Plate type Plate Dia x Height: 18” x 18” inch Max. Permissible Load: 500Ltr Make of Unit: PP Motor Power: 0.5 HP
2.12 | SEWAGE TREATMENT PLANT (MBR Technology 5 KLD Packaged Fully Automatic Operation) | 1.00 | Each |  | 1550000.00 | 1550000.00 | 1050000.00 | 1050000.00 | 1350000.00 | 1350000.00 | 1458600.00 | 1458600.00 | 1050000.00 | Max Tech Infra Projects Pvt Ltd
3.00 | Supply of PVC insulated and PVC sheathed aluminium conductor FRLSH armoured cable of 1.1 KV grade conforming to IS: 1554 (Part: I) / 1988 with upto date amendments etc., as required. 4 C x 25 Sq.mm | 200.00 | Meter |  | 230.00 | 46000.00 | 200.00 | 40000.00 | 211.00 | 42200.00 | 221.60 | 44320.00 | 40000.00 | Max Tech Infra Projects Pvt Ltd
4.00 | Supplying and laying of following size DWC HDPE pipe ISI marked along with all accessories like socket, bend, couplers etc. conforming to IS 14930, Part II complete with fitting and cutting, jointing etc.direct in ground (75 cm below ground level) including excavation and refilling the trench but excluding sand cushioning and protective covering etc., complete as required. 63 mm dia (OD-63 mm & ID-50 mm nominal) | 200.00 | Meter |  | 500.00 | 100000.00 | 105.00 | 21000.00 | 152.00 | 30400.00 | 245.00 | 49000.00 | 21000.00 | Max Tech Infra Projects Pvt Ltd
5.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 kV grade of following size in the existing RCC/ HUME/ METAL/DWC pipe as required. Upto 35 sq. mm | 200.00 | Meter |  | 25.00 | 5000.00 | 122.00 | 24400.00 | 84.00 | 16800.00 | 526.00 | 105200.00 | 5000.00 | AQUAWHIZZ
6.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 kV grade as required. 4C x 25 sq. mm | 4.00 | Set |  | 200.00 | 800.00 | 665.00 | 2660.00 | 296.00 | 1184.00 | 66.82 | 267.28 | 267.28 | Unistar environment and research labs pvt. ltd.
7.00 | Earthing with G.I. earth pipe 4.5 metre long, 40 mm dia including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe etc. with charcoal/ coke and salt as required. | 4.00 | Set |  | 4000.00 | 16000.00 | 10000.00 | 40000.00 | 847.00 | 3388.00 | 227.00 | 908.00 | 908.00 | Unistar environment and research labs pvt. ltd.
8.00 | Providing and fixing 25 mm X 5 mm G.I. strip in 40 mm dia G.I. pipe from earth electrode including connection with G.I. nut, bolt, spring, washer excavation and re-filling etc. as required. | 50.00 | Meter |  | 400.00 | 20000.00 | 200.00 | 10000.00 | 161.00 | 8050.00 | 1410.75 | 70537.50 | 8050.00 | greenagersenviro solutions and services pvt. ltd.
9.00 | Providing and fixing 25 mm x 5 mm GI strip on surface or in recess for connections etc. as required. | 20.00 | Meter |  | 70.00 | 1400.00 | 195.00 | 3900.00 | 161.00 | 3220.00 | 1410.75 | 28215.00 | 1400.00 | AQUAWHIZZ
10.00 | Supplying and fixing following way, horizontal type three pole and neutral, sheet steel, MCB distribution board, 415 V, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCB/RCCB/Isolator) 8 way (4 + 24), Double door | 1.00 | Each |  | 5000.00 | 5000.00 | 5000.00 | 5000.00 | 508.00 | 508.00 | 2301.75 | 2301.75 | 508.00 | greenagersenviro solutions and services pvt. ltd.
11.00 | Supplying and fixing 5 A to 32 A rating, 240/415 V, 10 kA, "C" curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required. Triple Pole and Neutral | 1.00 | Each |  | 1000.00 | 1000.00 | 6500.00 | 6500.00 | 1864.00 | 1864.00 | 1262.25 | 1262.25 | 1000.00 | AQUAWHIZZ
12.00 | Supplying and fixing 5 A to 32 A rating, 240/415 V, 10 kA, "C" curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required. Single pole | 24.00 | Each |  | 175.00 | 4200.00 | 650.00 | 15600.00 | 1525.00 | 36600.00 | 215.32 | 5167.68 | 4200.00 | AQUAWHIZZ
13.00 | AICMC work for 10 KLD after 01 Year DLP AICMC for 1st Year after Defects Liability Period (A) Bi-Monthly visit of technical person to check the STP plant and unlimited breakdown calls. (B) Repairing of Pumps, motors, Panel, Filter, UV, piping, cabling and filters work etc. whenever required for smooth operation of STP. (C) In the MBR STP as and when required to replace membrane, agency will replace immiediatly. (D) Materials likes Sodium Hypochlorite and any other chemical and materials required for smooth operation of STP will be provided by the agency. | 1.00 | Each |  | 50000.00 | 50000.00 | 150000.00 | 150000.00 | 101694.00 | 101694.00 | 180000.00 | 180000.00 | 50000.00 | AQUAWHIZZ
14.00 | AICMC for 2nd Year after Defects Liability Period (A) Bi-Monthly visit of technical person to check the STP plant and unlimited breakdown calls. (B) Repairing of Pumps, motors, Panel, Filter, UV, piping, cabling and filters work etc. whenever required for smooth operation of STP. (C) In the MBR STP as and when required to replace membrane, agency will replace immiediatly. (D) Materials likes Sodium Hypochlorite and any other chemical and materials required for smooth operation of STP will be provided by the agency. | 1.00 | Each |  | 50000.00 | 50000.00 | 150000.00 | 150000.00 | 122033.00 | 122033.00 | 180000.00 | 180000.00 | 50000.00 | AQUAWHIZZ
15.00 | AICMC for 3rd Year after Defects Liability Period (A) Bi-Monthly visit of technical person to check the STP plant and unlimited breakdown calls. (B) Repairing of Pumps, motors, Panel, Filter, UV, piping, cabling and filters work etc. whenever required for smooth operation of STP. (C) In the MBR STP as and when required to replace membrane, agency will replace immiediatly. (D) Materials likes Sodium Hypochlorite and any other chemical and materials required for smooth operation of STP will be provided by the agency. | 1.00 | Each |  | 50000.00 | 50000.00 | 150000.00 | 150000.00 | 132203.00 | 132203.00 | 180000.00 | 180000.00 | 50000.00 | AQUAWHIZZ
16.00 | AICMC for 4th Year after Defects Liability Period (A) Bi-Monthly visit of technical person to check the STP plant and unlimited breakdown calls. (B) Repairing of Pumps, motors, Panel, Filter, UV, piping, cabling and filters work etc. whenever required for smooth operation of STP. (C) In the MBR STP as and when required to replace membrane, agency will replace immiediatly. (D) Materials likes Sodium Hypochlorite and any other chemical and materials required for smooth operation of STP will be provided by the agency. | 1.00 | Each |  | 50000.00 | 50000.00 | 150000.00 | 150000.00 | 142372.00 | 142372.00 | 180000.00 | 180000.00 | 50000.00 | AQUAWHIZZ
17.00 | AICMC for 5th Year after Defects Liability Period (A) Bi-Monthly visit of technical person to check the STP plant and unlimited breakdown calls. (B) Repairing of Pumps, motors, Panel, Filter, UV, piping, cabling and filters work etc. whenever required for smooth operation of STP. (C) In the MBR STP as and when required to replace membrane, agency will replace immiediatly. (D) Materials likes Sodium Hypochlorite and any other chemical and materials required for smooth operation of STP will be provided by the agency. | 1.00 | Each |  | 50000.00 | 50000.00 | 150000.00 | 150000.00 | 152542.00 | 152542.00 | 180000.00 | 180000.00 | 50000.00 | AQUAWHIZZ
18.00 | AICMC work for 5 KLD after 01 Year DLP AICMC for 1st Year after Defects Liability Period (A) Bi-Monthly visit of technical person to check the STP plant and unlimited breakdown calls. (B) Repairing of Pumps, motors, Panel, Filter, UV, piping, cabling and filters work etc. whenever required for smooth operation of STP. (C) In the MBR STP as and when required to replace membrane, agency will replace immiediatly. (D) Materials likes Sodium Hypochlorite and any other chemical and materials required for smooth operation of STP will be provided by the agency. | 1.00 | Each |  | 50000.00 | 50000.00 | 50000.00 | 50000.00 | 101694.00 | 101694.00 | 180000.00 | 180000.00 | 50000.00 | Max Tech Infra Projects Pvt Ltd, AQUAWHIZZ
19.00 | AICMC for 2nd Year after Defects Liability Period (A) Bi-Monthly visit of technical person to check the STP plant and unlimited breakdown calls. (B) Repairing of Pumps, motors, Panel, Filter, UV, piping, cabling and filters work etc. whenever required for smooth operation of STP. (C) In the MBR STP as and when required to replace membrane, agency will replace immiediatly. (D) Materials likes Sodium Hypochlorite and any other chemical and materials required for smooth operation of STP will be provided by the agency. | 1.00 | Each |  | 50000.00 | 50000.00 | 50000.00 | 50000.00 | 122033.00 | 122033.00 | 180000.00 | 180000.00 | 50000.00 | Max Tech Infra Projects Pvt Ltd, AQUAWHIZZ
20.00 | AICMC for 3rd Year after Defects Liability Period (A) Bi-Monthly visit of technical person to check the STP plant and unlimited breakdown calls. (B) Repairing of Pumps, motors, Panel, Filter, UV, piping, cabling and filters work etc. whenever required for smooth operation of STP. (C) In the MBR STP as and when required to replace membrane, agency will replace immiediatly. (D) Materials likes Sodium Hypochlorite and any other chemical and materials required for smooth operation of STP will be provided by the agency. | 1.00 | Each |  | 50000.00 | 50000.00 | 50000.00 | 50000.00 | 132203.00 | 132203.00 | 180000.00 | 180000.00 | 50000.00 | Max Tech Infra Projects Pvt Ltd, AQUAWHIZZ
21.00 | AICMC for 4th Year after Defects Liability Period (A) Bi-Monthly visit of technical person to check the STP plant and unlimited breakdown calls. (B) Repairing of Pumps, motors, Panel, Filter, UV, piping, cabling and filters work etc. whenever required for smooth operation of STP. (C) In the MBR STP as and when required to replace membrane, agency will replace immiediatly. (D) Materials likes Sodium Hypochlorite and any other chemical and materials required for smooth operation of STP will be provided by the agency. | 1.00 | Each |  | 50000.00 | 50000.00 | 50000.00 | 50000.00 | 142372.00 | 142372.00 | 180000.00 | 180000.00 | 50000.00 | Max Tech Infra Projects Pvt Ltd, AQUAWHIZZ
22.00 | AICMC for 5th Year after Defects Liability Period (A) Bi-Monthly visit of technical person to check the STP plant and unlimited breakdown calls. (B) Repairing of Pumps, motors, Panel, Filter, UV, piping, cabling and filters work etc. whenever required for smooth operation of STP. (C) In the MBR STP as and when required to replace membrane, agency will replace immiediatly. (D) Materials likes Sodium Hypochlorite and any other chemical and materials required for smooth operation of STP will be provided by the agency. | 1.00 | Each |  | 50000.00 | 50000.00 | 65000.00 | 65000.00 | 152542.00 | 152542.00 | 180000.00 | 180000.00 | 50000.00 | AQUAWHIZZ
23.00 | Earth work in excavation by mechanical means (Hydraulic excavator) /manual means in foundation trenches or drains (not exceeding 1.5 m in width or 10 sqm on plan), including dressing of sides and ramming of bottoms, lift upto 1.5 m, including getting out the excavated soil and disposal of surplus excavated soil as directed, within a lead of 50 m. All kinds of soil. | 180.00 | CUM |  | 520.00 | 93600.00 | 95.00 | 17100.00 | 152.00 | 27360.00 | 282.15 | 50787.00 | 17100.00 | Max Tech Infra Projects Pvt Ltd
24.00 | Filling available excavated earth (excluding rock) in trenches, plinth, sides of foundations etc. in layers not exceeding 20cm in depth, consolidating each deposited layer by ramming and watering, lead up to 50 m and lift upto 1.5 m. | 90.00 | CUM |  | 250.00 | 22500.00 | 125.00 | 11250.00 | 135.00 | 12150.00 | 163.35 | 14701.50 | 11250.00 | Max Tech Infra Projects Pvt Ltd
25.00 | Centering and shuttering including strutting, propping etc. and removal of form for Foundations, footings, bases of columns, etc. for mass concrete. | 12.00 | SQM |  | 450.00 | 5400.00 | 500.00 | 6000.00 | 254.00 | 3048.00 | 1262.25 | 15147.00 | 3048.00 | greenagersenviro solutions and services pvt. ltd.
26.00 | Centering and shuttering including strutting, propping etc. and removal of form for Walls (any thickness) including attached pilasters, butteresses, plinth and string courses etc. | 207.00 | SQM |  | 450.00 | 93150.00 | 400.00 | 82800.00 | 322.00 | 66654.00 | 1262.25 | 261285.75 | 66654.00 | greenagersenviro solutions and services pvt. ltd.
27.00 | Centering and shuttering including strutting, propping etc. and removal of form for Suspended floors, roofs, landings, balconies and access platform. | 18.00 | SQM |  | 500.00 | 9000.00 | 400.00 | 7200.00 | 296.00 | 5328.00 | 1262.25 | 22720.50 | 5328.00 | greenagersenviro solutions and services pvt. ltd.
28.00 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering - All work up to plinth level: 1:3:6 (1 Cement: 3 coarse sand (zone-III) derived from natural sources: 6 graded stone aggregate 40 mm nominal size derived from natural sources) | 4.00 | CUM |  | 5600.00 | 22400.00 | 5500.00 | 22000.00 | 5254.00 | 21016.00 | 6682.50 | 26730.00 | 21016.00 | greenagersenviro solutions and services pvt. ltd.
29.00 | Providing and laying in position ready mixed or site batched design mix cement concrete for reinforced cement concrete work; using coarse aggregate and fine aggregate derived from natural sources, Portland Pozzolana / Ordinary Portland /Portland Slag cement, admixtures in recommended proportions as per IS: 9103 to accelerate / retard setting of concrete, to improve durability and workability without impairing strength; including pumping of concrete to site of laying, curing, carriage for all leads; but excluding the cost of centering, shuttering, finishing and reinforcement as per direction of the engineer-in-charge; for the following grades of concrete. Concrete of M30 grade with minimum cement content of 350 kg/cum. | 32.00 | CUM |  | 8000.00 | 256000.00 | 5500.00 | 176000.00 | 6610.00 | 211520.00 | 11731.50 | 375408.00 | 176000.00 | Max Tech Infra Projects Pvt Ltd
30.00 | Steel reinforcement for R.C.C. work including straightening, cutting, bending, placing in position and binding all complete upto plinth level. Thermo-Mechanically Treated bars of grade Fe-500D or more. | 4000.00 | Kg |  | 70.00 | 280000.00 | 65.00 | 260000.00 | 72.00 | 288000.00 | 126.25 | 505000.00 | 260000.00 | Max Tech Infra Projects Pvt Ltd
31.00 | Structural steel work in single section, fixed with or without connecting plate, including cutting, hoisting, fixing in position and applying a priming coat of approved steel primer all complete. | 155.00 | Kg |  | 120.00 | 18600.00 | 165.00 | 25575.00 | 76.00 | 11780.00 | 155.92 | 24167.60 | 11780.00 | greenagersenviro solutions and services pvt. ltd.
| Total in Figures |  |  |  |  | 4550050.00 |  | 3991985.00 |  | 4792758.00 |  | 6577726.81
Lowest Amount Quoted BY: Max Tech Infra Projects Pvt Ltd(3991985.00)

## BOQ Summary
BOQ Summary Details Tender Title: Provision of STP for ATC Tower, New MSSR and New Fire Station at R. B. Airport, Bhopal. Tender ID: 2025_AAI_238591_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Max Tech Infra Projects Pvt Ltd (BID ID -869292) | 3991985.00 | L1
| 2 | AQUAWHIZZ (BID ID -869988) | 4550050.00 | L2
| 3 | greenagersenviro solutions and services pvt. ltd. (BID ID -870445) | 4792758.00 | L3
| 4 | Unistar environment and research labs pvt. ltd. (BID ID -871374) | 6577726.81 | L4