## BoQ1
Government eProcurement System Created By: Amritanshu Pal Created Date/Time: 27-Aug-2025 04:04 PM Tender Title: Electrical work for metro railway work at NSCBI Airport, Kolkata, SH Perimeter Lighting. Tender ID: 2025_AAI_240134_1
Tender Inviting Authority: Sr. Manager (E-E), AAI, NSCBI Airport, Kolkata.
Name of Work: Electrical work for metro railway work at NSCBI Airport, Kolkata (SH: Perimeter lighting).
Contract No: 2025_AAI_240134_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Youngmen Traders (GSTN-19AEIPB6323B1ZZ) BID ID -870976 |  | M/s J.K. Electric Engineering Works (GSTN-19AAHFJ4404E1ZL) BID ID -875825 |  | MANNA ELECTRONICS AND ELECTRICAL WORKS (GSTN-19AALFM9363P2Z6) BID ID -876009 |  | PMW Infratech Pvt Ltd (GSTN-NA) BID ID -870567
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | SITC of Vermin proof, powder coated, free floor-standing type, fully compartmentalized, double door, IP55 outdoor type electrical LT Panel fabricated of 2 mm. thick CRCA sheet, treated through seven tank process suitable for 415V +/-10% 3-ph 4-wire 50Hz AC supply with detachable CRCA gland plate, busbar alley, cable alley, required internal electrical connections, auto-manual operation, ventilation louver covered with wiremesh, lifting hooks, required foundation, rain shed etc. complete as required having components a) Incomer 01 no.: 200 A 4P MCCB with over load, short circuit protection, ON-OFF-TRIP LED indication with MCB protection. b) Outgoing 08 nos. : 63 A 4P MCCB c) Busbar: 200A TPN PVC sleaved and insulator supported. d) Contactor and on delay timer for auto operation with auto manual switch. | 1.00 | Each |  | 300000.00 | 300000.00 | 185000.00 | 185000.00 | 215000.00 | 215000.00 | 271170.00 | 271170.00 | 185000.00 | M/s J.K. Electric Engineering Works
2.00 | Supply of IP66, 5700K, efficacy >110 Lumen/W, CRI>70 Integral type minimum 70W LED Street Light Luminaire with 50,000 burning hours, driver efficay not less than 85%, high pressure die cast aluminum housing, 4kV surge protection, p.f.>0.95, suitable for 140-270V 50Hz AC supply as per the technical specification. | 90.00 | Each |  | 1800.00 | 162000.00 | 2000.00 | 180000.00 | 1700.00 | 153000.00 | 1880.00 | 169200.00 | 153000.00 | MANNA ELECTRONICS AND ELECTRICAL WORKS
3.00 | Supply of IP66, 5700K, efficacy >110 Lumen/W, CRI>70 Integral type minimum 30W LED flood light with 50,000 burning hours, driver efficay not less than 85%, high pressure die cast aluminum housing, 4kV surge protection, p.f.>0.95, suitable for 140-270V 50Hz AC as per the technical specification. | 196.00 | Each |  | 1000.00 | 196000.00 | 1250.00 | 245000.00 | 1150.00 | 225400.00 | 920.00 | 180320.00 | 180320.00 | PMW Infratech Pvt Ltd
4.00 | Installation testing commissioning of LED luminaire on the existing pole/ bracket including angle setting as per design, all required accessories, reducer/modification in existing pole/bracket, clamp, nuts, bolts etc. as required, connection from thermoplastic enclosure with 1.1kV grade 3Cx1.5 sqmm. PVC insulated FR Copper conductor flexible cable through pole/bracket in GI flexible conduit (required if cable is exposed outside) including proper terminatin with lugs/ferrules etc. complete as required as directed by Engineer-In-Charge. Note: Perimeter lighting design by OEM of LED luminaire to be submitted to AAI for approval. | 286.00 | Each |  | 225.00 | 64350.00 | 135.00 | 38610.00 | 350.00 | 100100.00 | 580.00 | 165880.00 | 38610.00 | M/s J.K. Electric Engineering Works
5.00 | Supply erection of high strength marine grade, double coat aluminum spray painted Aluminum street lighting pole with fixture mount height 3.5 mtr, round shaped 70-60 mm diameter 3 mm thick (minimum), suitable for wind speed as per IS 875 and having integral swan -neck type arm of required length, angle with reducer (if required) for fixing LED fitting to achieve desired lux level including pole cap, pre drilled holes for cable entry-exit, epoxy coated steel base plate, grouted SS foundation bolt in RCC foundation, pole fixing hardware, provision of pipes for cable loop-in loop-out, excavation, refilling, cement plaster with good finish painting, numbering, earthing etc. complete as required. NOTE: Sample pole foundation design to be vetted from Govt. Engg. College and to be submitted. | 90.00 | Each |  | 11600.00 | 1044000.00 | 10700.00 | 963000.00 | 12300.00 | 1107000.00 | 22940.00 | 2064600.00 | 963000.00 | M/s J.K. Electric Engineering Works
6.00 | Supply, fixing of 40mm dia class 'B' GI pipe bracket of length not less than 2.0 mtr by bending the pipe at the desired angle to achieve required lux level on perimeter wall suitable for fixing LED street light luminaire including MS clamp, anchor fastners, painiting, numbering etc. as per site requirement. | 8.00 | Each |  | 1000.00 | 8000.00 | 1000.00 | 8000.00 | 950.00 | 7600.00 | 2940.00 | 23520.00 | 7600.00 | MANNA ELECTRONICS AND ELECTRICAL WORKS
7.00 | Supply & fixing of IP65 Thermoplastic enclosure lid made of hinged transparent Polycarbonate and base made of Polystyrene, light weight, corrosion proof, fire retardant, polyurethane gasket, fitted with internally fixed 01 no. 6A C-type SP MCB 10kA Isc, one no. 4 way terminal, earth terminal, clamp and GI Strip at the back of the enclosure to be fixed with pole including screws, nuts, bolts, washers etc. complete as required as per site condition and instruction of Engineer-In-Charge.. | 98.00 | Each |  | 3900.00 | 382200.00 | 3000.00 | 294000.00 | 4200.00 | 411600.00 | 2350.00 | 230300.00 | 230300.00 | PMW Infratech Pvt Ltd
8.00 | Excavation of earth/soft soil mechanically/manually not exceeding 1.5 mtr in width, and lift upto 1.5mtr, including back filling as required and as directed by the Engineer-In-Charge | 399.00 | Cum |  | 225.00 | 89775.00 | 200.00 | 79800.00 | 200.00 | 79800.00 | 170.00 | 67830.00 | 67830.00 | PMW Infratech Pvt Ltd
9.00 | Excavation of the trench in hard rock or bituminous / cement concrete of runways/taxiways/ apron/RESA/ Road etc. by power saw cutting without disturbing the other area, upto 1.5 mtr in width, and depth upto 1.0 mtr, including getting out the excavated debris, cleaning the cut area and disposal of excavated debris as directed within a lead of 5 KM including all machineries like power saw, hammer drill / pneumatic drill, water browser, mobile DG set, transportation etc. complete as required. | 8.00 | Cum |  | 1200.00 | 9600.00 | 1300.00 | 10400.00 | 2500.00 | 20000.00 | 6470.00 | 51760.00 | 9600.00 | Youngmen Traders
10.00 | Providing and laying in position cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size) including form work etc. as required as per the site condition. | 8.00 | Cum |  | 8500.00 | 68000.00 | 5700.00 | 45600.00 | 4500.00 | 36000.00 | 4110.00 | 32880.00 | 32880.00 | PMW Infratech Pvt Ltd
11.00 | Supplying and laying of 1 run X 63 mm dia (OD), UV stabilized, HDPE pipe (PE-63, PN-6) as per IS - 4984 and IS marked with uptodate amendment along with accessories like socket, bend, couplers etc. complete with fitting, cuttings, jointing in the existing trench/soil/gravel area/along with PQC work complete as required. | 1425.00 | Mtr |  | 145.00 | 206625.00 | 175.00 | 249375.00 | 115.00 | 163875.00 | 200.00 | 285000.00 | 163875.00 | MANNA ELECTRONICS AND ELECTRICAL WORKS
12.00 | Supplying and laying of 1 run X 63 mm dia (OD), UV stabilized, HDPE pipe (PE- 63, PN-6) as per IS - 4984 and IS marked with upto date amendment along with accessories like socket, bend, couplers etc. complete with fitting, cuttings, jointing etc. below the ground (i/c Road crossing ,Cement concrete Apron Area, Runway, taxiway) at a depth upto 6 m through horizontal directional drilling etc. after doing Ground Penetrating radar survey and submitting its report etc.complete as required. | 75.00 | Mtr |  | 315.00 | 23625.00 | 400.00 | 30000.00 | 485.00 | 36375.00 | 730.00 | 54750.00 | 23625.00 | Youngmen Traders
13.00 | Supplying and laying of 1 run X 90 mm dia (OD), UV stabilized, HDPE pipe (PE- 63, PN-6) as per IS - 4984 and IS marked with uptodate amendment along with accessories like socket, bend, couplers etc. complete with fitting, cuttings, jointing etc. below the ground (i/c Road crossing ,Cement concrete Apron Area, Runway, taxiway) at a depth upto 6 m through horizontal directional drilling etc. after doing Ground Penetrating radar survey and submitting its report etc.complete as required. | 2375.00 | Mtr |  | 450.00 | 1068750.00 | 500.00 | 1187500.00 | 610.00 | 1448750.00 | 520.00 | 1235000.00 | 1068750.00 | Youngmen Traders
14.00 | Supplying and laying of 1 run X 90 mmdia (OD), UV stabilized, HDPE pipe (PE-63, PN-6) as per IS - 4984 and IS marked with uptodate amendment along with accessories like socket, bend, couplers etc. complete with fitting, cuttings, jointing in the existing trench/soil/gravel area/along with PQC work complete as required. | 125.00 | Mtr |  | 255.00 | 31875.00 | 300.00 | 37500.00 | 200.00 | 25000.00 | 340.00 | 42500.00 | 25000.00 | MANNA ELECTRONICS AND ELECTRICAL WORKS
15.00 | Supply, laying of 3.5C x 120 sqmm. PVC seathed XLPE insulated 1.1kV grade armoured aluminum conductor power cable conforming to IS 7098 part-I ammended up to date in existing covered cable trench/pipe/open duct/cable tray/wall with suitable clamps etc. complete as required as per site condition and direction of Engineer-In-Charge. | 2500.00 | Mtr |  | 575.00 | 1437500.00 | 645.00 | 1612500.00 | 555.00 | 1387500.00 | 660.00 | 1650000.00 | 1387500.00 | MANNA ELECTRONICS AND ELECTRICAL WORKS
16.00 | Supply and making end termination with brass compression gland and aluminum lugs for 3.5C x 120Sqmm. (45mm) PVC insulated, PVC seathed/XLPE aluminum cable of 1.1kV grade as required. | 6.00 | Each |  | 590.00 | 3540.00 | 300.00 | 1800.00 | 421.00 | 2526.00 | 2350.00 | 14100.00 | 1800.00 | M/s J.K. Electric Engineering Works
17.00 | Supplying and making straight through joint with heat shrinkable kit including ferrules and other jointing materials for 3½ X 120 sq. mm PVC insulated and PVC sheathed / XLPE armoured, aluminium conductor cable of 1.1 KV grade as required. | 4.00 | Each |  | 2500.00 | 10000.00 | 1700.00 | 6800.00 | 1689.00 | 6756.00 | 5260.00 | 21040.00 | 6756.00 | MANNA ELECTRONICS AND ELECTRICAL WORKS
18.00 | Supply and laying of 4C x 25sqmm. 1.1kV grade XLPE insulated PVC seathed armoured aluminum conductor cable conforming to IS 7098 part-I with up to date ammendment in the existing trench/HDPE pipe/GI Pipe/pole/wall with suitable clamp etc. as required. | 1800.00 | Mtr |  | 215.00 | 387000.00 | 220.00 | 396000.00 | 205.00 | 369000.00 | 220.00 | 396000.00 | 369000.00 | MANNA ELECTRONICS AND ELECTRICAL WORKS
19.00 | Supply and making end termination with brass compression gland and aluminum lugs for 4Cx25Sqmm. PVC insulated, PVC seathed/XLPE aluminum cable of 1.1kV grade as required. | 196.00 | Each |  | 250.00 | 49000.00 | 125.00 | 24500.00 | 185.00 | 36260.00 | 520.00 | 101920.00 | 24500.00 | M/s J.K. Electric Engineering Works
20.00 | Supplying and making straight through joint with heat shrinkable kit including ferrules and other jointing materials for 4 X 25 sq. mm of PVC insulated and PVC sheathed / XLPE armourred aluminium conductor cable of 1.1 KV grade as required. | 2.00 | Each |  | 1500.00 | 3000.00 | 1200.00 | 2400.00 | 1200.00 | 2400.00 | 2880.00 | 5760.00 | 2400.00 | M/s J.K. Electric Engineering Works, MANNA ELECTRONICS AND ELECTRICAL WORKS
21.00 | Providing laying and fixing 6 SWG dia G.I. wire on surface or in recess (in existing pipe and/or along with submain wiring/cable) for loop earthing etc.complete as required. | 1800.00 | Mtr |  | 20.00 | 36000.00 | 21.00 | 37800.00 | 15.00 | 27000.00 | 30.00 | 54000.00 | 27000.00 | MANNA ELECTRONICS AND ELECTRICAL WORKS
22.00 | Dismantling of existing perimeter light fitting with its pole/wall bracket (as applicable), pipe, clamp, its loop-in loop-out box etc. by diconnecting it from electrical circuuitry in safe manner, sealing the electrical cables, pipe ends if any, demolishing of old brick and/or concrete pedestal/muffing if any, making the surface smooth, keeping the fitting, pipe/bracket, clamp, pole in store under safe custody and handing over the same to AAI at the completion of the project/ as decided by the Engineer-In-Charge etc. complete as required. Power cable has to be disconnected from source end also. | 63.00 | Each |  | 300.00 | 18900.00 | 75.00 | 4725.00 | 110.00 | 6930.00 | 580.00 | 36540.00 | 4725.00 | M/s J.K. Electric Engineering Works
23.00 | Earthing with G.I. earth pipe 4.5 meter long, 40 mm dia including accessories, and providing enclosure of size 750mm x 350 mm x 550 mm ( H) made out 6 mm thick MS sheet and top cover 10 mm thick MS sheet ( counter shunk fitting, M-10 nuts and bolts.) having locking arrangement and watering pipe etc. with charcoal/ coke and salt as required. | 6.00 | Each |  | 6000.00 | 36000.00 | 7500.00 | 45000.00 | 5500.00 | 33000.00 | 12940.00 | 77640.00 | 33000.00 | MANNA ELECTRONICS AND ELECTRICAL WORKS
24.00 | Providing and fixing 3mm thick 750mm long 50mm X 50mm GI angle frame by use of suitable clamp on existing street light pole at required height to iluminate perimeter wall as per BCAS, DGCA guideline inlcuding all accessories like nuts, bolts, washers etc., making holes for fixing luminaires, spray painting of approved color complete as required. | 90.00 | Each |  | 900.00 | 81000.00 | 500.00 | 45000.00 | 975.00 | 87750.00 | 1110.00 | 99900.00 | 45000.00 | M/s J.K. Electric Engineering Works
25.00 | The execution of Delhi Schedule of Rates (E&M) 2022 of estimated amount of Rs 2,00,000/- for the items mentioned in Chapter 1 to Chapter 17 including Appendix-I & II as and when required basis in connection with the work and as decided by Engineer-In-Charge. [For quoted Rate 0.9, the Estimated amount of Rs 2,00,000/- means amount will be Rs.1,80,000/. Similarly for quoted Rate 1.1, the Estimated amount of Rs 2,00,000/- means amount will be Rs. 2,20,000/-] (Note: Payment of DSR rate will be made after deduction of GST considered in the Rate of DSR-2022 and then multiplied by the quoted rate. ) | 200000.00 | MF |  | .95 | 190000.00 | .70 | 140000.00 | .75 | 150000.00 | 1.10 | 220000.00 | 140000.00 | M/s J.K. Electric Engineering Works
| Total in Figures |  |  |  |  | 5906740.00 |  | 5870310.00 |  | 6138622.00 |  | 7551610.00
Lowest Amount Quoted BY: M/s J.K. Electric Engineering Works(5870310.00)

## BOQ Summary
BOQ Summary Details Tender Title: Electrical work for metro railway work at NSCBI Airport, Kolkata, SH Perimeter Lighting. Tender ID: 2025_AAI_240134_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | M/s J.K. Electric Engineering Works (BID ID -875825) | 5870310.00 | L1
| 2 | Youngmen Traders (BID ID -870976) | 5906740.00 | L2
| 3 | MANNA ELECTRONICS AND ELECTRICAL WORKS (BID ID -876009) | 6138622.00 | L3
| 4 | PMW Infratech Pvt Ltd (BID ID -870567) | 7551610.00 | L4