## BoQ1
Government eProcurement System Created By: Partha Saha Created Date/Time: 11-Sep-2025 03:48 PM Tender Title: SITC of GLF system works at Darbhanga Airport Tender ID: 2025_AAI_240167_1
Tender Inviting Authority: Airports Authority of India
Name of Work: SITC of GLF system works at Darbhanga Airport
Contract No:
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | REWINDER TECHNO ELECTRICALS (GSTN-18AAFFR7457K1ZL) BID ID -882296 |  | Balaji Engineering (GSTN-33ADGPV2628A1ZV) BID ID -882641 |  | YPR ENGINEERING AND SOLUTIONS PRIVATE LIMITED (GSTN-NA) BID ID -882498 |  | Vardhman Airport Solutions Limited (GSTN-NA) BID ID -877372
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | SH-I A : Supply of GLF system & associated electrical works
1.01 | Supply of FAA/ICAO/DGCA-CAR Compliant Inset type LED Uni directional Stop Bar (RED) light fitting suitable for straight section/straight section (off set) / curved section for aviation visual aids requirements complete with shallow base and matching body of the fitting, inner body and outer cover made of die cast aluminium complete with LED lamp with integral driver and electronics suitable for 6.6 amps current with connected heat resistant accessories, prism assembly, optical assembly, "O" ring seal, pressure relief test plug, hardware, red prism / lenses and all standard accessories and ready for site installation complete as required as per sepcifications. | 20.00 | Each | 65632.32 | 40000.00 | 800000.00 | 65000.00 | 1300000.00 | 42000.00 | 840000.00 | 50000.00 | 1000000.00 | 800000.00 | REWINDER TECHNO ELECTRICALS
1.02 | Supply of FAA/ICAO/DGCA-CAR Compliant high intensity Elevated LED Runway guard light with two flashing light fixtures with black independent visors, 6.6A Current driven input power supply, LED lamps/module , flashing rates 45-50 Per Minute, frangible support, high strength base plate for runway guard light to resist wind speed (300 mph) gaskets, SS hardware etc as per sepcifications complete as required as per sepcifications. | 5.00 | Set | 250651.44 | 175000.00 | 875000.00 | 300000.00 | 1500000.00 | 150000.00 | 750000.00 | 165000.00 | 825000.00 | 750000.00 | YPR ENGINEERING AND SOLUTIONS PRIVATE LIMITED
1.03 | Supply of FAA/ICAO/DGCA-CAR Compliant elevated type Omni-directional Blue colour, medium intensity LED type Taxiway Edge Light fitting suitable for Taxiway, Apron Edge Lights, Turning Pad Lights suitable for operation at 6.6 Amps, series circuit supply, complete with Omni-directional, Lens clamping mechanism, breakable coupling, gasket, two pin secondary leads, base plate with SS Hardware and other accessories including integrated encapsulated electronic module complete as required as per sepcifications. | 144.00 | Each | 6026.80 | 4000.00 | 576000.00 | 10500.00 | 1512000.00 | 4200.00 | 604800.00 | 4200.00 | 604800.00 | 576000.00 | REWINDER TECHNO ELECTRICALS
1.04 | Supply of FAA/ICAO/DGCA-CAR Compliant LED type inset omnidirectional Blue colour light fitting for aviation visual aid at taxiway edge, apron edge, turning pad lights complete with LED and integral driver and electronics suitable for 6.6 Amps, lenses / prism, filters , lense protection ring , shallow base, matching body, single plug, inner & outer cover, two pin secondary leads complete with other accessories, ready for site installation on existing housing boxes etc. in conformity with ICAO/DGCA-CAR, complete as required as per specifications. complete as required as per sepcifications. | 9.00 | Each | 64928.24 | 40000.00 | 360000.00 | 62300.00 | 560700.00 | 42000.00 | 378000.00 | 42000.00 | 378000.00 | 360000.00 | REWINDER TECHNO ELECTRICALS
1.05 | Supply of 2C x 2.5 sqmm secondary lead made out of multi stranded copper conductor EPR insulated & PCP sheathed, anti-termite & anti rodent treated 600 V grade AGL cable as specified in particular complete as required as per specifications. | 1000.00 | Mtr | 199.68 | 200.00 | 200000.00 | 300.00 | 300000.00 | 140.00 | 140000.00 | 175.00 | 175000.00 | 140000.00 | YPR ENGINEERING AND SOLUTIONS PRIVATE LIMITED
1.06 | Supply of 1C x 6 sq.mm, 5 KV grade, AFL cable, stranded copper conductor, XLPE insulated PE sheathed, anti-termite & anti rodent treated Airfield Ground Lighting series cable generally confirming to IS 7098 as ammended up to date in conformity with ICAO/DGCA-CAR, complete as required as per specifications. | 14800.00 | Mtr | 149.76 | 160.00 | 2368000.00 | 190.00 | 2812000.00 | 105.00 | 1554000.00 | 155.00 | 2294000.00 | 1554000.00 | YPR ENGINEERING AND SOLUTIONS PRIVATE LIMITED
1.07 | Supply of 6 sqmm, 5 KV grade plug and receptacle of type I, class 'B' connector suitable for field attachment with 5 KV grade XLPE insulated, PE sheathed, copper conductor cable in conformity with ICAO/DGCA-CAR, complete as required as per specifications. | 191.00 | Set | 792.48 | 600.00 | 114600.00 | 820.00 | 156620.00 | 700.00 | 133700.00 | 800.00 | 152800.00 | 114600.00 | REWINDER TECHNO ELECTRICALS
1.08 | Supply 2 pin plug and recepetacles suitable for 2 x 2.5 Sq mm copper conductor secondary lead in conformity with ICAO/DGCA-CAR, complete as required as per specifications. | 191.00 | Set | 819.52 | 700.00 | 133700.00 | 840.00 | 160440.00 | 700.00 | 133700.00 | 1200.00 | 229200.00 | 133700.00 | REWINDER TECHNO ELECTRICALS, YPR ENGINEERING AND SOLUTIONS PRIVATE LIMITED
1.09 | Supply of Indoor type air cooled constant current regulator of micro processor controlled, thyristor type suitable for remote as well as local control operations on input voltage 230/415 volts, 50Hz AC supply with 6.6A output having 5 steps brightness control with variation of current output and able to communicate with PC or PLC controlled system, with suitable rating Microprocessor based release (Ics = Icu = 25kA) incomer 3 Pole 63 Amp. MCCB, digital output ammeter (0-10A), overcurrent, overvoltage, open circuit and earth fault protection and digital earth leakage meter, two stage earth leakage detector, positive back indication equipments, LED/LCD display, suitable for connection and communication with ALCMS for operation of LED type AGL Circuits etc complete as required confirming to technical specifications for the following rating. a) 4 KVA | 9.00 | Each | 330176.08 | 175000.00 | 1575000.00 | 300000.00 | 2700000.00 | 210000.00 | 1890000.00 | 300000.00 | 2700000.00 | 1575000.00 | REWINDER TECHNO ELECTRICALS
1.10 | Design, Supply, Assembling, installation, testing and commissioning of Airfield Lighting Control and Monitoring System (ALCMS) with hardware and software i/c incorporating the control & operation of microprocessor type CCRs . The system involves single Touch-Screen LCD/ LED type along with computer with all associated accessories at the ATC for remote control and operation of associated Airfield lighting system & Single PC with all associated accesories for monitoring at Powerhouse. This item include complete hardware and software, interconnecting cables (OFC Control), switches, terminations, splicing etc. as required and capable of 5 step indication of CCRs, indication of fixed circuits, mimic display of systems in operation confirming to the specifications enclosed and complying the latest DGCA-CAR / ICAO requirement. The system shall be suitable for controlling 10 Nos. CCR’s (CCR Circuits), 2 Nos. Motorized Sliding Gate & 04 Nos. Boom Barriers (Fixed Circuits) and as per attached Technical Specifications.There shall be single network adapter in the ATC and single network adapter in the power house & both connected via OFC Cable. This item also includes to provide all hardware, software, licences, OFC / CAT-VI / control / Power cabling interconnection, End terminations, vault processor, associated furniture/rack for installation of accesories as per requirement of site etc. as required (excluding supply & laying of OFC/Power Cable/Control Cable required to connect ALCMS from CCR hall to ATC & field devices ), 1 no. colour laser printer suitable for A3 print including providing training, documentation as per specifications up to satisfaction of Engg. In Charge etc. complete as required. | 1.00 | Job | 2073664.32 | 1000000.00 | 1000000.00 | 2500000.00 | 2500000.00 | 1400000.00 | 1400000.00 | 3750000.00 | 3750000.00 | 1000000.00 | REWINDER TECHNO ELECTRICALS
1.11 | Supply of 15 Watt, 6.6/6.6 Amp rating completely enclosed rubber covered isolating transformer for use of 6.6 amps series airport lighting circuits having nominal voltage rating of 5KV rated for operation on 50 Hz. The transformer shall be water tight and shall be designed for direct burial in the earth or installation in a Housing Box in conformity with ICAO/DGCA-CAR, complete as required as per specifications. | 173.00 | Each | 4112.16 | 3000.00 | 519000.00 | 4000.00 | 692000.00 | 2800.00 | 484400.00 | 3250.00 | 562250.00 | 484400.00 | YPR ENGINEERING AND SOLUTIONS PRIVATE LIMITED
1.12 | Supply of 45 Watt, 6.6/6.6 Amp rating completely enclosed rubber covered isolating transformer for use of 6.6 amps series airport lighting circuits having nominal voltage rating of 5KV rated for operation on 50 Hz. The transformer shall be water tight and shall be designed for direct burial in the earth or installation in a Housing Box in conformity with ICAO/DGCA-CAR, complete as required as per specifications. | 18.00 | Each | 4879.68 | 3500.00 | 63000.00 | 4500.00 | 81000.00 | 3200.00 | 57600.00 | 4000.00 | 72000.00 | 57600.00 | YPR ENGINEERING AND SOLUTIONS PRIVATE LIMITED
1.13 | Supply of 16 Sq.mm PVC insulated copper conductor single core un-armoured flexible cable of 1.1 KV grade confirming to IS 694 for earth connection | 100.00 | Mtr | 215.28 | 250.00 | 25000.00 | 300.00 | 30000.00 | 230.00 | 23000.00 | 320.00 | 32000.00 | 23000.00 | YPR ENGINEERING AND SOLUTIONS PRIVATE LIMITED
1.14 | Supply of LED Guidance signage board of various sizes made out of 2 mm thick anodized aluminium frame with suitable angle support, 1.5 mm thick aluminium back symbols of sign should be screen printed on inside of sign face made of self-adhesive 3M film applied on the inside face with required coloring as approved by E-I-C. Sign board shall be uniformly internally illuminated with required LED's i/c all other accessories to achieve uniform illumination level and with suitable driver and electronics to operate on 2.8 Amp to 6.6 Amp AC, made for water tightness and locking arrangements, mounting legs with frangible coupling & base frame etc. meeting the latest ICAO/DGCA-CAR standards complete as per specifications etc. as required. Note- The rate shall be quoted considering Wastages. | 20.00 | Sq Mtr | 52147.68 | 30000.00 | 600000.00 | 55000.00 | 1100000.00 | 45000.00 | 900000.00 | 54000.00 | 1080000.00 | 600000.00 | REWINDER TECHNO ELECTRICALS
1.15 | Supply of 50 mm dia OD ISI marked HDPE pipe as per IS:4984:2016, of rating PE 100, PN 8 complete as required | 5700.00 | Mtr. | 90.48 | 100.00 | 570000.00 | 150.00 | 855000.00 | 90.00 | 513000.00 | 120.00 | 684000.00 | 513000.00 | YPR ENGINEERING AND SOLUTIONS PRIVATE LIMITED
1.16 | Supply of 32 mm dia OD ISI marked HDPE pipe as per IS:4984:2016, of rating PE 100, PN 8 complete as required | 6300.00 | Mtr. | 45.76 | 70.00 | 441000.00 | 125.00 | 787500.00 | 60.00 | 378000.00 | 80.00 | 504000.00 | 378000.00 | YPR ENGINEERING AND SOLUTIONS PRIVATE LIMITED
1.17 | Supply of 3C x 16 Sq. mm.size 1.1 KV grade XLPE insulated, PVC sheathed, armoured Copper conductor power cable conforming to IS 7098 as amended upto date. | 200.00 | Mtr | 1185.60 | 600.00 | 120000.00 | 850.00 | 170000.00 | 650.00 | 130000.00 | 900.00 | 180000.00 | 120000.00 | REWINDER TECHNO ELECTRICALS
1.18 | Supply of 4C x 16 Sq. mm.size 1.1 KV grade XLPE insulated, PVC sheathed, armoured Copper conductor power cable conforming to IS 7098 as amended upto date. | 100.00 | Mtr | 1494.48 | 900.00 | 90000.00 | 1050.00 | 105000.00 | 950.00 | 95000.00 | 1200.00 | 120000.00 | 90000.00 | REWINDER TECHNO ELECTRICALS
1.19 | Supply of yellow/ green 2.5 Sq.mm PVC insulated FRLS copper conductor single core flexible cable of 1.1 KV grade as per IS 694 for earth connection | 400.00 | Mtr. | 34.32 | 40.00 | 16000.00 | 50.00 | 20000.00 | 45.00 | 18000.00 | 60.00 | 24000.00 | 16000.00 | REWINDER TECHNO ELECTRICALS
1.20 | Supplying of 1100V grade Aluminium Conductor XLPE insulated galvanised steel strip armoured & overall PVC sheathed armoured power cables as per IS: 7098 Part-I complete as required. a)3.5C X 120 Sq.mm | 150.00 | Mtr. | 1235.52 | 700.00 | 105000.00 | 850.00 | 127500.00 | 900.00 | 135000.00 | 980.00 | 147000.00 | 105000.00 | REWINDER TECHNO ELECTRICALS
1.21 | Supply of 8C x 2.5 Sq. mm.size 1.1 KV grade XLPE insulated, PVC sheathed, armoured Copper conductor Control Cable conforming to IS 7098 as amended upto date. | 4300.00 | Mtr | 604.24 | 247.00 | 1062100.00 | 400.00 | 1720000.00 | 610.00 | 2623000.00 | 520.00 | 2236000.00 | 1062100.00 | REWINDER TECHNO ELECTRICALS
2.00 | SH-IB:Installation, Testing & Commissioning of GLF system & associated electrical works
2.01 | Installation, testing and Commissioning of inset type fitting with deep core cutting upto 500 mm depth, aligning and setting i/c providing sealing material and installation of Isolating Transformer, Crimping / Jointing of secondary lead connectors & other accessories required for commissioning i/c supply of all materials except isolating transformer etc. as per specification complete as required. a) Fitting size up to 8 " / 12 " | 26.00 | Job | 9362.08 | 2000.00 | 52000.00 | 4000.00 | 104000.00 | 5500.00 | 143000.00 | 3750.00 | 97500.00 | 52000.00 | REWINDER TECHNO ELECTRICALS
2.02 | Installation, testing & commissioning of Elevated type taxiway light fixtures/ Runway Guard light on existing transformer housing boxes and Crimping / Jointing of secondary lead connectors, installation of isolating transformers, i/c supply of all materials except isolating transformer etc.as per specificaiton complete as required. | 135.00 | Job | 604.24 | 50.00 | 6750.00 | 200.00 | 27000.00 | 600.00 | 81000.00 | 105.00 | 14175.00 | 6750.00 | REWINDER TECHNO ELECTRICALS
2.03 | Installation, Testing, Commissioning of CCR including termination of incoming and outgoing power and control cables, inter connection, making foundation, earthing connection etc. complete as required | 9.00 | Job | 7550.40 | 1000.00 | 9000.00 | 5000.00 | 45000.00 | 5000.00 | 45000.00 | 4000.00 | 36000.00 | 9000.00 | REWINDER TECHNO ELECTRICALS
2.04 | Installation, Testing and Commissioning of guidance signboards of various sizes (upto 1.5m length) i/c installation of isolating transformer of suitable rating and providing secondary leads etc. i/c pedestal of 1m all around the signage board with 1:2:4 (cement, concrete, coarse) of thickness 100mm with neat cement finish plaster, testing and commissioning etc. as required as per specification. | 20.00 | Sq Mtr | 7550.40 | 3000.00 | 60000.00 | 10000.00 | 200000.00 | 7000.00 | 140000.00 | 8000.00 | 160000.00 | 60000.00 | REWINDER TECHNO ELECTRICALS
2.05 | Laying of 01 No. upto 50 mm dia size HDPE pipe through trenchless technology (HDD) upto a depth of approx. 3 meter as per specification as required. | 6300.00 | Mtr. | 1098.24 | 150.00 | 945000.00 | 600.00 | 3780000.00 | 250.00 | 1575000.00 | 190.00 | 1197000.00 | 945000.00 | REWINDER TECHNO ELECTRICALS
2.06 | Laying of 01 No. 50 mm dia size HDPE pipe with accessories like couplers, bends, tee etc. in the soil for GLF work upto a depth of approx. 750 mm, back filling & making good the same as per site requirement as per the direction of engineer in charge. | 5440.00 | Mtr. | 132.08 | 65.00 | 353600.00 | 150.00 | 816000.00 | 80.00 | 435200.00 | 100.00 | 544000.00 | 353600.00 | REWINDER TECHNO ELECTRICALS
2.07 | Laying of 50mm outer dia. HDPE pipe with accessories like socket, couplers, bends etc. complete with fitting, cuttings, jointing wherever applicable to connect the consecutive transformer housing boxes and transformer housing box to other fitting / location. The laying shall be in Apron/Taxiway shoulder at suitable depth along the civil construction works etc complete as required as directed by EIC. | 220.00 | Mtr. | 120.64 | 10.00 | 2200.00 | 20.00 | 4400.00 | 50.00 | 11000.00 | 175.00 | 38500.00 | 2200.00 | REWINDER TECHNO ELECTRICALS
2.08 | Laying of one number PVC / XLPE / EPR insulated & PVC / PE / PCP sheathed copper conductor power cable of grade exceeding 0.4 KV but not exceeding 11 KV of size not exceeding 25 sq. mm. in the existing cable duct / RCC/HUME/METAL/HDPE/DWC pipes etc. as required. | 14000.00 | Mtr. | 37.44 | 3.00 | 42000.00 | 20.00 | 280000.00 | 20.00 | 280000.00 | 30.00 | 420000.00 | 42000.00 | REWINDER TECHNO ELECTRICALS
2.09 | Laying of one number PVC / XLPE / EPR insulated & PVC / PE / PCP sheathed copper conductor power cable of grade exceeding 0.4 KV but not exceeding 11 KV of size not exceeding 25 sq. mm in the existing masonary open duct/trench/open surface as required | 600.00 | Mtr. | 35.36 | 5.00 | 3000.00 | 20.00 | 12000.00 | 20.00 | 12000.00 | 30.00 | 18000.00 | 3000.00 | REWINDER TECHNO ELECTRICALS
2.10 | Laying of one number 2 X 2.5 sq mm AFL secondary cable along with 1 X 4 sq mm earth cable of voltage grade not exceeding 1.1 KV in the cable duct / masonary trench / RCC / HUME / METAL / GI / HDPE / DWC pipe etc. as required. | 420.00 | Mtr. | 33.28 | 5.00 | 2100.00 | 20.00 | 8400.00 | 20.00 | 8400.00 | 15.00 | 6300.00 | 2100.00 | REWINDER TECHNO ELECTRICALS
2.11 | Cutting kerf of suitable size in taxiway/runway/apron of PQC/bituminous surface i/c chipping, hammering, cleaning & drying etc. & refilling the kerf with sealant material including primer etc. as reqd. in bitumin/PQC area & laying following numbers of secondary leads:- a) 01 No. Secondary lead of size 2C x 2.5 sq.mm. | 70.00 | Mtr. | 483.60 | 200.00 | 14000.00 | 450.00 | 31500.00 | 380.00 | 26600.00 | 500.00 | 35000.00 | 14000.00 | REWINDER TECHNO ELECTRICALS
2.12 | Cutting kerf of suitable size in taxiway/runway/apron of PQC/bituminous surface i/c chipping, hammering, cleaning & drying etc. & refilling the kerf with sealant material including primer etc. as reqd. in bitumin/PQC area & laying following numbers of secondary leads:- a) 2 No. Secondary lead of size 2C x 2.5 sq.mm. | 100.00 | Mtr. | 595.92 | 225.00 | 22500.00 | 500.00 | 50000.00 | 400.00 | 40000.00 | 550.00 | 55000.00 | 22500.00 | REWINDER TECHNO ELECTRICALS
2.13 | Cutting kerf of suitable size in taxiway/runway/apron of PQC/bituminous surface i/c chipping, hammering, cleaning & drying etc. & refilling the kerf with sealant material including primer etc. as reqd. in bitumin/PQC area & laying following numbers of secondary leads:- a)3 No. Secondary lead of size 2C x 2.5 sq.mm. | 30.00 | Mtr. | 668.72 | 245.00 | 7350.00 | 500.00 | 15000.00 | 480.00 | 14400.00 | 580.00 | 17400.00 | 7350.00 | REWINDER TECHNO ELECTRICALS
2.14 | Earthing with 'B' class G. I. earth pipe 4.5 mtrs. long x 40 mm dia i/c accessories and providing masonry enclosures with cover plate having locking arrangement & watering pipe etc. i/c charcoal/ coke and salt complete as required as per specification. | 32.00 | Each | 9945.52 | 3000.00 | 96000.00 | 7000.00 | 224000.00 | 9000.00 | 288000.00 | 8000.00 | 256000.00 | 96000.00 | REWINDER TECHNO ELECTRICALS
2.15 | Earthing with copper earth plate 600mm x 600mm x 3.0mm thick including accessories and providing masonary enclosure with cover plate having locking arrangement and watering pipe etc. Including charcoal and salt complete as required. | 12.00 | Set | 26510.64 | 7000.00 | 84000.00 | 16000.00 | 192000.00 | 25000.00 | 300000.00 | 20000.00 | 240000.00 | 84000.00 | REWINDER TECHNO ELECTRICALS
2.16 | Earthing with GI earth plate 600mm x 600mm x 6.0mm thick including accessories and providing masonary enclosure with cover plate having locking arrangement and watering pipe etc. Including charcoal and salt complete as required. | 2.00 | Set | 8490.56 | 4000.00 | 8000.00 | 7000.00 | 14000.00 | 12000.00 | 24000.00 | 12000.00 | 24000.00 | 8000.00 | REWINDER TECHNO ELECTRICALS
2.17 | Providing and fixing 25mm x 5mm copper strip in 40mm dia G.I. pipe from earth electrode including connection with brass nut, bolt, spring, washer excavation and re-filling etc. as required. | 60.00 | Mtr. | 1652.56 | 800.00 | 48000.00 | 1500.00 | 90000.00 | 1900.00 | 114000.00 | 2400.00 | 144000.00 | 48000.00 | REWINDER TECHNO ELECTRICALS
2.18 | Providing and fixing 25mm x 5 mm G.I. strip in 40mm dia G.I. pipe from earth electrode including connection with G.I. nut, bolt, spring, washer excavation and re-filling etc. as required. | 10.00 | Mtr. | 719.68 | 300.00 | 3000.00 | 800.00 | 8000.00 | 750.00 | 7500.00 | 990.00 | 9900.00 | 3000.00 | REWINDER TECHNO ELECTRICALS
2.19 | Providing and fixing 25mm x 5mm copper strip on surface/in recess/existing pipe for connections etc. as required. | 120.00 | Mtr. | 1151.28 | 600.00 | 72000.00 | 1000.00 | 120000.00 | 1400.00 | 168000.00 | 2200.00 | 264000.00 | 72000.00 | REWINDER TECHNO ELECTRICALS
2.20 | Providing and fixing 25mm x 5mm G.I. strip on surface/in recess/existing pipes etc. for connections etc. as required. | 40.00 | Mtr. | 226.72 | 100.00 | 4000.00 | 200.00 | 8000.00 | 300.00 | 12000.00 | 280.00 | 11200.00 | 4000.00 | REWINDER TECHNO ELECTRICALS
2.21 | Providing and laying earth connection from earth electrode with 6 SWG dia G.I. Wire in 15 mm dia G.I. pipe medium class from earth electrode including connection with G.I. thimble excavation and re-filling as required. | 192.00 | Mtr. | 440.96 | 100.00 | 19200.00 | 300.00 | 57600.00 | 210.00 | 40320.00 | 330.00 | 63360.00 | 19200.00 | REWINDER TECHNO ELECTRICALS
2.22 | Providing and fixing 6 SWG G. I. wire on surface or in recess for loop earthing as required. | 7700.00 | Mtr. | 39.52 | 16.00 | 123200.00 | 38.00 | 292600.00 | 30.00 | 231000.00 | 25.00 | 192500.00 | 123200.00 | REWINDER TECHNO ELECTRICALS
2.23 | Making connection of 5 KV grade, 6 Sq.mm Copper conductor cable with plug & receptacle (but excluding cost of plug & receptacles) i/c connecting continutity wire for screen etc. complete as required. | 173.00 | Job | 257.92 | 10.00 | 1730.00 | 100.00 | 17300.00 | 300.00 | 51900.00 | 120.00 | 20760.00 | 1730.00 | REWINDER TECHNO ELECTRICALS
2.24 | Supply and Fixing of secondary Connectors (male and Female) to 2C x 2.5 Sq.mm multi stranded annealed conductor PCP sheathed unshielded cable of 600 V grade on both ends. | 173.00 | Job | 1022.32 | 700.00 | 121100.00 | 800.00 | 138400.00 | 300.00 | 51900.00 | 1200.00 | 207600.00 | 51900.00 | YPR ENGINEERING AND SOLUTIONS PRIVATE LIMITED
2.25 | Numbering of Airfield Light Fixtures/Panel board on the front/base/ top surface/ RCC foundation with good quality of black color enamel paint with yellow background etc. complete as required. | 172.00 | Job | 156.00 | 10.00 | 1720.00 | 100.00 | 17200.00 | 50.00 | 8600.00 | 80.00 | 13760.00 | 1720.00 | REWINDER TECHNO ELECTRICALS
2.26 | MV Panel (GLF PANEL) Supply, Installation, Testing and Commissioning of indoor cubicle LT panel as per IEC 61439, IP42, suitable for 415V+/-10%, 3 Phase, 4 wire 50 Hz AC supply system, fabricated in compartmentalized modular design from CRCA sheet steel of 2 mm thick for frame work and covers, 3 mm thick for gland plates i/c cleaning & finishing complete with 7 tank process for powder coating in approved shade, having TPN Aluminium alloy bus bars with 100% size neutral bus as that of phase bus, supported with SMC bus bar supports, with short circuit withstand capacity as per design subject to minimum 25 kA for 1 sec, bottom base channel of MS section not less than 75 mm x 40 mm, fabrication shall be done in transportable sections, entire panel shall have a common Copper earth bus bar of size as per IS 3043 subject to minimum 32 mm x 5 mm at the rear with 2 Nos. earth stud, solid/ flexible copper connections from main earth bus bar to switchgears with required size of Cooper conductors/ bus bars and control wiring with 2.5 sqmm FRLS PVC insulated copper conductor cable, cable alleys, cable gland plates in two halves, including control and interlocking of incomers, bus coupler and providing following switchgears/ accessories as per specifications. Incomer 2 Nos. 100A, 4P MCCB, Microprocessor based release (Ics = Icu = 25kA) with inbuilt O/L , S/C & E/F protection as per specification and each incommer shall be provided with following accessories. 1 No. 96 x 96 sqmm Digital MFM meter and 3 nos. Cast resin CTs of ratio 100/5A , Class 0.5 accuracy and 10 VA burden, suitable to measure voltage, Ampere, Frequency, Power Factor, KVA, KW, KVAH, KWH, MDI with RS-485 port. 1 Set of ON/ OFF/TRIP Indicating LED Lamps With 2 Amp MCB Buscoupler 1 Nos. 100A 4P MCCB, Microprocessor based release (Ics = Icu = 25kA) with inbuilt O/L , S/C & E/F protection as per specification with following accessories. 1 Set of ON/ OFF/TRIP Indicating LED Lamps With 2 Amp MCB Electrical & Mechnical Interlocking between both incomers & Buscoupler Busbars 4P aluminium bus bars of 100A capacity with heat shrinkable coloured sleeves including SMC bus bars supports at required intervals complete for cross section, size supports & their spacing etc. for withstanding fault level of 25 KA for 1 sec. Outgoings 6 Nos. 63A 4P MCCB with built in thermal magnetic release with adjustable setting (Ics = Icu = minimum 25 KA) For each busbar section-1 Set Surge protection device Type 2 ( Class C), 4 Module, MOV type suitable for 8/ 20µs surge,Voltage Protection level Up < 1.5kV. SPD shall be with built in fuse and plugable type. For connecting SPD minimum 10sqmm copper wire must be used. The SPD shall be complient and tested from KEMA KEUR / VDE / NABL tested as per relevant IEC. GLF PANEL as described above. | 1.00 | Job | 427431.68 | 200001.00 | 200001.00 | 400000.00 | 400000.00 | 299980.00 | 299980.00 | 350000.00 | 350000.00 | 200001.00 | REWINDER TECHNO ELECTRICALS
2.27 | Supply Installation ,Testing and Commissioning of IGBT Three level PWM Design based, modular type, true online double conversion type 2 X 20 KVA UPS System in parallel configuration with harmonic filter suitable to drive constant current regulators(CCR) with 100% unbalanced load at output at full load condition , working on 3 phase, 4 Wire, 415 Volt, 50 Hz and delivering output 3 phase, 4 Wire, 415 Volt, 50 Hz , High Efficiency , having SMF Barreries to support minimum 30 minutes back up with each UPS, THD less than 3% , Power Factor not less than 0.90, having transfer time of 0 m sec, up along with all accessories i.e.breakers,DC cables, cabinets,battery racks, interconnecting links and related items etc as per site requirement for making the UPS Operational and meeting the standard of IEC and as per specification complete as required. | 1.00 | Job | 1502297.68 | 1200002.00 | 1200002.00 | 1800000.00 | 1800000.00 | 849301.00 | 849301.00 | 1750000.00 | 1750000.00 | 849301.00 | YPR ENGINEERING AND SOLUTIONS PRIVATE LIMITED
2.28 | Laying of one number PVC insulated & PVC sheathed XLPE power cable of 1.1 KV grade of following size in the existing masonary open duct/surface/pipe/raceway as per specification as required a) Above 95 sqmm and upto 185 sqmm | 150.00 | Mtr. | 50.96 | 10.00 | 1500.00 | 40.00 | 6000.00 | 110.00 | 16500.00 | 130.00 | 19500.00 | 1500.00 | REWINDER TECHNO ELECTRICALS
2.29 | Supplying and installing following size of perforated Hot dipped G.I. cable trays with perforation not more than 17.5%, in convienient sections, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc. as required. a) 150 mm width X 50 mm depth X 1.6 mm thickness | 300.00 | Mtr | 604.24 | 200.00 | 60000.00 | 450.00 | 135000.00 | 450.00 | 135000.00 | 920.00 | 276000.00 | 60000.00 | REWINDER TECHNO ELECTRICALS
2.30 | Laying and fixing of one no. PVC insulated and PVC Sheathed/XLPE Power of 1.1 KV grade of following sizes on the existing cable tray as required a) Upto 35 sqmm (clamped with 1mm thick saddle) | 200.00 | Mtr | 60.32 | 10.00 | 2000.00 | 50.00 | 10000.00 | 45.00 | 9000.00 | 60.00 | 12000.00 | 2000.00 | REWINDER TECHNO ELECTRICALS
2.31 | Laying and fixing of one no. PVC insulated and PVC Sheathed/XLPE Power cable of 1.1 KV grade of following sizes on the existing cable tray as required a) Above 95 sqmm and upto 185 sqmm | 100.00 | Mtr | 125.84 | 10.00 | 1000.00 | 50.00 | 5000.00 | 110.00 | 11000.00 | 200.00 | 20000.00 | 1000.00 | REWINDER TECHNO ELECTRICALS
2.32 | Supplying and making end termination with brass compression gland and Aluminimum lugs for following size of PVC insulated and PVC sheathed / XLPE Aluminium conductor cable of 1.1 KV grade as required. a) 3.5 X 120 Sq.mm | 4.00 | Set | 570.96 | 200.00 | 800.00 | 700.00 | 2800.00 | 600.00 | 2400.00 | 1200.00 | 4800.00 | 800.00 | REWINDER TECHNO ELECTRICALS
2.33 | Supplying and making end termination with brass compression gland and Copper lugs for following size of PVC insulated and PVC sheathed / XLPE Copper conductor cable of 1.1 KV grade as required. a) 3C x 16 Sq. mm. | 24.00 | Set | 370.24 | 200.00 | 4800.00 | 500.00 | 12000.00 | 400.00 | 9600.00 | 800.00 | 19200.00 | 4800.00 | REWINDER TECHNO ELECTRICALS
2.34 | Supplying and making end termination with brass compression gland and Copper lugs for following size of PVC insulated and PVC sheathed / XLPE Copper conductor cable of 1.1 KV grade as required. a) 4C x 16 Sq. mm. | 8.00 | Set | 360.88 | 200.00 | 1600.00 | 500.00 | 4000.00 | 400.00 | 3200.00 | 820.00 | 6560.00 | 1600.00 | REWINDER TECHNO ELECTRICALS
2.35 | Supply and fixing of fire retardant electrically insulated synthetic mat of class A, 2.5 mm thick suitable for all voltages not exceeding 11 KV AC and 240V DC system meeting requirements of IS 15652:2006 tested for breakdown strength, tensile/elongation, aging properties, insulation resistance, effect to acid, alkaline, diesel, transformer oil & leakage current test, fire test etc. having minimum width of 1000 mm ±20 mm along with all allied materials such as Pu-resin, Chemi bound, special PVC adhesive, liquid primer etc. in what so ever quantity required to complete the job as per site conditions and as per instructions from Engineer-in-Charge. | 20.00 | Mtr | 2208.96 | 800.00 | 16000.00 | 2100.00 | 42000.00 | 1400.00 | 28000.00 | 1000.00 | 20000.00 | 16000.00 | REWINDER TECHNO ELECTRICALS
2.36 | Supply and laying including termination of Armored Single-Mode Optic fiber cable (6-core) in existing pipe/masonary open duct/trench/open surface/raceway/cable tray as required | 6400.00 | Mtr | 100.88 | 60.00 | 384000.00 | 120.00 | 768000.00 | 90.00 | 576000.00 | 60.00 | 384000.00 | 384000.00 | Vardhman Airport Solutions Limited, REWINDER TECHNO ELECTRICALS
2.37 | Constructing 23cm thick brick wall masonry chamber in cement mortar 1:4 ( 1 cement : 4 coarse sand ) R.C.C top slab with 1:2:4 mix ( 1 cement : 2 coarse sand : 4 graded stone aggregate 20mm nominal size), foundation concrete 1:4:8 mix ( 1 cement : 4 coarse sand : 8 graded stone aggregate 40mm nominal size) inside plastering 12mm thick with cement mortar 1:3 ( 1 cement : 3 coarse sand ) finished with floating coat of neat cement complete as per standard design: Inside size1000 mm X 1000 mm x 1200 mm including RCC Cover is to be provided along with hook for lifting purpose etc complete as required as per the direction of Engineer-In-Charge | 6.00 | Job | 23354.24 | 4000.00 | 24000.00 | 21000.00 | 126000.00 | 25000.00 | 150000.00 | 20000.00 | 120000.00 | 24000.00 | REWINDER TECHNO ELECTRICALS
2.38 | DSR Works: Execution of works as per CPWD schedule of work and specifications as & when required: WORKS BASED ON DSR (E&M)-2022 ITEMS. Rate for Each one rupee value of work executed from the CPWD DSR (E&M)-2022 electrical rates. {For example if the quoted rate for this item is Rs. 0.90 then the executed DSR (E&M)-2022 schedule works of value Rs. 1,00,000.00 at DSR(E&M)-2022 rates, the quoted amount will be Rs. 90,000.00. And if quoted rate for this item is Rs. 1.25 then quoted amount for the same will be Rs. 1,25,000.00} | 50000.00 | Each | 1.04 | 0.60 | 30000.00 | 1.90 | 95000.00 | 4.00 | 200000.00 | 1.00 | 50000.00 | 30000.00 | REWINDER TECHNO ELECTRICALS
| Total in Figures |  |  |  |  | 15640553.00 |  | 29147960.00 |  | 19580001.00 |  | 24868065.00
Lowest Amount Quoted BY: REWINDER TECHNO ELECTRICALS(15640553.00)

## BOQ Summary
BOQ Summary Details Tender Title: SITC of GLF system works at Darbhanga Airport Tender ID: 2025_AAI_240167_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | REWINDER TECHNO ELECTRICALS (BID ID -882296) | 15640553.00 | L1
| 2 | YPR ENGINEERING AND SOLUTIONS PRIVATE LIMITED (BID ID -882498) | 19580001.00 | L2
| 3 | Vardhman Airport Solutions Limited (BID ID -877372) | 24868065.00 | L3
| 4 | Balaji Engineering (BID ID -882641) | 29147960.00 | L4