## BoQ1
Government eProcurement System Created By: Rahul S Mankar Created Date/Time: 02-Sep-2025 01:55 PM Tender Title: SITC of GLF Fixtures, Signage Boards and Allied Works at Jabalpur Airport Tender ID: 2025_AAI_240417_1
Tender Inviting Authority: AGM (E-E), Airports Authority of India, Jabalpur Airport, Jabalpur.
Name of Work : SITC of GLF Fixtures, Signage Boards & Allied Works at Jabalpur Airport.
Tender ID - 2025_AAI_240417_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Manish Electricals (GSTN-23ABLPM9012E1ZW) BID ID -887235 |  | JCC ENGINEERS PRIVATE LIMITED (GSTN-NA) BID ID -891045
[5 empty] | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply of FAA and ICAO compliant Inset type omni-directional 8" dia, 10-13 mm protrusion height, medium intensity, shallow depth (100 mm) runway turn pad LED edge light complete fixture with vulcanized plug for connection to isolating transformer, lamp holder assembly, Blue LED with lens with stopper & gaskets, O-ring, washers, brass cable gland assembly, shallow base with bottom hole entry and matching body of the fitting, inner body and outer cover made of die cast aluminium etc. and all other accessories complete as per technical specifications as required. | 12.00 | Each | 0.00 | 40000.00 | 480000.00 | 35000.00 | 420000.00 | 420000.00 | JCC ENGINEERS PRIVATE LIMITED
2.00 | Supply of FAA and ICAO compliant, Medium Intensity, elevated type, omni-directional Blue LED taxi way edge light fixture suitable for series circuit with 2.8 - 6.6 Amps complete with breakable coupling, die cast aluminium upper body, lens, lens bracket, control assembly, vulcanised two pin secondary lead plug for connection to isolating transformer, base plate, gaskets and all other accessories complete as per technical specifications as required (Fixed Intensity - For Turn Pad). | 28.00 | Each | 0.00 | 3700.00 | 103600.00 | 3500.00 | 98000.00 | 98000.00 | JCC ENGINEERS PRIVATE LIMITED
3.00 | Supply of FAA and ICAO compliant, Medium Intensity, elevated type, omni-directional Blue LED taxi way edge light fixture suitable for series circuit with 2.8 - 6.6 Amps complete with breakable coupling, die cast aluminium upper body, lens, lens bracket, control assembly, vulcanised two pin secondary lead plug for connection to isolating transformer, base plate, gaskets and all other accessories complete as per technical specifications as required (Variable Intensity - For Taxiway & Apron). | 12.00 | Each | 0.00 | 3700.00 | 44400.00 | 3500.00 | 42000.00 | 42000.00 | JCC ENGINEERS PRIVATE LIMITED
4.00 | Supply of FAA and ICAO compliant Inset type, bi-directional, 12" dia, 12-13 mm protrusion height, High Intensity runway edge light fixture, suitable for 2 x 105 Watt Halogen lamps complete with vulcanised plug for connection to isolating transformer, lamp holder assembly, clear prisms with stopper & gaskets-ring, washers, cable gland assembly, shallow base with bottom hole entry and matching body of the fitting, inner body and outer cover made of die cast aluminium etc. and all other accessories complete as per technical specifications as required. | 3.00 | Each | 0.00 | 60000.00 | 180000.00 | 54000.00 | 162000.00 | 162000.00 | JCC ENGINEERS PRIVATE LIMITED
5.00 | Supply of FAA and ICAO compliant Inset type, bi-directional, 12" dia, 12-13 mm protrusion height, High Intensity runway edge light fixture, suitable for 2 x 105 Watt Halogen lamps complete with vulcanised plug for connection to isolating transformer, lamp holder assembly, Yellow / Clear prisms with stopper & gaskets-ring, washers, cable gland assembly, shallow base with bottom hole entry and matching body of the fitting, inner body and outer cover made of die cast aluminium etc. and all other accessories complete as per technical specifications as required. | 3.00 | Each | 0.00 | 60000.00 | 180000.00 | 54000.00 | 162000.00 | 162000.00 | JCC ENGINEERS PRIVATE LIMITED
6.00 | Supply, Installation, Testing & Commissioning of ICAO compliant Aviation Orange colour coated, Aluminium Alloy body, IP-66/67 rated Airport Rotating Beacon with flashing rate of 24 - 30 flashes/min, pre-focussed, narrow angle, four lamp heads with 4 Nos x 120 V, 1000 W PAR 64 lamps with holder (02 lamps are used as back-up and will automatically be energized in case of failure of one of the on-duty lamps), with obstruction light, suitable for operation on 230 VAC, single phase supply etc. and all other accessories complete as per technical specifications as required. (Beacon base size shall not be more than 550 mm x 550 mm) | 1.00 | Each | 0.00 | 550000.00 | 550000.00 | 385000.00 | 385000.00 | 385000.00 | JCC ENGINEERS PRIVATE LIMITED
7.00 | Supply, installation, testing and commissioning of mandatory/ information operational area guidance sign board of various sizes, meeting ICAO Annex 14 specifications, made out of 4 mm thick glare free polycarbonate sheet at front and body made out of 2.0 mm thick powder coated aluminium sheet and frangible coupling as required. Light source shall be high luminous, long life typical 50,000 Hrs type, 0.5 Watts LED's assembled on aluminium PCB of size approx. 700mm X 30mm and having minimum 11 LED's per PCB. The thickness of the aluminium PCB should be 2 mm in order to ensure proper heat dissipation. Board should be equipped with converter suitable for operation on 2.8 A to 6.6 A series airfield lighting circuit without flickering, internal wiring, water tight & locking arrangement etc., grouting of each mounting each leg is to be made of Aluminium having frangibility. The Aluminium leg should have fixing plate at bottom so that each leg can be fixed with frangible coupling on the concrete block with M 10 bolts by providing & laying 1:2:4 (1 Cement: 2 Coarse sand : 3 graded stone aggregate 20 mm nominal size) cement concrete foundation of suitable size) including excavation, shuttering & centring, refilling, levelling etc., secondary cable laying, connection to isolating transformer, crimping / jointing of plug & receptacles including filling the gap with water sealant material & applying PVC HT insulation tape, testing and commissioning etc. complete as per technical specifications as required. (Excluding Isolating transformer and secondary cable for connections). | 11.00 | Sq. Meter | 0.00 | 38000.00 | 418000.00 | 40000.00 | 440000.00 | 418000.00 | Manish Electricals
8.00 | Supply of FAA and ICAO compliant 5 KV, 50 Hz, PCP isolating transformer of following rating, suitable for individual series lamps airport lighting circuits, encapsulated in polyster resin and finally moulded with neoprene rubber with primary & secondary connection leads etc. complete as per technical specifications as required.
8.01 | 15 Watts 6.6/6.6 Amps | 48.00 | Each | 0.00 | 2800.00 | 134400.00 | 2500.00 | 120000.00 | 120000.00 | JCC ENGINEERS PRIVATE LIMITED
8.02 | 300 Watts 6.6/6.6 Amps | 6.00 | Each | 0.00 | 6500.00 | 39000.00 | 5500.00 | 33000.00 | 33000.00 | JCC ENGINEERS PRIVATE LIMITED
9.00 | Supply of FAA and ICAO compliant 6 sq.mm plug & receptacle of type-I, class-B connector with suitable field attachment and suitable for 5 KV grade XLPE insulated PE sheathed single core screened copper conductor cable etc. complete as per technical specifications as required. | 68.00 | Each | 0.00 | 550.00 | 37400.00 | 600.00 | 40800.00 | 37400.00 | Manish Electricals
10.00 | Supply of FAA and ICAO compliant elevated type high intensity uni-directional approach light fitting suitable for use with 150 Watts, 6.6 Amps Halogen lamp complete with breakable coupling, die-cast Aluminium Alloy body, central column assembly, vulcanised two-pin secondary lead plug for connection to isolation transformer, base plate, gasket, inner lens with clamping mechanism, elevation and horizontal adjustment mechanism, pre-focus lamp holder, gaskets, washers, clear front lens, anodized Aluminium reflector etc. complete with all accessories as required. | 20.00 | Each | 0.00 | 9800.00 | 196000.00 | 9500.00 | 190000.00 | 190000.00 | JCC ENGINEERS PRIVATE LIMITED
11.00 | Supply of 6.5 watts, LED type, IP-66 rated fixture suitable for AMA make Landing H Indicator, compliant with ICAO CAR requirements, Yellow light output, suitable for 230 VAC supply etc.. complete as required. (Ray dynamic model LTL-5Y-UI or Similar). | 20.00 | Each | 0.00 | 3500.00 | 70000.00 | 4000.00 | 80000.00 | 70000.00 | Manish Electricals
12.00 | Supply of 150 W, 6.6 Amps bi-pin halogen lamps suitable for AMA Make elevated runway light fixtures etc. as required. | 400.00 | Each | 0.00 | 600.00 | 240000.00 | 650.00 | 260000.00 | 240000.00 | Manish Electricals
13.00 | Supply of Bi-pin holder for 150/200 W halogen lamp to be installed in AGL light fixtures, etc. as required. (Make: AMA) | 400.00 | Each | 0.00 | 450.00 | 180000.00 | 480.00 | 192000.00 | 180000.00 | Manish Electricals
14.00 | Supply of 6 mm thick powder coated MS cover plate with 300 mm outside dia, to cover the CI/MS transformer housing box, complete with 6 nos. M10 tapped holes matching with housing box etc. complete as required. (Supply of bolts not included in the scope). | 10.00 | Each | 0.00 | 1425.00 | 14250.00 | 1200.00 | 12000.00 | 12000.00 | JCC ENGINEERS PRIVATE LIMITED
15.00 | Supply of Red Filter suitable for AMA make PAPI units installed at site and compliant with ICAO CAR specifications, complete with all accessories as required. (Make: AMA) | 24.00 | Each | 0.00 | 4800.00 | 115200.00 | 6500.00 | 156000.00 | 115200.00 | Manish Electricals
16.00 | Supply of inner & outer gasket suitable for inset light fitting (Make: ADB Safegate) installed at site complete with all accessories as required as per standard ICAO/CAR specifications. | 20.00 | Each | 0.00 | 600.00 | 12000.00 | 1500.00 | 30000.00 | 12000.00 | Manish Electricals
17.00 | Supply of 100 A HRC Fuse, bolt type 690 VAC (Make: Bussmann) complete with all accessories as required. | 15.00 | Each | 0.00 | 500.00 | 7500.00 | 900.00 | 13500.00 | 7500.00 | Manish Electricals
18.00 | Supply of 200 A HRC Fuse, bolt type, 700 VAC (Make: Bussmann) complete with all accessories as required. | 10.00 | Each | 0.00 | 900.00 | 9000.00 | 900.00 | 9000.00 | 9000.00 | Manish Electricals, JCC ENGINEERS PRIVATE LIMITED
19.00 | Supply of Low Voltage 20 A HRC Fuse, 500 VAC, 120 kA (Make: Siemens) Model: 3NA7 807-0RC complete as required. | 10.00 | Each | 0.00 | 150.00 | 1500.00 | 400.00 | 4000.00 | 1500.00 | Manish Electricals
20.00 | Supply of Low Voltage 32 A HRC Fuse, 500 VAC, 120 kA (Make: Siemens) Model: 3NA7 812- 0RC complete as required. | 10.00 | Each | 0.00 | 200.00 | 2000.00 | 325.00 | 3250.00 | 2000.00 | Manish Electricals
21.00 | Supply of Low Voltage 63 A HRC Fuse, 500 VAC, 120 kA (Make: Siemens) Model: 3NA7 822-0RC complete as required. | 10.00 | Each | 0.00 | 325.00 | 3250.00 | 325.00 | 3250.00 | 3250.00 | Manish Electricals, JCC ENGINEERS PRIVATE LIMITED
22.00 | Supply of Low Voltage 160 A HRC Fuse, 500 VAC, 120 kA (Make: Siemens) Model: 3NA 3NA7 136-0RC complete as required. | 10.00 | Each | 0.00 | 550.00 | 5500.00 | 460.00 | 4600.00 | 4600.00 | JCC ENGINEERS PRIVATE LIMITED
23.00 | Supply, Installation, Testing & Commissioning of Single phase input/output online 3 KVA UPS, with Input voltage range 150-280 VAC, Output voltage : 230 VAC constant, suitable for backup time of minimum 15 minutes, Zero change over time, Pure sine wave output, Low total harmonic distortion <= 3%, protection features to ensure 100% protection to the load, input power factor correction, power factor > 0.7, High efficiency > 85%, Voltage regulation +/- 1%, Operating temp. 0 Deg. C to 40 Deg. C, Audible warning alarms; short circuits, overload, battery deep discharge & over charge protection, installation at site with accessories, communication interface & management etc. complete as required. (Excluding Batteries for Backup). | 4.00 | Job | 0.00 | 48000.00 | 192000.00 | 90000.00 | 360000.00 | 192000.00 | Manish Electricals
24.00 | Supply, Installation, Testing & Commissioning of 26 AH - 12 V SMF Battery complete with all accessories as required. | 24.00 | Each | 0.00 | 3000.00 | 72000.00 | 3000.00 | 72000.00 | 72000.00 | Manish Electricals, JCC ENGINEERS PRIVATE LIMITED
25.00 | Supply, Installation, Testing & Commissioning of horizontal double mounting siren with audible range of 5 kms, suitable for 3 phase AC supply, 3 H.P. motor rating, 2800 rpm, including suitable size MS Framing for mounting arrangement etc. complete with all accessories as required. (Make: Kheraj / Model: HDT-500 or similar). | 1.00 | Each | 0.00 | 54000.00 | 54000.00 | 80000.00 | 80000.00 | 54000.00 | Manish Electricals
26.00 | Supply, Installation, Testing & Commissioning of motorized, open execution auto changeover switch in existing LT panels, rating - 125 A, 4 Pole, 415 VAC, 50 Hz, conforming to IS/IEC 60947-3, with all standard accessories e.g. terminal shroud, phase barriers, source separator, auxiliary contacts, extended handle with shaft etc. complete with dismantling old switchgear in LT panel for replacement, accessories and minor job work required for mounting, making power / control connections etc, complete as required. (Make: L&T - Lauritz Knudsen / Model - FR2 125A, 4P, 415 VAC or similar). | 3.00 | Each | 0.00 | 41000.00 | 123000.00 | 45000.00 | 135000.00 | 123000.00 | Manish Electricals
27.00 | Supply and laying of DWC/HDPE pipe of outer dia up to 50 mm by cutting of pipe groove with kerf cutting machine for laying of AGL cable in the concrete/ bituminous runway surface i/c kerfing, chiselling, cleaning and filling the groove with concrete and making good the same complete etc. as required. | 60.00 | Mtr | 0.00 | 900.00 | 54000.00 | 450.00 | 27000.00 | 27000.00 | JCC ENGINEERS PRIVATE LIMITED
28.00 | Supplying and laying of 50 mm outer dia DWC HDPE pipe along with all accessories like socket, bend, couplers etc. marked conforming to IS 14930, Part II complete with fitting and cutting, jointing etc. direct in ground at 45 cm depth below ground level including excavation and refilling the trench but excluding sand cushioning and protective covering etc. complete as required. | 300.00 | Mtr | 0.00 | 210.00 | 63000.00 | 280.00 | 84000.00 | 63000.00 | Manish Electricals
29.00 | Laying of one number XLPE insulated & PE sheathed un-armoured copper conductor Runway primary / secondary cable of grade 5 KV of size not exceeding 16 Sq.mm in the existing RCC / HUME / STONEWARE / METAL / HDPE pipe etc. as required. | 1320.00 | Mtr | 0.00 | 50.00 | 66000.00 | 50.00 | 66000.00 | 66000.00 | Manish Electricals, JCC ENGINEERS PRIVATE LIMITED
30.00 | Installation, testing and commissioning of elevated runway edge / turn pad / taxiway light fittings with all accessories on the existing transformer housing box i/c. assembling of accessories, alignment, levelling, installation of isolating transformer, crimping / jointing of plug & receptacles including filling the gap with water sealant material & applying PVC HT insulation tape etc. complete as required. | 34.00 | Job | 0.00 | 250.00 | 8500.00 | 600.00 | 20400.00 | 8500.00 | Manish Electricals
31.00 | Installation, testing, commissioning of inset runway edge light fittings with shallow base on runway i/c cutting the concrete / bitumen pavement with core cutting machine, installing the inset fitting with shallow base with the help of jigs, filling the bottom and side with sealant DOBEFIL-60/Hardener mixture, installation of isolating transformer, crimping / jointing of plug & receptacles, connections including filling the gap with water sealant material & applying PVC HT insulation tape, making connection with secondary lead & isolating transformer, levelling, aligning etc. complete as required. | 14.00 | Job | 0.00 | 7500.00 | 105000.00 | 7900.00 | 110600.00 | 105000.00 | Manish Electricals
32.00 | Dismantling, shifting & reinstallation of existing mandatory / guidance signboard in operational area along with existing isolating transformer housing box, including grouting of each mounting leg by providing & laying 1:2:4 (1 Cement: 2 Coarse sand : 3 graded stone aggregate 20 mm nominal size) cement concrete foundation of suitable size) including excavation, shuttering & centring, refilling, levelling etc., fixing of coupling through M10 bolts, secondary cable laying, connection to isolating transformer, crimping / jointing of plug & receptacles, supply & making permanent joints with jointing kit of suitable grade for 5 KV 6 Sqmm AGL cable extension of both runway circuits up to new signboard location, including filling the gap with water sealant material & applying PVC HT insulation tape, testing and commissioning asper ICOA CAR requirements etc. complete as required. (Excluding Isolating transformers, plug & receptacle and secondary cable). | 5.00 | Set | 0.00 | 9000.00 | 45000.00 | 12000.00 | 60000.00 | 45000.00 | Manish Electricals
33.00 | Dismantling, shifting of existing 01 number RWY elevated end light and 01 number elevated threshold light at RWY 06 side including re-installation, testing, commissioning along with cutting the concrete / bitumen pavement with core cutting machine, supply & installing the MS housing box (330 mm x 330 mm, 150 mm height, made of top & bottom surfaces with 10 mm thick plate and side surfaces with 6 mm thick plates and having two holes to receive DWC / GI pipes as per site requirement, clear opening of 225 mm dia. on top surface, 06 nos. M10 tapped holes on top surface to match base plates of light fittings, drain hole on bottom surface to receive 15 mm dia. GI pipe, SS earth studs with bolts etc.) with the help of jigs, filling the bottom and side with sealant DOBEFIL-60/Hardener mixture, installation of isolating transformer, crimping / jointing of plug & receptacles connection including filling the gap with water sealant material& applying PVC HT insulation tape, making connection with secondary lead & isolating transformer, levelling, aligning etc. complete as required. (Excluding Isolating transformers, plug & receptacle and secondary cable). | 1.00 | Job | 0.00 | 12800.00 | 12800.00 | 17000.00 | 17000.00 | 12800.00 | Manish Electricals
34.00 | Supply of 105W, 6.6A, Pre-focus dichroic coated reflector lamp suitable for use in ADB Safegate make inset airfield lighting fixtures (Similar to OSRAM make Cat. No. 64339A or Philips/Narva make Cat. No. 58308) etc. complete as required. | 50.00 | Each | 0.00 | 1400.00 | 70000.00 | 1450.00 | 72500.00 | 70000.00 | Manish Electricals
35.00 | Supply of Alignment device for Elevated Runway Approach / Threshold / End Light with following features complete with all accessories as required. (Make: AMA / Model: AD-APN or similar) a) Shall have accurate telescope for exact horizontal alignment. b) Shall have digital clinometer for accurate vertical alignment. c) Shall have provision for toe-in angle setting. | 1.00 | Set | 0.00 | 105000.00 | 105000.00 | 80000.00 | 80000.00 | 80000.00 | JCC ENGINEERS PRIVATE LIMITED
36.00 | Manufacturing, supplying and fixing retro-reflective sign board made up of 3 mm thick Aluminium sheet, face to be fully covered with high intensity encapsulated type heat activated retro-reflective sheeting conforming to type-IV of ASTM-D 4956 in Red and silver white or other colour combination including subject matter, message (bilingual), symbols and borders etc. as per IRC : 67:2001 / DGCA CAR /requirements, pasted on substrate by an adhesive backing which shall be activated by applying heat and pressure and fixing the same with suitable sized aluminium alloy rivets @ 20 cm c/c to back support frame of Aluminium extrusion of size 25x25x3 mm including provision of frangible coupling, suitable nos. & size anodized powder coated Aluminium pipes, aluminium alloy base plate for mounting the legs with frangible coupling on concrete pedestal with M10 anchor bolts, backside of Aluminium sheet to be painted with two or more coats of epoxy paint over and including appropriate priming coat, providing & laying 1:2:4 (1 Cement: 2 Coarse sand : 3 graded stone aggregate 20 mm nominal size) cement concrete foundation of suitable size including excavation, shuttering & centring, refilling, levelling, fixing of base plates with M10 anchor bolts etc. complete as required as per technical specifications and direction of Engineer-In-Charge. | 5.00 | Sq. Meter | 0.00 | 21000.00 | 105000.00 | 15000.00 | 75000.00 | 75000.00 | JCC ENGINEERS PRIVATE LIMITED
| Total in Figures |  |  |  |  | 4098300.00 |  | 4119900.00
Lowest Amount Quoted BY: Manish Electricals(4098300.00)

## BOQ Summary
BOQ Summary Details Tender Title: SITC of GLF Fixtures, Signage Boards and Allied Works at Jabalpur Airport Tender ID: 2025_AAI_240417_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Manish Electricals (BID ID -887235) | 4098300.00 | L1
| 2 | JCC ENGINEERS PRIVATE LIMITED (BID ID -891045) | 4119900.00 | L2