## BoQ1
Government eProcurement System Created By: Debdeep Dutta Created Date/Time: 21-Aug-2025 06:48 PM Tender Title: Provision for the works for compliance of the observation by Aviation Safety at Katihar. Sub head- Rectification or repair of HT panel, AVR and provision of AVR cum Transformer and its associated works at Katihar MSSR station Tender ID: 2025_AAI_240943_1
Tender Inviting Authority: AGM(E-E)
Name of Work: Provision for the works for compliance of the observation by Aviation Safety at Katihar. Sub head: - Rectification or repair of HT panel, AVR and provision of AVR cum Transformer and its associated works at Katihar MSSR Station
Contract No: 2025_AAI_240943_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | HLP SOLUTION (GSTN-NA) BID ID -877671
[5 empty] | Rate | Amount | L1 Amount | L1 Vendor
1.00 | PART A REPAIR WORKS OF EXISTING PANELS & AVR
2.00 | HT PANEL
3.00 | 11 KV VCB Incomer- 1 Nos and Outgoing - 2Nos
4.00 | Overhauling cleaning/servicing/rectification of existing 11 KV Kirloskar make VCB panel with 3 Nos. VCBs, totally enclosed & fully interlocked , 11 KV VCB Mechanism dismantling, 11 KV CT Spouts dismantling from Panel, VI Housing Rubbing, Cleaning by applying CRC, WD-40, Varnishing done by applying Red Insulation Varnish and Heating treatment done for IR Improvement, AC & DC control circuit rectification, closing circuit rectification, Racked IN inside Panel and power charging, checking all operational mechanism , functions,tripping action, proper operation of relays and meter via secondary current injection test by standard procedure as per IEC 62271-200, as amended up to date and additional specifications and as per special conditions complete as required. Job includes following works to be carried out for keeping the HT Panel & breaker in servicable condition as per OEM guidelines and providing training to staff on operations of VCBs including Rack in and Rack out. | 1.00 | Job | 511539.00 | 498750.00 | 498750.00 | 498750.00 | HLP SOLUTION
5.00 | 11 KV VCB INCOMER
6.00 | a) SITC of 1 no of power pack I/P:- 220V AC, O/P : 24 V DC
7.00 | b) SITC of 1 no of 8 Window Annunciator (Make : Minilec Model- MBAS 08 or equivalent)
8.00 | c) SITC of 1 no of 3 Phase Digital Ammeter (Make : Schneider or equivalent)
9.00 | d) SITC of 4 nos of 200W space heater (make : RECO, 230 V or equivalent) and 2 nos of Thermostat (Make: ELCON GOLD, Model : MM-106 or equivalent) along with connection
10.00 | e) SITC of 1 no of 25 Amp TNC switch (Make : Kaycee or equivalent)
11.00 | OUTGOING-1
12.00 | a) SITC of 1 no of power pack I/P:- 220V AC, O/P : 24 V DC
13.00 | b) SITC of 1 no of 8 Window Annunciator (Make : Minilec Model- MBAS 08 or equivalent)
14.00 | c) SITC of 1 no of 3 Phase digital Ammeter and voltmeter (Make : Schneider or equivalent)
15.00 | d) SITC of 4 nos of 200W space heater (make : RECO, 230 V or equivalent) 2 nos Thermostat (Make: ELCON GOLD, Model : MM-106 or equivalent) along with connection for each panel
16.00 | e) SITC of 1 no 25 Amp TNC switch (Make : Kaycee or equivalent)
17.00 | f) Replacement of defective 1 no of TCS relay and SITC of 1 no of TCS relay (Make- EasunReyrolle, Model- XR351, Aux volt- 24 V DC or equivalent )
18.00 | g) SITC of 1 no of Multi-Function Meter (Make: Schneider, Model: EM6400NG or equivalent)
19.00 | h) SITC of 1 no of Auxiliary Relay for Trip supply (Make: EasunReyrolle, Model: B33X3, Aux. supply: 24 V DC or equivalent)
20.00 | i) SITC of 1 no of Auxiliary Relay for Alarm supply (Make: EasunReyrolle, Model: B33X3, Aux. supply: 24 V DC or equivalent)
21.00 | j) SITC of 1 no of closing coil for Kirloskar make or equivalent 11 KV Outgoing-1 VCB Coil Voltage: 24 V DC
22.00 | k) SITC of 1 no of tripping coil for Kirloskar make or equivalent 11 KV Outgoing-1 VCB Coil Voltage: 24 V DC
23.00 | l) SITC of 3 set of Current Transformer Ratio: 25/5+5 A, Core1: 7.5 VA, Class: 1.0 Core2: 7.5 VA, Class: 5P20 STC: 25 kA for 1 SEC, HSV : 12 KV, ILV : 28/75 KV
24.00 | OUTGOING-2
25.00 | a) SITC of 1 no of power pack I/P:- 220V AC, O/P : 24 V DC
26.00 | b) SITC of 1 no of 8 Window Annunciator (Make : Minilec Model- MBAS 08 or equivalent)
27.00 | c) SITC of 1 no of Electronic Buzzer
28.00 | d) SITC of 6 nos of 200W space heater (make : RECO, 230 V or equivalent) 3 nos Thermostat (Make: ELCON GOLD, Model : MM-106 or equivalent) along with connection with each panel and Bus-Bar section
29.00 | e) SITC of 1 no of 25 Amp TNC switch (Make : Kaycee or equivalent)
30.00 | AVR
31.00 | 250 KVA AVR (9-12 KV/433V) Unit-"A","B","C"
32.00 | Overhauling servicing/rectification of existing 250 KVA (9-12 KV/433 V) Brentford make AVR including oil filtration, testing of transformer oil (BDV Test) before and after filtration till reach of satisfactory di-electric strength of 50 KV or above, providing grouting material and grouting works, minor adjustment and reapir, replacement of wornout/defective parts like auxillariary contactor, PCB relay card,OTI, gaskets, oil seal for HT and LT busing , gasket change,arresting of any oil leakage,top cover, inspection cover, tap switch, conservator tank, radiators, buchholz, drain valve (as where required) and HT-LT bushing portion etc complete as required. Job includes following works for keeping the AVR in servicable condition as per OEM guidelines and providing training to staff on operations of AVR | 1.00 | Job | 328426.00 | 315755.00 | 315755.00 | 315755.00 | HLP SOLUTION
33.00 | 250 KVA AVR (9-12 KV/433V) Unit-"A"
34.00 | a) Oil filtration and di electric strength test for A unit
35.00 | b) Supply and fixing of transparent breather and replacement of silica gel as per site.
36.00 | c) Supply and fixing of Cu Link (50 mm X5 mm) as per site.
37.00 | d) SITC of 4 nos of 12 mm STUDD and 3 nos of 19 mm STUDD
38.00 | 250 KVA AVR (7-12 KV/11 KV) Unit-"B"
39.00 | a) Oil filtration and di electric strength test for B unit
40.00 | b) Supply and fixing of transparent breather and replacement of silica gel as per site.
41.00 | c) SITC of 1 no of Control transformer 50VA, 240V/110V
42.00 | d) SITC of 1 no of Aux contactor (4NO-4 NC) Make : Siemens/ABB or equivalent, Coil voltage : 110 VAC
43.00 | e) SITC of 3 no of Aux contactor (3NO-2 NC) Make : Siemens/ABB or equivalent, Coil voltage : 220 VAC
44.00 | f) SITC of 1 no of PCB Relay card
45.00 | g) SITC of 6 Nos of Carbon Roller and Tag & Tail
46.00 | h) SITC of 1 no of 1000VA UPS , Input: 230 V AC
47.00 | i) SITC of 1 no of Catler Hammer Timer (Coil Volt- 220 V AC)
48.00 | j) SITC of 6 Inch OTI with 2 nos micro switch and 5 mtrs capillary (Make- PTCI or equivalent)
49.00 | 250 KVA AVR (9-12 KV/433 V) Unit-"C"
50.00 | a) Oil filtration and di electric strength test for C unit
51.00 | b) Supply and fixing of transparent breather and replacement of silica gel as per site.
52.00 | PART B SITC WORKS
53.00 | AVR CUM TRANSFORMER
54.00 | Design, supply,transportation, assembling, installing in position, testing and commissioning of copper wound 250 KVA oil immersed,naturally cooled, on load, stepless, Indoor type HT AVR Transformers having input voltage 9000V to 12000V 3 phase 50 Hz to get output stablized voltage at 415 V +- 1%, 3 phase, 50 Hz consist of main step down transformer unit having capacity 295 KVA, regulator unit capacity 50/+-415/415 and Buck/Boost unit capacity 45 KVA including civil foundation work in paved area with associated work as per specifications complete as required. Unit A- Main step down transformer completely independent unit complete with all fittings such as uni/bidirectional plain rollers,lifting lugs,earthing terminals,rating plate, filter valve,drain valve, oil filling hole, thermometer pocket, oil level gauge, silica gel breather, conservator, explosion vent, buchholz relay, marshalling box, Radiator Shut-off Valve, OTI, pressure release valve etc complete as required Unit (B & C) Buck boost & regulator in same base but separated by steel plate with all fittings such as uni/bidirectional plain rollers,lifting lugs,earthing terminals,rating plate, diagram plate, drain valve, oil filling hole, thermometer pocket, oil level gauge, marshalling box, Radiator Shut-off Valve, OTI etc complete as required. (The above transformer shall have losses as per ECBC compliant.) | 1.00 | Job | 1897386.00 | 1795000.00 | 1795000.00 | 1795000.00 | HLP SOLUTION
55.00 | PART C MISCELLENOUS WORKS
56.00 | Top up the transformer with ISI marked Transformer oil during filtraion as per site requirement etc complete as required | 1000.00 | Ltr | 189.00 | 145.00 | 145000.00 | 145000.00 | HLP SOLUTION
57.00 | Supplying and making indoor cable end termination with heat shrinkable jointing kit complete with all accessories including lugs suitable for 120 sq. mm. X 3 core, 11 KV grade, XLPE aluminium conductor cable of 11 KV grade as required | 15.00 | Job | 17353.00 | 8000.00 | 120000.00 | 120000.00 | HLP SOLUTION
58.00 | Supplying and making outdoor cable end termination with heat shrinkable jointing kit complete with all accessories including lugs suitable for 120 sq. mm. X 3 core, 11 KV grade, XLPE aluminium conductor cable of 11 KV grade as required | 2.00 | Job | 22075.00 | 10000.00 | 20000.00 | 20000.00 | HLP SOLUTION
59.00 | Supplying of the following sizes of 11KV aluminium, armoured XLPE HT power cable as per IS7098(part-2)-1985 amended up to date, as per specifications. (The outer sheath shall be FRLS.) a) 11 KV, 3C x 120 Sq. mm XLPE Aluminium Armoured cable | 50.00 | Mtr | 1693.00 | 1500.00 | 75000.00 | 75000.00 | HLP SOLUTION
60.00 | Laying of one number PVC insulated and PVC sheatehd / XLPE power cable of 11 KV grade of upto 120 sq. mm on existing cable tray/ direct in ground including excavation, sand cushioning, protective covering and refilling the trench etc as required. | 50.00 | Mtr | 488.00 | 77.00 | 3850.00 | 3850.00 | HLP SOLUTION
61.00 | Supply and drawing of 2.5 Sq mm, single core 1.1 KV grade copper cable for space heater and thermostat wiring. | 100.00 | Mtr | 116.00 | 60.00 | 6000.00 | 6000.00 | HLP SOLUTION
62.00 | Supply and laying of 2.5 sq mm x 3 core Cu cable for UPS connection | 30.00 | Mtr | 197.00 | 355.00 | 10650.00 | 10650.00 | HLP SOLUTION
63.00 | Supply and laying of 2.5 sq mm x 12 core Cu armoured. cable for protection purpose | 30.00 | Mtr | 549.00 | 505.00 | 15150.00 | 15150.00 | HLP SOLUTION
64.00 | SITC 1 KVA UPS for AVR Cum Transformer. | 2.00 | Job | 5604.00 | 13000.00 | 26000.00 | 26000.00 | HLP SOLUTION
65.00 | Supply and fixing of 2.5 mm (nominal ± 10%) thick and 1 mtr wide synthetic insulation mat suitable for 11KV grade as per IS: 15652:2006 with upto date amendments. Insulating mat should be flexible, anti-skid, fire retardant, water and moisture proof with no adverse effect of acids, alkalis and transformer oil and other sealing materials as per specifications. Insulating mats should be lSI marked along- with CM/L nos at every meter. Insulating mats should be ERDA and CPRI tested. | 50.00 | Sq Mtr | 863.00 | 850.00 | 42500.00 | 42500.00 | HLP SOLUTION
66.00 | Supply and fixing of following types of high voltage Synthetic Insulating Mat made out of synthetic Elastomer conforming to IS 15652:2006 with minimum width of 1 Metre. Insulating mat should be flexible, anti-skid, fire retardant, water and moisture proof with no adverse effect of acids, alkalis and transformer oil. Insulating mat should be fixed with suitable adhesive/Chem bound resin, water proofing compound and other sealing materials as per specifications. Insulating mats should be lSI marked along- with CM/L nos at every meter. Insulating mats should be ERDA and CPRI tested. (a) Class- A type, Up-to 3.3 KV (Thickness: 2 mm) | 50.00 | Sq Mtr | 744.00 | 750.00 | 37500.00 | 37500.00 | HLP SOLUTION
67.00 | Earthing with G.I. earth plate 600 mm X 600 mm X 6 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with charcoal/ coke and salt as required. | 6.00 | Job | 5534.00 | 7000.00 | 42000.00 | 42000.00 | HLP SOLUTION
68.00 | Providing and fixing 25 mm X 5 mm G.I. strip in 40 mm dia G.I. pipe from earth electrode including connection with G.I. nut, bolt, spring, washer excavation and re-filling etc. as required. | 100.00 | Mtr | 527.00 | 500.00 | 50000.00 | 50000.00 | HLP SOLUTION
69.00 | Providing and fixing 50 mm X 6 mm G.I. strip on surface or in recess for connections etc. as required. | 100.00 | Mtr | 181.00 | 600.00 | 60000.00 | 60000.00 | HLP SOLUTION
| Total in Figures |  |  |  |  | 3263155.00
Lowest Amount Quoted BY: HLP SOLUTION(3263155.00)

## BOQ Summary
BOQ Summary Details Tender Title: Provision for the works for compliance of the observation by Aviation Safety at Katihar. Sub head- Rectification or repair of HT panel, AVR and provision of AVR cum Transformer and its associated works at Katihar MSSR station Tender ID: 2025_AAI_240943_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | HLP SOLUTION (BID ID -877671) | 3263155.00 | L1