## BoQ1
Government eProcurement System Created By: Sachin Khangar Created Date/Time: 29-Aug-2025 01:15 PM Tender Title: Provision of 30.52 KW Roof Top Solar Power System at Diu airport Tender ID: 2025_AAI_241108_1
Tender Inviting Authority: Joint Gen. Manager(E-E), AAI, CA, Vadodara
Name of Work: -Provision of 30.52 KWp Roof Top Solar Power System at Diu airport.
Contract No: AAI /WR/ EE/Diu/Solar/N-5/2025-26
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | M/S Renesys Power Systems Private Limited (GSTN-24AAICR4957J1ZY) BID ID -874489 |  | Naturetech Infrastruture Pvt. Ltd. (GSTN-NA) BID ID -883230 |  | INSTANT ELECTRIC SERVICES (GSTN-NA) BID ID -882774
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.10 | Design, supply, installation, testing and commissioning of Rooftop Solar PV Systems Conforming to MNRE Specifications Consisting of Mono Crystalline Silicon Solar Cells, Net metering facility, necessary Protections, Earthing, Mounted on Hot Dip Galvanized Structure of Suitable Strength with Following Components: i)Solar PV Mono Crystalline half cut module 540 Wp or above capacity, manufactured in India conforming to IS 14286/IEC, 61215, IS/IEC61730-Part-1, IS/IEC 61730-Part-2. Solar photovoltaic module conversion efficiency shall not be less than 16.5%, PV modules use solar power plant must be warranted for their output peak watt capacity which should not be less than 90% at the end off 10 years and 80% at the end of 25 years. ii)Power Conditioning Unit (PCU) of 350-800 V DC Input voltage range and 400 V AC, three phase, 4 wire, 50Hz +/- 2.5 Hz, output voltage suitable to generate AC Power with efficiency not less than 97%, total harmonic distortion less than 3% and suitable for ambient temperature from 0 to 50°C. The PCU shall adjust the voltage and frequency level to suit the Grid Voltage Frequency. Data Monitoring System complete with accessories. iii)DCDB & ACDB with Energy Meter & remote monitoring system (Ethernet/Wireless based) iv) Array junction box & Main junction box with IP 65 protection and termination arrangement for incoming and outgoing cable: along with glands, lugs and other accessories as required. v) Galvanized Iron Solar PV Structure suitable for seashore environment (Heavily Corrosive) for Sloppy Sheet metal roof mounted system or as per site requirement. vi) Lightning and surge voltage protection i/c 2 No. of lightening protection, 2 no. of AC earthing, 4 No. of DC earthing. vii) AICMC of above said Solar power Plant for 05 years after expiry of DLP 02 years. viii) Connections & Interconnections by supplying & fixing required size XLPE insulated copper/Al. conductor 1.1 kV grade armoured AC & DC power cable as below- a.Suitable AC Cable(Inverter to ACDB) & (ACDB to Panel) b.1x4 sqmm DC Cable including MC4 connector c.control cables if required along with supplying & fixing of necessary and other lugs channel/conduit accessories etc. ( As per Annexure "K" Drawing) ix) Carrying out Glint/Glare Analysis if Required at site for safe flight operations, shadow analysis, clearance/approval from DISCOM, CEA and other statuatory agencies, transportaions & insuarnce of materials etc and all other items/ acessories/ services which are required for successful commissioning of Solar Power plant complete as required as per technical specifications & terms & conditions of the contract. x) Automatic Solar Panel Cleaning system with spraying Nozzle. ( As per Annexure "L" Drawing) | 30.52 | kWp |  | 53900.00 | 1645028.00 | 48700.00 | 1486324.00 | 39750.00 | 1213170.00 | 1213170.00 | INSTANT ELECTRIC SERVICES
| Total in Figures |  |  |  |  | 1645028.00 |  | 1486324.00 |  | 1213170.00
Lowest Amount Quoted BY: INSTANT ELECTRIC SERVICES(1213170.00)

## BOQ Summary
BOQ Summary Details Tender Title: Provision of 30.52 KW Roof Top Solar Power System at Diu airport Tender ID: 2025_AAI_241108_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | INSTANT ELECTRIC SERVICES (BID ID -882774) | 1213170.00 | L1
| 2 | Naturetech Infrastruture Pvt. Ltd. (BID ID -883230) | 1486324.00 | L2
| 3 | M/S Renesys Power Systems Private Limited (BID ID -874489) | 1645028.00 | L3