## BoQ1
Government eProcurement System Created By: Partha Saha Created Date/Time: 13-Nov-2025 04:57 PM Tender Title: SITC of High Mast works at Darbhanga Airport Tender ID: 2025_AAI_241347_1
Tender Inviting Authority: Airports Authority of India
Name of Work: SITC of High Mast (Apron Flood Light) works at Darbhanga Airport
Contract No:
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Utkarsh India Limited (GSTN-19AAACW4982C1Z6) BID ID -882443 |  | Bajaj Electricals Limited (GSTN-27AAACB2484Q1Z8) BID ID -883948 |  | elektron (GSTN-09AAFFE6230P1Z2) BID ID -884670 |  | M/S Jagdish Singh Enterprises (GSTN-NA) BID ID -884487 |  | Vishal Technopower Private Limited (GSTN-NA) BID ID -883678 |  | VL SERVICES (GSTN-NA) BID ID -874616 |  | YPR ENGINEERING AND SOLUTIONS PRIVATE LIMITED (GSTN-NA) BID ID -884053 |  | ENGINEERING SOLUTIONS (GSTN-NA) BID ID -884678 |  | waystone engicon private limited (GSTN-NA) BID ID -884632
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Design, manufacture, supply, installation, erection ,testing & commissioning of 20 meter height integral type hot dipped galvanised high mast (as per approved make list of AAI) with in built power tool suitable for wind velocity as per IS -875 , luminaries carriage suitable to install luminaries as per lighting design complying ICAO/DGCA CAR standards complete with all accessories like lightning finial , double/triple drum winch ,compensating disc, counter weight (of suitable no. LED Flood light luminiaries as approved by E-I-C) etc , head frame ,SS wire rope ,trailing cable , connectors ,mannual handle , junction box complete as required as per manufacturer design. This item also includes following: i) Necessary design & costing of suitable foundation with M25 grade concrete as per site condition or OEM recommended along with all civil materials/supplies i/c supply and erection of suitable nos of foundation bolts , anchor plates,common template, nuts wahsers etc. complete as required ii) Supply of suitable no. aesthetically designed LED Flood lights as per the lighting design approved by E-I-C to acheive minimum lux level in the apron area as per ICAO/DGCA CAR standards complete and as per techinical specifications for each high mast. iii)Supply of LED Type low intensity aviation obstruction light suitable for single phase, 230 V, 50 HZ AC supply and as per ICAO standard etc. complete as required for each high mast. iii) Installation ,testing and commisioning of all required luminaries including obstruction light as per design with switch gears, required wiring/cabling,cable connection from panel to mast top & fitting, cable connection with lantern carriage & aviation obstruction light, connection and interconnection complete as required and as per particular specificaions enclosed. | 8.00 | Job | 836693.52 | 520264.60 | 4162116.80 | 328618.00 | 2628944.00 | 591802.00 | 4734416.00 | 630000.00 | 5040000.00 | 388208.00 | 3105664.00 | 725000.00 | 5800000.00 | 620776.00 | 4966208.00 | 421800.00 | 3374400.00 | 459600.00 | 3676800.00 | 2628944.00 | Bajaj Electricals Limited
2.00 | High Mast Main Outdoor PANEL Supply, Installation, Testing and Commissioning of dust & vermin proof outdoor type, IP-54, floor mounted feeder pillar of suitable size on cement concrete foundations generally conforming to IS 5039 and to withstand rough usage and weather, with canopy, suitable for 415V+/-10%, 3 Phase, 4 wire 50 Hz AC supply system, fabricated from CRCA sheet steel of 2 mm thick for frame work and covers, 3 mm thick for gland plates, having TPN Aluminium alloy bus bars with 100% size neutral bus as that of phase bus. The panel shall be fabricated with hinged centre opening type double doors (fabricated out of 2mm CRCA sheet steel) on front side with locking arrangement, suitable angle/ channels frame in the bottom, legs for grouting in foundation, openable cable protection covers at bottom portion, painting etc, entire panel shall have a common GI earth bus bar of size as per IS 3043 subject to minimum 40mm x 5mm at the rear with 2 Nos. earth stud, solid/ flexible connections from main earth bus bar to switchgears with required size of Cooper conductors/ bus bars and control wiring with 2.5 sqmm FRLS PVC insulated copper conductor cable, cable alleys, control and interlocking of incomers, bus coupler and providing following switchgears/ accessories as per specifications. Incomer 2 Nos. 250A, 4P MCCB, Microprocessor based release (Ics = Icu = 35kA) with inbuilt O/L , S/C & E/F protection as per specification and each incommer shall be provided with following accessories. 1 Set of phase indicating LED lamps with 2 amp back up MCB. 1 No. 96 x 96 sqmm Digital MFM meter and 3 nos. Cast resin CTs of ratio 250/5A , Class 0.5 accuracy and 10 VA burden, suitable to measure voltage, Ampere, Frequency, Power Factor, KVA, KW, KVAH, KWH, MDI etc. 1 Set of ON/ OFF/TRIP Indicating LED Lamps With 2 Amp MCB for each incomer Buscoupler 1 Nos. 250A 4P MCCB, Microprocessor based release (Ics = Icu = 35kA) with inbuilt O/L , S/C & E/F protection as per specification with following accessories. 1 Set of ON/ OFF/TRIP Indicating LED Lamps With 2 Amp MCB Electrical & Mechnical Interlocking between both incomers & Buscoupler Busbars 4P aluminium bus bars of 250A capacity with heat shrinkable coloured sleeves including SMC bus bars supports at required intervals complete for cross section, size supports & their spacing etc. for withstanding fault level of 35 KA for 1 sec. Outgoings 4 Nos. 125A 4P MCCB with built in thermal magnetic release with adjustable setting (Ics = Icu = minimum 25 KA) 10Nos. 63A 4P MCCB with built in thermal magnetic release with adjustable setting (Ics = Icu = minimum 25 KA) 4 Nos. 32 A DP MCBs -C curve, 10kA For each busbar section-1 Set Surge protection device Type 2 ( Class C), 4 Module, MOV type suitable for 8/ 20µs surge,Voltage Protection level Up < 1.5kV. SPD shall be with built in fuse and plugable type. For connecting SPD minimum 10sqmm copper wire must be used. The SPD shall be complient and tested from KEMA KEUR / VDE / NABL tested as per relevant IEC. High Mast Main Outdoor PANEL as described above. | 1.00 | Job | 611121.68 | 545122.50 | 545122.50 | 665810.00 | 665810.00 | 669711.00 | 669711.00 | 450002.00 | 450002.00 | 623800.00 | 623800.00 | 850000.00 | 850000.00 | 1493849.00 | 1493849.00 | 337200.00 | 337200.00 | 180000.00 | 180000.00 | 180000.00 | waystone engicon private limited
3.00 | High Mast outdoor Feeder Pillar Panel Supply, installation, testing and commissioning of dust & vermin proof ourdoor, IP-54, floor mounted feeder pillar of suitable size on cement concrete foundations generally conforming to IS 5039 and to withstand rough usage and weather, with canopy & suitable for 415V+/-10%, 3 Phase, 4 wire 50 Hz AC supply system. The panel shall be fabricated with 14 SWG M.S.sheet with hinged door on front side with locking arrangement, suitable angle/ channels frame in the bottom, legs for grouting in foundation, openable cable protection covers at bottom portion, painting etc. including supplying and fixing of following accessories and making inter connection, earth connection, neutral link, suitable TPN Bus bars of Aluminium alloy, etc.as per the drawings. Incomer: 63 Amps.4P,MCB, C-Series, 10kA - 1 No. RYB Indicating Lamp ( LED Type) - 1 set Ammeter with selector switch and suitable CT etc. -01 set Voltmeter with selector switch - 01 set Auto Manual Switch Power Contactor of 32 Amp with necessary timer & relay for automatic switching of Luminaries. Outgoing : 40 Amps. FP, MCB, C-series 10 kA -3 No. MCBs 16A/20A, DP, 10kA, C series -3 Nos. on each phase 15 Amps Socket and switch -1 set Start & Stop Push Button for motor opeartion-1 Set 16 sq. mm & 2.5 Sqmm terminals/connectors for connecting outgoings High Mast Feeder Pillar Panel as above. | 8.00 | Job | 60996.00 | 90000.00 | 720000.00 | 68650.00 | 549200.00 | 61500.00 | 492000.00 | 45000.00 | 360000.00 | 53360.00 | 426880.00 | 38500.00 | 308000.00 | 96457.00 | 771656.00 | 45600.00 | 364800.00 | 31400.00 | 251200.00 | 251200.00 | waystone engicon private limited
4.00 | Taxilink Feeder Pillar Panel Supply, installation, testing and commissioning of dust & vermin proof ourdoor, IP-54, floor mounted feeder pillar of suitable size on cement concrete foundations generally conforming to IS 5039 and to withstand rough usage and weather, with canopy & suitable for 415V+/-10%, 3 Phase, 4 wire 50 Hz AC supply system. The panel shall be fabricated with 14 SWG M.S.sheet with hinged door on front side with locking arrangement, suitable angle/ channels frame in the bottom, legs for grouting in foundation, openable cable protection covers at bottom portion, painting etc. including supplying and fixing of following accessories and making inter connection, earth connection, neutral link, suitable TPN Bus bars of Aluminium alloy, etc.as per the drawings. Incomer: 2 Nos. 100A, 4P MCCB, Microprocessor based release (Ics = Icu = 25kA) with inbuilt O/L , S/C & E/F protection as per specification and each incommer shall be provided with following accessories. RYB Indicating Lamp ( LED Type) - 1 set Ammeter with selector switch and suitable CT etc. -01 set Voltmeter with selector switch - 01 set Auto Change Over One No. 100A, 4 Pole,415V,3 phase,50 Hz Auto Change Over System with Bypass mechanism, within the panel All accessories, wiring etc requried for proper interlocking of incommers and autochange over system OUTGOING 03 Nos 63 AMP 4 pole MCCB(Ics=100%Icu=25 KA) with Thermal magnetic release Extended Rotary operating Mechanism 04Nos-16A DP MCB,C curve UPS COMPARTMENT A separate compartment for UPS shall be provided with following : 1KVA single phase UPS ( with suitable battery of minimum 30min backup ) with provision of 4 Nos. 16A DP MCB,C curve UPS output | 2.00 | Job | 520000.00 | 308272.90 | 616545.80 | 427160.00 | 854320.00 | 344559.00 | 689118.00 | 225000.00 | 450000.00 | 289000.00 | 578000.00 | 625000.00 | 1250000.00 | 420067.00 | 840134.00 | 267600.00 | 535200.00 | 169000.00 | 338000.00 | 338000.00 | waystone engicon private limited
5.00 | Supplying of 1100V grade Aluminium Conductor XLPE insulated galvanised steel strip armoured & overall PVC sheathed armoured power cables as per IS: 7098 Part-I complete as required. 3.5C X 185 Sq.mm | 700.00 | Mtr. | 1853.28 | 1548.96 | 1084272.00 | 1010.00 | 707000.00 | 911.00 | 637700.00 | 1450.00 | 1015000.00 | 1040.38 | 728266.00 | 1250.00 | 875000.00 | 970.00 | 679000.00 | 840.00 | 588000.00 | 830.00 | 581000.00 | 581000.00 | waystone engicon private limited
6.00 | Supplying of 1100V grade Aluminium Conductor XLPE insulated galvanised steel strip armoured & overall PVC sheathed armoured power cables as per IS: 7098 Part-I complete as required. 4C X 25 Sq.mm | 1200.00 | Mtr. | 376.48 | 316.80 | 380160.00 | 207.00 | 248400.00 | 214.00 | 256800.00 | 310.00 | 372000.00 | 212.78 | 255336.00 | 335.00 | 402000.00 | 200.00 | 240000.00 | 234.00 | 280800.00 | 175.00 | 210000.00 | 210000.00 | waystone engicon private limited
7.00 | Supply of 3C x 4 Sq. mm.size 1.1 KV grade XLPE insulated, PVC sheathed, armoured Copper conductor power cable conforming to IS 7098 as amended upto date. | 700.00 | Mtr. | 343.20 | 325.62 | 227934.00 | 197.00 | 137900.00 | 396.00 | 277200.00 | 230.00 | 161000.00 | 194.41 | 136087.00 | 225.00 | 157500.00 | 191.00 | 133700.00 | 309.00 | 216300.00 | 175.00 | 122500.00 | 122500.00 | waystone engicon private limited
8.00 | Supply of 90 mm dia OD ISI marked HDPE pipe as per IS:4984:2016, of rating PE 100, PN 8 complete as required | 600.00 | Mtr. | 266.24 | 206.40 | 123840.00 | 226.00 | 135600.00 | 203.00 | 121800.00 | 700.00 | 420000.00 | 210.80 | 126480.00 | 225.00 | 135000.00 | 195.00 | 117000.00 | 144.00 | 86400.00 | 290.00 | 174000.00 | 86400.00 | ENGINEERING SOLUTIONS
9.00 | Supply of 50 mm dia OD ISI marked HDPE pipe as per IS:4984:2016, of rating PE 100, PN 8 complete as required | 1150.00 | Mtr. | 90.48 | 68.40 | 78660.00 | 87.00 | 100050.00 | 83.00 | 95450.00 | 500.00 | 575000.00 | 74.40 | 85560.00 | 185.00 | 212750.00 | 74.00 | 85100.00 | 104.00 | 119600.00 | 68.00 | 78200.00 | 78200.00 | waystone engicon private limited
10.00 | Laying of upto 90 mm dia HDPE/MS Pipe direct in underground at depth of 75 cm below ground level including soil excavation and refilling the trench etc. as required. | 550.00 | Mtr. | 122.72 | 90.00 | 49500.00 | 130.00 | 71500.00 | 110.00 | 60500.00 | 350.00 | 192500.00 | 100.00 | 55000.00 | 250.00 | 137500.00 | 72.00 | 39600.00 | 132.00 | 72600.00 | 30.00 | 16500.00 | 16500.00 | waystone engicon private limited
11.00 | Laying of additional upto 90 mm dia HDPE/MS Pipe direct in underground in the same trench in one tier horizontal formation at depth of 75 cm below ground level including soil excavation and refilling the trench etc. as required. | 500.00 | Mtr. | 57.20 | 90.00 | 45000.00 | 52.00 | 26000.00 | 110.00 | 55000.00 | 250.00 | 125000.00 | 90.00 | 45000.00 | 180.00 | 90000.00 | 543.00 | 271500.00 | 108.00 | 54000.00 | 30.00 | 15000.00 | 15000.00 | waystone engicon private limited
12.00 | Earthing with GI earth plate 600mm x 600mm x 6.0mm thick including accessories and providing masonary enclosure with cover plate having locking arrangement and watering pipe etc. Including charcoal and salt complete as required. | 22.00 | Set | 8490.56 | 11056.80 | 243249.60 | 15671.00 | 344762.00 | 14300.00 | 314600.00 | 8000.00 | 176000.00 | 15000.00 | 330000.00 | 18500.00 | 407000.00 | 10626.00 | 233772.00 | 17160.00 | 377520.00 | 5000.00 | 110000.00 | 110000.00 | waystone engicon private limited
13.00 | Providing and fixing 25mm x 5 mm G.I. strip in 40mm dia G.I. pipe from earth electrode including connection with G.I. nut, bolt, spring, washer excavation and re-filling etc. as required. | 110.00 | Mtr. | 719.68 | 1638.00 | 180180.00 | 228.00 | 25080.00 | 176.00 | 19360.00 | 250.00 | 27500.00 | 160.05 | 17605.50 | 190.00 | 20900.00 | 405.00 | 44550.00 | 132.00 | 14520.00 | 200.00 | 22000.00 | 14520.00 | ENGINEERING SOLUTIONS
14.00 | Providing and fixing 25mm x 5mm G.I. strip on surface/in recess/existing pipes etc. for connections etc. as required. | 440.00 | Mtr. | 226.72 | 202.80 | 89232.00 | 228.00 | 100320.00 | 176.00 | 77440.00 | 360.00 | 158400.00 | 160.05 | 70422.00 | 235.00 | 103400.00 | 127.00 | 55880.00 | 132.00 | 58080.00 | 100.00 | 44000.00 | 44000.00 | waystone engicon private limited
15.00 | Laying of one number PVC insulated & PVC sheathed XLPE power cable of 1.1 KV grade of following size in the existing masonary open duct/surface/pipe/raceway as per specification as required a) upto 35 sqmm | 1200.00 | Mtr. | 29.12 | 66.00 | 79200.00 | 65.00 | 78000.00 | 27.00 | 32400.00 | 250.00 | 300000.00 | 50.00 | 60000.00 | 65.00 | 78000.00 | 24.00 | 28800.00 | 66.00 | 79200.00 | 50.00 | 60000.00 | 28800.00 | YPR ENGINEERING AND SOLUTIONS PRIVATE LIMITED
16.00 | Laying of one number PVC insulated & PVC sheathed XLPE power cable of 1.1 KV grade of following size in the existing masonary open duct/surface/pipe/raceway as per specification as required a) Above 95 sqmm and upto 185 sqmm | 600.00 | Mtr. | 50.96 | 108.00 | 64800.00 | 111.00 | 66600.00 | 99.00 | 59400.00 | 350.00 | 210000.00 | 120.00 | 72000.00 | 72.00 | 43200.00 | 109.00 | 65400.00 | 132.00 | 79200.00 | 50.00 | 30000.00 | 30000.00 | waystone engicon private limited
17.00 | Supplying and installing following size of perforated Hot dipped G.I. cable trays with perforation not more than 17.5%, in convienient sections, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc. as required. a) 150 mm width X 50 mm depth X 1.6 mm thickness | 100.00 | Mtr | 604.24 | 583.20 | 58320.00 | 1228.00 | 122800.00 | 605.00 | 60500.00 | 600.00 | 60000.00 | 584.00 | 58400.00 | 350.00 | 35000.00 | 568.00 | 56800.00 | 145.00 | 14500.00 | 200.00 | 20000.00 | 14500.00 | ENGINEERING SOLUTIONS
18.00 | Laying and fixing of one no. PVC insulated and PVC Sheathed/XLPE Power cable of 1.1 KV grade of following sizes on the existing cable tray as required a) Above 95 sqmm and upto 185 sqmm | 100.00 | Mtr | 125.84 | 108.00 | 10800.00 | 124.00 | 12400.00 | 99.00 | 9900.00 | 100.00 | 10000.00 | 120.00 | 12000.00 | 60.00 | 6000.00 | 109.00 | 10900.00 | 108.00 | 10800.00 | 100.00 | 10000.00 | 6000.00 | VL SERVICES
19.00 | Supplying and making end termination with brass compression gland and Aluminimum lugs for following size of PVC insulated and PVC sheathed / XLPE Aluminium conductor cable of 1.1 KV grade as required. a) 3.5 X 185 Sq.mm | 4.00 | Set | 837.20 | 1140.00 | 4560.00 | 2347.00 | 9388.00 | 2860.00 | 11440.00 | 5000.00 | 20000.00 | 2000.00 | 8000.00 | 1250.00 | 5000.00 | 845.00 | 3380.00 | 540.00 | 2160.00 | 80.00 | 320.00 | 320.00 | waystone engicon private limited
20.00 | Supplying and making end termination with brass compression gland and aluminium lugs for size 4C x 25 sqmm of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required : | 30.00 | Set | 291.20 | 780.00 | 23400.00 | 913.00 | 27390.00 | 810.00 | 24300.00 | 4500.00 | 135000.00 | 350.00 | 10500.00 | 650.00 | 19500.00 | 459.00 | 13770.00 | 420.00 | 12600.00 | 100.00 | 3000.00 | 3000.00 | waystone engicon private limited
21.00 | Supplying and making end termination with brass compression gland and Copper lugs for following size of PVC insulated and PVC sheathed / XLPE Copper conductor cable of 1.1 KV grade as required. 3C x 4 Sq. mm. | 16.00 | Set | 256.88 | 540.00 | 8640.00 | 522.00 | 8352.00 | 303.00 | 4848.00 | 3500.00 | 56000.00 | 250.00 | 4000.00 | 450.00 | 7200.00 | 441.00 | 7056.00 | 350.00 | 5600.00 | 90.00 | 1440.00 | 1440.00 | waystone engicon private limited
| Total in Figures |  |  |  |  | 8795532.70 |  | 6919816.00 |  | 8703883.00 |  | 10313402.00 |  | 6809000.50 |  | 10942950.00 |  | 10158055.00 |  | 6683480.00 |  | 5943960.00
Lowest Amount Quoted BY: waystone engicon private limited(5943960.00)

## BOQ Summary
BOQ Summary Details Tender Title: SITC of High Mast works at Darbhanga Airport Tender ID: 2025_AAI_241347_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | waystone engicon private limited (BID ID -884632) | 5943960.00 | L1
| 2 | ENGINEERING SOLUTIONS (BID ID -884678) | 6683480.00 | L2
| 3 | Vishal Technopower Private Limited (BID ID -883678) | 6809000.50 | L3
| 4 | Bajaj Electricals Limited (BID ID -883948) | 6919816.00 | L4
| 5 | elektron (BID ID -884670) | 8703883.00 | L5
| 6 | Utkarsh India Limited (BID ID -882443) | 8795532.70 | L6
| 7 | YPR ENGINEERING AND SOLUTIONS PRIVATE LIMITED (BID ID -884053) | 10158055.00 | L7
| 8 | M/S Jagdish Singh Enterprises (BID ID -884487) | 10313402.00 | L8
| 9 | VL SERVICES (BID ID -874616) | 10942950.00 | L9