## BoQ1
Government eProcurement System Created By: M Vargees Created Date/Time: 01-Sep-2025 03:19 PM Tender Title: SITC of 60kVA UPS for Aeronautical Ground Lighting System at Agatti Airport Tender ID: 2025_AAI_241402_1
Tender Inviting Authority: The Senior Manager(Engg-E), AAI, Agatti Airport.
Name of Work : SITC of 60kVA UPS for Aeronautical Ground Lighting System at Agatti Airport
Contract No: 2025_AAI_ 241402_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | SUN POWER CONVERSION PVT LTD (GSTN-09AAICS9074K1ZL) BID ID -882412 |  | Virtus Techno (GSTN-NA) BID ID -886191
[5 empty] | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply , Installation , Testing and commissioning of 60 KVA capacity online UPS 3 phase input / 3 phase output side with double conversion PWM IGBT technology to drive constant current regulators & suitable for 100% unbalanced load at various load inclluding full load condition as per technical specifications. The UPS shall have built in isolation transformer at input side , automatic static by pass, active input powerfactor correction, phase sequence corrector, pure sine wave output, input - output isolation , compatibility with generator supply , cold start capability , EMI/RFI noise filter , advanced communication port and user friendly LCD display with necessary safety protections , THDi<=5% including transportation , loading unloading etc complete as required. | 1.00 | Job |  | 690000.00 | 690000.00 | 525375.00 | 525375.00 | 525375.00 | Virtus Techno
2.00 | Supply Installation and testing and commissioning of SMF battery C20 rated for minimum 30 min backup at 60kVA unit pf (Batter bank shall be of 57600 VAH -12V 150 Ah x 32 nos). The job also includes supply and fixing of suitable MS battery rack along with interconnection cables for batteries , suitable capacity power cable interconnections between UPS and Battery Rack etc complete as required. (Note: The battery shall be having 3 yrs OEM Warranty) | 1.00 | Job |  | 600000.00 | 600000.00 | 698227.50 | 698227.50 | 600000.00 | SUN POWER CONVERSION PVT LTD
3.00 | Supply, installation, testing, and commissioning of a factory-fabricated 8-way Sub-Main Distribution Board (SMDB) of 250A rating, suitable for 415V, 3-phase, 4-wire system, with short circuit withstand capacity of 36kA for 1 second, IP43 protection, and aluminum busbar system. The panel shall be equipped with 1 No. 160A 3P MCCB as incomer and 8 Nos. 3P MCCBs as outgoing feeders (40A - 03 Nos,63A - 03 Nos, 100A - 02 Nos), enclosed in CRCA steel powder-coated cabinet with Metering Box on Top and bottom cable entry provisions, earth and neutral bars, internal wiring, phase indication lamps, identification labels, and shall be suitable for wall mounting. The SMDB shall conform to IEC 61439-2 / IS 8623 standards and shall be supplied complete with all necessary accessories, cable terminations, earthing connections, transportation, loading and unloading, installation, testing, and commissioning as required. | 1.00 | Job |  | 175000.00 | 175000.00 | 212500.00 | 212500.00 | 175000.00 | SUN POWER CONVERSION PVT LTD
4.00 | Earthing with copper earth plate 600 mm x 600 mm x 3 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 meter long etc. with charcoal/ coke and salt as required | 2.00 | Set |  | 30000.00 | 60000.00 | 23625.00 | 47250.00 | 47250.00 | Virtus Techno
5.00 | All Inclusive Comprehensive maintenance contract of 60kVA UPS, Battery and all electrical equipments installed under this contract including supply and replacement of spares , carrying preventive maintenance once in 03 months as per the manufacturers recommendations and carrying breakdown maintenance etc. complete as required as per the special conditions of the contract on expiry of the Defects Liability Period of 2 Years (1 Job / annum = CMC of 1 UPS for 1 year) Note: The replacement of battery is excluded from scope of CMC after completion of warrenty period of battery
5.01 | First Year after DLP of Two Years | 1.00 | Job/ Annum |  | 129000.00 | 129000.00 | 122360.25 | 122360.25 | 122360.25 | Virtus Techno
5.02 | Second Year after DLP of Two Years | 1.00 | Job/ Annum |  | 141900.00 | 141900.00 | 134596.28 | 134596.28 | 134596.28 | Virtus Techno
5.03 | Third Year after DLP of Two Years | 1.00 | Job/ Annum |  | 156090.00 | 156090.00 | 148055.90 | 148055.90 | 148055.90 | Virtus Techno
5.04 | Fourth Year after DLP of Two Years | 1.00 | Job/ Annum |  | 171699.00 | 171699.00 | 162861.49 | 162861.49 | 162861.49 | Virtus Techno
5.05 | Fifth Year after DLP of Two Years | 1.00 | Job/ Annum |  | 188856.00 | 188856.00 | 179135.41 | 179135.41 | 179135.41 | Virtus Techno
| Total in Figures |  |  |  |  | 2312545.00 |  | 2230361.83
Lowest Amount Quoted BY: Virtus Techno(2230361.83)

## BOQ Summary
BOQ Summary Details Tender Title: SITC of 60kVA UPS for Aeronautical Ground Lighting System at Agatti Airport Tender ID: 2025_AAI_241402_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Virtus Techno (BID ID -886191) | 2230361.83 | L1
| 2 | SUN POWER CONVERSION PVT LTD (BID ID -882412) | 2312545.00 | L2