## BoQ1
Government eProcurement System Created By: Gajraj Singh Bhati Created Date/Time: 29-Aug-2025 03:46 PM Tender Title: Provision of replacement of existing signages in operational area and additional signages at Dimapur Airport Tender ID: 2025_AAI_241783_1
Tender Inviting Authority: AGM(E-E) AAI, Dimapur Airport.
Name of Work: Provision of replacement of existing signages in operational area and additional signages at Dimapur Airport.
Contract No: 2025_AAI_241783_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | POSHDECOR (GSTN-27ABDFP5348N1ZO) BID ID -879388 |  | CREATIVE TRADING CO (GSTN-07AMEPK8023F1Z9) BID ID -882454 |  | NASU SYSTEMS (GSTN-27ABAPS2566G1ZK) BID ID -882762 |  | REWINDER TECHNO ELECTRICALS (GSTN-18AAFFR7457K1ZL) BID ID -883000 |  | GARIMA SALES CORPORATION (GSTN-NA) BID ID -881838 |  | Airfield Solutions India pvt Ltd (GSTN-NA) BID ID -879082
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply of LED Type Guidance Sign Board of various sizes made out of anodized 2 mm thick Aluminium frame with suitable angle support and 1.5 mm thick al. backcover, 4 mm thick polycarbonate sheet with glare free front face, the letter & symbol should be screen printed / on inside face with required colouring, suitable arrangement shall be made for water tighness & locking arrangement, including supporting frangible legs & frame etc., signboard shall be uniformly inernally illuminated with required numbers of LED lights to achieve illumination level and can operate on series circuit without flickering, complete as required and as specified in ICAO Annex. 14 Vol. I (legends as approved by Engineer-in-Charge). | 30.00 | Sqmtr |  | 33000.00 | 990000.00 | 44500.00 | 1335000.00 | 39000.00 | 1170000.00 | 36000.00 | 1080000.00 | 27000.00 | 810000.00 | 27390.00 | 821700.00 | 810000.00 | GARIMA SALES CORPORATION
2.00 | Installation, testing and commissioning of operational guidance /mandatory signages of various sizes at various location at operational area of Airport. The signages should be installed in 1:2:4 grade cement concrete of 400X400X500mm (for legs) and a total base of 150mm thick which extends all around the board with the distance of 1500mm (front, back and both sides). The concrete base and leg foundation should be on the same level and 20-25mm above the ground level etc., complete as required as per the Annexure 14. | 50.00 | Sqmtr |  | 4500.00 | 225000.00 | 8000.00 | 400000.00 | 5000.00 | 250000.00 | 5500.00 | 275000.00 | 14400.00 | 720000.00 | 11000.00 | 550000.00 | 225000.00 | POSHDECOR
3.00 | SITC of Triangular SNI (Stand Number Indicator) boards (Fascia 800 x600 x 2) to indicate Aircraft parking stand in Apron, fabricated with 2mm Aluminium Sheet. The SNI shall be triangular in shape with rear side of 1700 mm and each front side of 1000 mm. The total height of triangle shall be 900 mm. There shall be laser cut opening of 800 X 600 mm of front fascia for indicating SNI. The long-life facia shall be UV stabilized polycarbonate face sheet of 4mm thickness with special adhesive and vinyl pasting from inside of polycarbonate face fixed from inside of fascia with changing arrangement from inside. The boards shall be internally & uniformly illuminated with LED lamp (modules) and all other accessories including having individual LED drivers to work on 230V AC supply complete with all internal wirings, connectors. The top cover shall be of single piece 2mm Al sheet which shall cover the entire triangle with edge bent up to 15mm on all side to prevent ingress of water and shall be openable for maintenance of board. The board shall be in grey colour or any other colour as decided by EIC. Note: The signage matter will be provided by AAI. | 4.00 | Job |  | 42000.00 | 168000.00 | 50000.00 | 200000.00 | 60000.00 | 240000.00 | 48000.00 | 192000.00 | 36000.00 | 144000.00 | 57200.00 | 228800.00 | 144000.00 | GARIMA SALES CORPORATION
4.00 | Supply of WGS 84 (World Geodetic System) in Apron, fabricated with central split type opening for easy maintenance made of reinforced 2mm thick anodized aluminum profile with suitable support. The rear panel shall be made of 1.2 mm with ready to install fitting for mounting on pole or façade. The long-life facia shall be UV stabilized polycarbonate face sheet of 4mm thickness with special adhesive and vinyl pasting from inside of polycarbonate face fixed from inside of fascia with changing arrangement from inside. The board shall have hinged front face to allow easy access for maintenance. Light distributionshall be made even provided with LED array. The boards shall be internally uniformly illuminated with LED lamp(modules) and all other accessories including having individual LED drivers to work on 230V AC supply complete with all internal wirings, connectors. The board shall be in grey colour or any other colour as decided by EIC. | 4.00 | Job |  | 21000.00 | 84000.00 | 35000.00 | 140000.00 | 35000.00 | 140000.00 | 40000.00 | 160000.00 | 9000.00 | 36000.00 | 34100.00 | 136400.00 | 36000.00 | GARIMA SALES CORPORATION
5.00 | Supply of 4.5 Mtr height Stepped MS Pole fabricated from MS Pipes of sizes 200mm dia x 5 mm thick upto 1.5 Mtrs from Bottom, 140 mm dia x 5 mm thick from 1.5 Mtr to 4.5 Mtr with 1 Mtr inside overlap in the 200 mm dia pipe with Stepped Flange including providing suitable sized base plate for erection, including supply of suitable sized foundation Bolt. The Pole shall be painted in desired grey color or any other colour approved by EIC. | 4.00 | Job |  | 54000.00 | 216000.00 | 10499.00 | 41996.00 | 10015.00 | 40060.00 | 15000.00 | 60000.00 | 18000.00 | 72000.00 | 19800.00 | 79200.00 | 40060.00 | NASU SYSTEMS
6.00 | Supply of Cast iron Isolating Transformer housing box, water tight round type, metal container of outside dia 330 mm, height 450 mm made of 10 mm thick cast iron moulding all round, except the top surface, which is 15 mm thick cast iron moulding suitable to receive a light fitting base plate/cover plate on the top and underground housing associated with transformer power cable and having three/two/one nos holes as per site requirement on the periphery centre, 75 mm above bottom surface suitable to receive 50 mm HDPE pipes as required . The box should have two SS earth bolts of M10 x 40 mm tapped inside near the hole (4" away from the hole centre) and having a drain hole at the bottom suitably tapped to receive 15 mm dia, 'B' class GI pipe and having clear opening of 220 mm at the top surface and 6 Nos. M10 tapped hole having centre to center distance of 260 mm alongwith bolts as required as per the drawings. The CI top cover of 310 mm dia x 15 mm thick with suitable rubber gasket and 6 Nos. M10 tapped hole and bolts as required. | 14.00 | Each |  | 5400.00 | 75600.00 | 6800.00 | 95200.00 | 6500.00 | 91000.00 | 6500.00 | 91000.00 | 9000.00 | 126000.00 | 6160.00 | 86240.00 | 75600.00 | POSHDECOR
7.00 | Installation of round type transformer housing box with base concrete of 1:3:6 of size 630 x 630 x 100 mm thick all around concrete of 1:2:4, 150 mm thick top slopped with 1:2:4 cement concrete including providing and fixing 10" long 1/2" dia B class GI pipe with check nuts for drainage of water including excavation and refilling, aligning the boxes in straight line etc complete as required. | 14.00 | Each |  | 2700.00 | 37800.00 | 2800.00 | 39200.00 | 4000.00 | 56000.00 | 2000.00 | 28000.00 | 6300.00 | 88200.00 | 10780.00 | 150920.00 | 28000.00 | REWINDER TECHNO ELECTRICALS
8.00 | Laying of DWC HDPE pipe up to 50 mm size complete with fitting and cutting, jointing etc.direct in ground (80 cm below ground level) including excavation and refilling the trench but excluding sand cushioning and protective covering etc. , complete as required. | 200.00 | mtr |  | 150.00 | 30000.00 | 190.00 | 38000.00 | 50.00 | 10000.00 | 100.00 | 20000.00 | 135.00 | 27000.00 | 214.50 | 42900.00 | 10000.00 | NASU SYSTEMS
9.00 | Laying of one number PVC insulated and PVC sheathed/ XLPE power cable of 5 KV/1.1KV grade of upto 35 sq.mm in the existing RCC/HUME/STONE WARE/METAL/DWC-HDPE pipe as required. | 150.00 | mtr |  | 39.00 | 5850.00 | 30.00 | 4500.00 | 50.00 | 7500.00 | 20.00 | 3000.00 | 135.00 | 20250.00 | 66.00 | 9900.00 | 3000.00 | REWINDER TECHNO ELECTRICALS
10.00 | Laying of one number XLPE armoured power cable of 1.1 KV grade of following size in the existing RCC/HUME/METAL pipe as required:upto 35 sq. mm | 150.00 | Mtr |  | 45.00 | 6750.00 | 40.00 | 6000.00 | 50.00 | 7500.00 | 20.00 | 3000.00 | 135.00 | 20250.00 | 66.00 | 9900.00 | 3000.00 | REWINDER TECHNO ELECTRICALS
11.00 | Making field connections by crimping of 6/16 sq.mm plug & receptacle with suitable existing size single core PVC cu. Conductor cable of 5 KV grade Airfield cable including filling the gap with water sealant material applying PVC insulation tape etc. complete as required | 14.00 | Each |  | 90.00 | 1260.00 | 190.00 | 2660.00 | 500.00 | 7000.00 | 100.00 | 1400.00 | 5400.00 | 75600.00 | 330.00 | 4620.00 | 1260.00 | POSHDECOR
| Total in Figures |  |  |  |  | 1840260.00 |  | 2302556.00 |  | 2019060.00 |  | 1913400.00 |  | 2139300.00 |  | 2120580.00
Lowest Amount Quoted BY: POSHDECOR(1840260.00)

## BOQ Summary
BOQ Summary Details Tender Title: Provision of replacement of existing signages in operational area and additional signages at Dimapur Airport Tender ID: 2025_AAI_241783_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | POSHDECOR (BID ID -879388) | 1840260.00 | L1
| 2 | REWINDER TECHNO ELECTRICALS (BID ID -883000) | 1913400.00 | L2
| 3 | NASU SYSTEMS (BID ID -882762) | 2019060.00 | L3
| 4 | Airfield Solutions India pvt Ltd (BID ID -879082) | 2120580.00 | L4
| 5 | GARIMA SALES CORPORATION (BID ID -881838) | 2139300.00 | L5
| 6 | CREATIVE TRADING CO (BID ID -882454) | 2302556.00 | L6