## BoQ1
Government eProcurement System Created By: ARUN KUMAR K Created Date/Time: 17-Sep-2025 06:22 PM Tender Title: Design, Supply, Installation, Testing and Commissioning of Gas based Fire Suppression System for NAV- AIDS and other Installations at KIA, Bengaluru. Tender ID: 2025_AAI_242346_1
Tender Inviting Authority: Asst.General Manager (Engg. – Electrical), AAI, ATS Complex, Alpha-1, Kempegowda International Airport, Bengaluru
Name of work : Design, Supply, Installation, Testing and Commissioning of Gas based Fire Suppression System for NAV- AIDS and other Installations at KIA, Bengaluru.
Contract No: 2025_AAI_242346_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Nexus Fire And Security Systems (GSTN-07AAKFN7125K1ZY) BID ID -878895 |  | advent electric technologies pvt. ltd. (GSTN-07AAJCA2055K1ZN) BID ID -879241 |  | CENTRE TAP ENGINEERING (GSTN-24AGPPP8172K1ZP) BID ID -888959 |  | Kalpataru Industries (GSTN-NA) BID ID -878856 |  | Swastik Synergy Engineering Pvt. Ltd (GSTN-NA) BID ID -888383
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Design, Supply, Installation, Testing and Commissioning of Gas based Fire Suppression System for the following locations consisting of PESO Approved Cylinder and valve assembly, extinguishing agent, arrangement for supervisory switch connection for monitoring cylinder pressure, pressure guage with a safety burst disc, electronic control head / Solenoid with provision for manual operation, flexible hose, cylinder strap, NRV (if applicable), Pressure Switch and safety cap, required nos. of Discharge Nozzles, Piping, Manifold, Fire Alarm cum Gas Release Panel with required nos of smoke detectors, Strobe cum hooters, RI etc, Autodialler (Landline compatable), Manual gas release and abort station (Pull type) with weather proof enclosure, FRLS armoured copper cabling and all required modules/accessories etc. complete as required as per technical specifications. Note : (1) The system shall have PESO / BIS / UL / VDS certified technology that allows for a higher capacity to overcome frictional losses and allow for higher distances of the agent flow; and also allow for better agent penetration in enclosed electronic equipment such as Server Racks etc. (2) Extinguishing Agent : CLEAN AGENT (FK-5-1-12) shall be Colourless and odour less gas gaving Zero Ozone Depletion Potential (ODP). The Quantity of Clean agent shall be determined based on the given room volume and as per relevant certification. Fill Density certificate shall be submitted from PESO approved filling station. (3) Complete system design i/c preparation of shop drawings, submission of technical details of all components, selection of Cylinder capacity, Gas Volume, discharge valves, Nos. of Nozzles, piping design and pressure calculations using certified design software. The final design shall be duly vetted by the manufacturer (OEM) and submitted to the Engineer-in-Charge for approval before the commencement of work.
1.01 | Localizer Hut-27L (South Runway) Note :- (1) Room No. 1 :- Equipment Room (LxWxH) : 5.50m X 3.50m X 3.30m (Avg. H) = 63.53 m3 & Room No. 2 :- Battery Room (LxWxH) : 4.00m X 2.00m X 3.30m (Avg. H) = 26.40 m3 (2) Independent fire suppression system shall be provided for each rooms. (3) Room volume subject to tolerance of ±10% | 1.00 | SET |  | 425834.00 | 425834.00 | 446480.00 | 446480.00 | 600000.00 | 600000.00 | 487790.00 | 487790.00 | 632056.00 | 632056.00 | 425834.00 | Nexus Fire And Security Systems
1.02 | Localizer Hut-09R (South Runway) Note :- (1) Room No. 1 :- Equipment Room (LxWxH) : 5.50m X 3.50m X 3.30m (Avg. H) = 63.53 m3 & Room No. 2 :- Battery Room (LxWxH) : 4.00m X 2.00m X 3.30m (Avg. H) = 26.40 m3 (2) Independent fire suppression system shall be provided for each room. (3) Room volume subject to tolerance of ±10% | 1.00 | SET |  | 425834.00 | 425834.00 | 446480.00 | 446480.00 | 600000.00 | 600000.00 | 487790.00 | 487790.00 | 632056.00 | 632056.00 | 425834.00 | Nexus Fire And Security Systems
1.03 | Glide Path Hut-27L (South Runway) Note:- (1) Room No. 1 :- Equipment Room (LXWXH) : 4.00m X 3.50m X 3.30m (Avg. H) = 46.20 m3 & Room No. 2 :- Battery Room (LXWXH) : 2.72m X 3.50m X 3.30m (Avg. H) = 31.42 m3 (2) Independent fire suppression system shall be provided for each room. (3) Room volume subject to tolerance of ±10% | 1.00 | SET |  | 385300.00 | 385300.00 | 407890.00 | 407890.00 | 600000.00 | 600000.00 | 463275.00 | 463275.00 | 605570.00 | 605570.00 | 385300.00 | Nexus Fire And Security Systems
1.04 | Glide Path Hut-09R (South Runway) Note:- (1) Room No. 1 :- Equipment Room (LXWXH) : 4.00m X 3.50m X 3.30m (Avg. H) = 46.20 m3 & Room No. 2 :- Battery Room (LXWXH) : 2.72m X 3.50m X 3.30m (Avg. H) = 31.42 m3 (2) Independent fire suppression system shall be provided for each room. (3) Room volume subject to tolerance of ±10% | 1.00 | SET |  | 385300.00 | 385300.00 | 407890.00 | 407890.00 | 500000.00 | 500000.00 | 463275.00 | 463275.00 | 603520.00 | 603520.00 | 385300.00 | Nexus Fire And Security Systems
1.05 | Localizer Hut-27R (North Runway) Note :- (1) Room No. 1 :- Equipment Room (LXWXH) : 5.00m X 4.04m X 3.25m (Avg. H) = 65.65 m3 & Room No. 2 :- Battery Room (LXWXH) : 5m X 3.76m X 3.25m (Avg. H) = 61.1 m3 (2) Independent fire suppression system shall be provided for each room. (3) Room volume subject to tolerance of ±10% | 1.00 | SET |  | 493068.00 | 493068.00 | 560270.00 | 560270.00 | 500000.00 | 500000.00 | 539555.00 | 539555.00 | 689866.00 | 689866.00 | 493068.00 | Nexus Fire And Security Systems
1.06 | Localizer Hut-09L (North Runway) Note :- (1) Room No. 1 :- Equipment Room (LXWXH) : 5.00m X 4.04m X 3.25m (Avg. H) = 65.65 m3 & Room No. 2 :- Battery Room (LXWXH) : 5m X 3.76m X 3.25m (Avg. H) = 61.1 m3 (2) Independent fire suppression system shall be provided for each room. (3) Room volume subject to tolerance of ±10% | 1.00 | SET |  | 493068.00 | 493068.00 | 560270.00 | 560270.00 | 500000.00 | 500000.00 | 539555.00 | 539555.00 | 689866.00 | 689866.00 | 493068.00 | Nexus Fire And Security Systems
1.07 | Glidepath Hut-27R (North Runway) Note :- (1) Room No. 1 :- Equipment Room (LXWXH) : 5.00m X 4.04m X 3.25m (Avg. H) = 65.65 m3 & Room No. 2 :- Battery Room (LXWXH) : 5m X 3.76m X 3.25m (Avg. H) = 61.1 m3 (2) Independent fire suppression system shall be provided for each room. (3) Room volume subject to tolerance of ±10% | 1.00 | SET |  | 493068.00 | 493068.00 | 555470.00 | 555470.00 | 500000.00 | 500000.00 | 539555.00 | 539555.00 | 689866.00 | 689866.00 | 493068.00 | Nexus Fire And Security Systems
1.08 | Glidepath Hut-09L (North Runway) Note :- (1) Room No. 1 :- Equipment Room (LXWXH) : 5.00m X 4.04m X 3.25m (Avg. H) = 65.65 m3 & Room No. 2 :- Battery Room (LXWXH) : 5m X 3.76m X 3.25m (Avg. H) = 61.1 m3 (2) Independent fire suppression system shall be provided for each room. (3) Room volume subject to tolerance of ±10% | 1.00 | SET |  | 493068.00 | 493068.00 | 555470.00 | 555470.00 | 500000.00 | 500000.00 | 539555.00 | 539555.00 | 689866.00 | 689866.00 | 493068.00 | Nexus Fire And Security Systems
1.09 | DVOR Building (North Runway) Note :- (1) Room No. 1 :- Equipment Room (LXWXH*) : 5.00m X 4.00m X 3.40m = 68.00 m3 & Room No. 2 :- Battery Room (LXWXH*) : 2.25m X 3.00m X 3.40m = 22.95 m3 (2) Independent fire suppression system shall be provided for each room. (3) Room volume subject to tolerance of ±10% (4) *The given room height includes a 0.30 m high false ceiling void, which shall also be covered under fire protection. | 1.00 | SET |  | 424134.00 | 424134.00 | 496600.00 | 496600.00 | 500000.00 | 500000.00 | 508905.00 | 508905.00 | 642388.00 | 642388.00 | 424134.00 | Nexus Fire And Security Systems
1.10 | Fall back Server Room (Alpha-1 Building) Note :- (1) Room Dimensions (LXWXH)* :- 8.10m X 7.70m X 4.20m = 244.48 m3** (** After excluding Entrance lobby area of 2.60m (L) x 1.60m (W) x 4.20m (H) = 17.47 m3 from protection zone). (2) Room volume subject to tolerance of ±10% (3) * The given room height includes a 1.35 m high false ceiling void and 0.35m false floor void, which shall also be covered under fire protection. | 1.00 | SET |  | 489918.00 | 489918.00 | 651250.00 | 651250.00 | 500000.00 | 500000.00 | 771088.00 | 771088.00 | 843534.00 | 843534.00 | 489918.00 | Nexus Fire And Security Systems
1.11 | Fall Back UPS and Battery Room (Alpha-1 Building) Note :- (1) Room Dimensions (LXWXH)* :- 7.70 m X 7.60 m X 4.20 m* = 221.97** (* After excluding Entrance lobby area of 1.80m (L) x 3.15 m (W) x 4.20 m (H) = 23.81 m3 from protection zone). (2) Room volume subject to tolerance of ±10% (3) * The given room height includes a 1.40 m high false ceiling void, which shall also be covered under fire protection. | 1.00 | SET |  | 465418.00 | 465418.00 | 628980.00 | 628980.00 | 500000.00 | 500000.00 | 694028.00 | 694028.00 | 843534.00 | 843534.00 | 465418.00 | Nexus Fire And Security Systems
2.00 | Design, Supply, Installation, Testing and Commissioning of Automatic heat detection Tube Gas Fire Suppression System for Electrical Panels consisting of PESO approved storage cylinders with steel mounting bracket, extinguishing agent, heat sensitive detection tube and cylinder valve, associated accessories such as pressure guage, adaptors, pressure switch, tube fittings, Master control unit with hooter etc, complete as required for satisfactory operation of system complete as per technical specification. Note: (1) All system assemblies and components shall be subjected to the applicable testing by 3rd party testing agencies as PESO / BIS / VDS / UL / LPCB. (2) Extinguishing Agent : CLEAN AGENT (FK-5-1-12) shall be Colourless and odour less gas with Zero Ozone Depletion Potential (ODP). The Quantity of Clean agent shall be determined based on the given largest enclosure volume. (3) Complete system design i/c preparation of shop drawings, submission of technical details of all components, selection of Cylinder capacity, Gas Volume, tube sizing etc duly vetted by the manufacturer (OEM) and submitted to the Engineer-in-Charge for approval before the commencement of work.
2.01 | Main LT panel at Alpha-2 switch room Note :- (a) Panel Dimension : LxWxH = 6.4m x 0.6m x 2.4m (b) Total no. of Enclosures = 08 Nos (c) Volume of largest cubicle= 0.80mx0.60mx2.40m= 1.15 m3 (d) Cubicle volume subject to tolerance of ±10% | 1.00 | Job |  | 46000.00 | 46000.00 | 99000.00 | 99000.00 | 200000.00 | 200000.00 | 107650.00 | 107650.00 | 144990.00 | 144990.00 | 46000.00 | Nexus Fire And Security Systems
2.02 | UPS Panel Incomer Sub LT Panel at Alpha-2 switch room Note :- [a) Panel Dimension : LxWxH = 1.05 m x 0.3m x 1m (b) Total no. of Enclosures = 04 Nos (c) Volume of largest cubicle= 0.45mx0.30mx0.7m= 0.0945 m3 (d) Cubicle volume subject to tolerance of ±10% | 2.00 | Job |  | 46000.00 | 92000.00 | 12500.00 | 25000.00 | 200000.00 | 400000.00 | 39985.00 | 79970.00 | 45450.00 | 90900.00 | 25000.00 | advent electric technologies pvt. ltd.
2.03 | LT Panel and DB at NAV-AIDS sites at Localizer (South Runway) Note :- (a) Panel Dimension (LxWxH) = 1.7 m x 0.4 m x 1.6 m (b) Total no of Enclosures = 03 Nos (including adjacent DB) (c) Volume of largest cubicle= 0.8 mx0.40mx 1.60 m= 0.51 m3 (d) Cubicle volume subject to tolerance of ±10% | 2.00 | Job |  | 46000.00 | 92000.00 | 12500.00 | 25000.00 | 200000.00 | 400000.00 | 43285.00 | 86570.00 | 54945.00 | 109890.00 | 25000.00 | advent electric technologies pvt. ltd.
3.00 | Supply and fixing of following capacity of Modular type Automatic Fire extinguisher, filled with clean agent (FK5.1.12) with all accessories, valve assembly with sprinkler bulb etc i/c fixing on ceiling complete as per technical specification and as per the direction of Engineer-in-charge.
3.01 | 5 kg Capacity | 6.00 | Each |  | 17000.00 | 102000.00 | 20000.00 | 120000.00 | 25000.00 | 150000.00 | 14750.00 | 88500.00 | 12000.00 | 72000.00 | 72000.00 | Swastik Synergy Engineering Pvt. Ltd
| Total in Figures |  |  |  |  | 5306010.00 |  | 5986050.00 |  | 6950000.00 |  | 6397061.00 |  | 7979902.00
Lowest Amount Quoted BY: Nexus Fire And Security Systems(5306010.00)

## BOQ Summary
BOQ Summary Details Tender Title: Design, Supply, Installation, Testing and Commissioning of Gas based Fire Suppression System for NAV- AIDS and other Installations at KIA, Bengaluru. Tender ID: 2025_AAI_242346_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Nexus Fire And Security Systems (BID ID -878895) | 5306010.00 | L1
| 2 | advent electric technologies pvt. ltd. (BID ID -879241) | 5986050.00 | L2
| 3 | Kalpataru Industries (BID ID -878856) | 6397061.00 | L3
| 4 | CENTRE TAP ENGINEERING (BID ID -888959) | 6950000.00 | L4
| 5 | Swastik Synergy Engineering Pvt. Ltd (BID ID -888383) | 7979902.00 | L5