## BoQ1
Government eProcurement System Created By: Sunil Kumar Kotia Created Date/Time: 09-Sep-2025 10:14 AM Tender Title: Replacement of Runway End and Threshold lights with Inset type LED HIRL fitting and worn out main feeder cables of ATC cum Tech. Block at Dehradun Airport Tender ID: 2025_AAI_243247_1
Tender Inviting Authority: Assistant General Manager (Engg.-Elect.), AAI, Dehradun Airport.
Name of Work: Replacement of Runway end & threshold lights with Inset type LED HIRL fitting and worn out main feeder cables of ATC cum Tech. Block at Dehradun Airport.
Contract No:
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Techno Electricals (GSTN-24AAGFT9086M1ZG) BID ID -890951 |  | REWINDER TECHNO ELECTRICALS (GSTN-18AAFFR7457K1ZL) BID ID -891047 |  | Airfield Solutions India pvt Ltd (GSTN-NA) BID ID -881065 |  | SAURABH ENTERPRISES (GSTN-NA) BID ID -890841
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply of following FAA certified or compliant model, Inset type runway edge lights, suitable for ICAO Cat-I all weather operation, high intensity as per ICAO aviation visual aids requirements complete with suitable wattage LED Module/es as per OEM with integral driver, shallow base with side hole entry, suitable for 2.8 to 6.6 Amps current with connected heat resistant accessories, optical assembly, "O" ring seal, pressure relief test plug, hardware, lenses, cable lead with plug and all standard accessories and ready for site installation on existing cement/ asphaltic area and conforming to latest FAA/ICAO/DGCA-CAR and tender specifications complete as required.
1.10 | Bidirectional-Red/Green | 13.00 | Each | 0.00 | 90000.00 | 1170000.00 | 64200.00 | 834600.00 | 81466.60 | 1059065.80 | 60000.00 | 780000.00 | 780000.00 | SAURABH ENTERPRISES
1.20 | Unidirectional- Green | 9.00 | Each | 0.00 | 90000.00 | 810000.00 | 64200.00 | 577800.00 | 62409.92 | 561689.28 | 60000.00 | 540000.00 | 540000.00 | SAURABH ENTERPRISES
2.00 | Installation, Testing and Commissioning of inset fitting (8" / 12" dia) with core cutting, aligning and setting i/c providing sealing material suitable for flexible/rigid pavement. and installation of Isolating Transformer, Crimping / Jointing of Plug receptacles, laying of secondary lead in existing pipe/ in groove i/c groove cutting on existing cement/ asphaltic area & sealing of groove with suitable sealant material as per site requirement & other accessories required for commissioning except fixture, secondary lead, plug & receptacles & isolating transformer etc. as required. | 20.00 | Job | 0.00 | 6800.00 | 136000.00 | 4500.00 | 90000.00 | 7575.00 | 151500.00 | 3000.00 | 60000.00 | 60000.00 | SAURABH ENTERPRISES
3.00 | Supply of 1.1 kV grade Plug and receptacle, Type-II, Class 'B' connector suitable for EPR insulated PCP sheathed secondary lead of size 2 x 4 sq.mm. | 20.00 | Each | 0.00 | 450.00 | 9000.00 | 650.00 | 13000.00 | 707.00 | 14140.00 | 600.00 | 12000.00 | 9000.00 | Techno Electricals
4.00 | Supply of 2 X 4 sqmm, 1.1 kV grade, unarmoured secondary lead cable made out of multi stranded copper conductor, EPR insulated & PCP/ TCP/ CPE sheathed cable with insulation having ant termite & anti-rodent properties. | 100.00 | Mtr | 0.00 | 180.00 | 18000.00 | 200.00 | 20000.00 | 146.45 | 14645.00 | 150.00 | 15000.00 | 14645.00 | Airfield Solutions India pvt Ltd
5.00 | Supply of following ratings, 5KV individual lamp series to series type isolating transformer encapsulated in polyester resin finally molded in neoprene rubber as specified in particular specification.
5.10 | 150W, 20/6.6 Amps | 20.00 | Each | 0.00 | 5200.00 | 104000.00 | 5000.00 | 100000.00 | 3838.00 | 76760.00 | 4000.00 | 80000.00 | 76760.00 | Airfield Solutions India pvt Ltd
6.00 | Dismantling of existing elevated HIRL fitting and Supply & fixing of round Dummy/Blank M.S. Base Plate of 10mm thickness of size suitable to cover the existing transformer housing box. Plates shall have 6 nos. of suitable holes for M10 type bolt including anti-rust coating with black color enamel paint. | 12.00 | Each | 0.00 | 175.00 | 2100.00 | 1600.00 | 19200.00 | 1010.00 | 12120.00 | 1300.00 | 15600.00 | 2100.00 | Techno Electricals
7.00 | SITC of 4KW Indoor Type Air Cooled Constant Current Regulator (CCR) of Micro Processor Controlled, Thyristor Type suitable for operation on single phase 230V / 2-phase 400V AC + PE ± 10%, 50 Hz input AC supply with 5 steps variation of current output (2.8, 3.4, 4.0, 5.2 and 6.6 Amp) and able to communicate with PC or PLC controlled system with digital output ammeter (0-10 Amps), over current, over voltage, open circuit and earth fault protection and earth leakage meter, two stage earth leakage detector, positive back indication equipment's, hours run counter, LCD display complete as required and confirm to tender specifications and suitable for operation on the existing Airfield Lighting Control and Monitoring System (ALCMS) with communication, local and remote control and monitoring even and data recording and history keeping etc. complete as required. | 1.00 | Each | 0.00 | 250000.00 | 250000.00 | 225000.00 | 225000.00 | 181800.00 | 181800.00 | 200000.00 | 200000.00 | 181800.00 | Airfield Solutions India pvt Ltd
8.00 | Supply of following size Aluminum conductor Power Cable, multi stranded conductor, XLPE Insulated, Armoured, FRLSH at outer sheathed,1100V grade as per IS 7098(Part 1) 1988.
8.10 | 3.5C x 400 sq. mm | 2000.00 | Mtrs | 0.00 | 2000.00 | 4000000.00 | 2250.00 | 4500000.00 | 1605.02 | 3210040.00 | 1900.00 | 3800000.00 | 3210040.00 | Airfield Solutions India pvt Ltd
8.20 | 3.5C x 95 sq.mm | 300.00 | Mtrs | 0.00 | 524.00 | 157200.00 | 750.00 | 225000.00 | 437.33 | 131199.00 | 650.00 | 195000.00 | 131199.00 | Airfield Solutions India pvt Ltd
9.00 | Supplying of 120 mm dia (OD-120 mm & ID-103 mm nominal) size DWC HDPE pipe conforming to IS 14930, Part II complete from AAI preferred makes and ISI marked complete as required. | 2110.00 | Mtrs | 0.00 | 175.00 | 369250.00 | 450.00 | 949500.00 | 131.30 | 277043.00 | 350.00 | 738500.00 | 277043.00 | Airfield Solutions India pvt Ltd
10.00 | Laying of 120 mm dia (OD-120 mm & ID-103 mm nominal) size DWC HDPE pipe with all accessories like socket, bend, couplers etc. conforming to IS 14930, Part II complete with fitting and cutting, jointing etc.direct in ground (75 cm below ground level) including excavation and refilling the trench but excluding sand cushioning and protective covering etc., complete as required. | 2110.00 | Mtrs | 0.00 | 135.00 | 284850.00 | 100.00 | 211000.00 | 303.00 | 639330.00 | 80.00 | 168800.00 | 168800.00 | SAURABH ENTERPRISES
11.00 | Laying of one number PVC insulated & PVC sheathed / XPLE power cable of 1.1 kv grade of following sizes in the existing RCC/ Hume/ Stoneware/ Metal Pipe/HDPE DWC Pipe is required.
11.10 | Above 185 sq. mm and upto 400 sq. mm | 2110.00 | Mtrs | 0.00 | 75.00 | 158250.00 | 50.00 | 105500.00 | 252.50 | 532775.00 | 40.00 | 84400.00 | 84400.00 | SAURABH ENTERPRISES
11.20 | Above 35 sq. mm and upto 95 sq. mm | 300.00 | Mtrs | 0.00 | 45.00 | 13500.00 | 45.00 | 13500.00 | 252.50 | 75750.00 | 30.00 | 9000.00 | 9000.00 | SAURABH ENTERPRISES
12.00 | Supplying and making straight through joint with heat shrinkable kit including ferrules and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminum conductor cable of 1.1 KV grade as required.
12.10 | 3.5C X 400sqmm | 4.00 | Each | 0.00 | 8000.00 | 32000.00 | 8000.00 | 32000.00 | 2979.50 | 11918.00 | 4000.00 | 16000.00 | 11918.00 | Airfield Solutions India pvt Ltd
13.00 | Supplying & making end termination with brass compression gland and lugs for following Cable size of XLPE insulated & PVC sheathed power cable of 1.1 kv grade as required.
13.10 | 3.5C X 400sqmm | 16.00 | Each | 0.00 | 1500.00 | 24000.00 | 900.00 | 14400.00 | 2979.50 | 47672.00 | 100.00 | 1600.00 | 1600.00 | SAURABH ENTERPRISES
13.20 | 3.5C x 95 sq.mm | 2.00 | Each | 0.00 | 600.00 | 1200.00 | 700.00 | 1400.00 | 1010.00 | 2020.00 | 100.00 | 200.00 | 200.00 | SAURABH ENTERPRISES
14.00 | Excavation of the cable trenches in hard rock not exceeding 1.5 meters in width, and lift upto 1.5 meters, including getting out the excavated soil and disposal of excavated soil as directed within a lead of 50 meters. | 35.00 | Cu.m | 0.00 | 800.00 | 28000.00 | 600.00 | 21000.00 | 7070.00 | 247450.00 | 500.00 | 17500.00 | 17500.00 | SAURABH ENTERPRISES
15.00 | Dismantling, relocating and re-installation of existing joint feeder pillar (of 4 no.of 3.5x400 sqmm LT cable) including required excavation, making of PCC foundation & re-alignment of existing cable for proper connection to joint feeder pillar and refilling the excavated ground & making good the same as per site requirement & direction of E-I-C . | 2.00 | Job | 0.00 | 12000.00 | 24000.00 | 7000.00 | 14000.00 | 15150.00 | 30300.00 | 5000.00 | 10000.00 | 10000.00 | SAURABH ENTERPRISES
16.00 | Providing and laying of 110mm OD, PN 6 PE 63 HDPE pipe(IS:4984-95 marked) with HDD trenchless method direct in ground (upto 6 mtrs below ground level ) for runway crossing in all type soil including suitable size PP rope, etc. complete in all respect as per direction of Engineer-in-Charge required. Note: - 1. Spare length= 2 mtrs of HDPE pipe should be left as spare on both side. & this will be excluding the HDD measurements. 2. Agency is required to visit the site to survey the soil/ground conditions & site constraints which shall be considered while quoting the rate of this item. | 300.00 | Mtrs | 0.00 | 2900.00 | 870000.00 | 800.00 | 240000.00 | 707.00 | 212100.00 | 700.00 | 210000.00 | 210000.00 | SAURABH ENTERPRISES
| Total in Figures |  |  |  |  | 8461350.00 |  | 8206900.00 |  | 7489317.08 |  | 6953600.00
Lowest Amount Quoted BY: SAURABH ENTERPRISES(6953600.00)

## BOQ Summary
BOQ Summary Details Tender Title: Replacement of Runway End and Threshold lights with Inset type LED HIRL fitting and worn out main feeder cables of ATC cum Tech. Block at Dehradun Airport Tender ID: 2025_AAI_243247_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | SAURABH ENTERPRISES (BID ID -890841) | 6953600.00 | L1
| 2 | Airfield Solutions India pvt Ltd (BID ID -881065) | 7489317.08 | L2
| 3 | REWINDER TECHNO ELECTRICALS (BID ID -891047) | 8206900.00 | L3
| 4 | Techno Electricals (BID ID -890951) | 8461350.00 | L4