## BoQ1
Government eProcurement System Created By: Jagannath singh Deshmukh Created Date/Time: 30-Sep-2025 02:02 PM Tender Title: Replacement of existing DG sets by 02 Nos. 320 KVA DG sets at Jamnagar Airport. Tender ID: 2025_AAI_244547_1
Tender Inviting Authority:Asst.General Manager (E-E)
Name of Work: “Replacement of existing DG sets by 02 Nos. 320 KVA DG sets at Jamnagar Airport."
Contract No: 2025_AAI_244547_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | FUJI TECHNICAL SERVICES PVT. LTD. (GSTN-27AAACF1784F1ZQ) BID ID -893851 |  | AYESHA ENTERPRISES (GSTN-09BNPPA3665N1ZE) BID ID -893893 |  | Ascent Electrification Engineers (GSTN-24AAOFA2574R1ZU) BID ID -891489 |  | Awasthi Electric Works (GSTN-09ABAPA1866D1Z5) BID ID -893990 |  | Virtus Techno (GSTN-NA) BID ID -889999 |  | VOID FIRE CONSULTANTS (GSTN-NA) BID ID -893039
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply Installation Testing Commissioning of "Silent Type" Radiator Cooled,"Outdoor Type" Diesel Generating set along with having Prime mover power rating of 320 KVA at 0.8 lagging power factor, 415 volts, 1500 RPM, 3 phase system, for 0.85 load factor and consisting of the following including providing necessary CEA,CPCB approval etc. as required: (a) Diesel Engine: 4 stroke, electronic governor, radiator cooled, electric start, of suitable BHP at 1500 RPM suitable for above output of alternator at 40 Degree C, 50% RH & at 500 Meter MSL and conforming to BS 5514, BS 649, IS 10000, capable of taking 10% over loading for one hour after 12 hours of continuous operation. The engine will be fitted complete with all the required accessories.The DG set shall comply CPCB-IV Plus norms. (b) Engine mounted Instrument Panel fitted with having digital display for following: (i) Start- stop switch with Key. (ii) Water Temprature Indication (iii) Lubrication Oil Pressure Indication (iv) Lubrication Oil Temprature Indication (v) Battery Charging Indication (vi) RPM Indication (Vii) Over Speed Indication (Viii) Low Lub Oil Trip Indication (ix) Engine Running Hours Indication (c) Alternator: Synchronous alternator rated for 320 KVA, 415 volts at 1500 RPM, 3 phase 50 Hz, AC supply with 0.8 lagging power factor at 40 Degree C, 50% RH & at 500 Meter MSL. The alternator shall be having SPDP enclosure, brushless, continuous duty, self-excited and self-regulated through AVR, conforming to IS:4722 / BS 2613 suitable for tropical conditions and with class-F/H insulation. (d) Base Frame & Foundation: Both the engine and alternator shall be mounted on suitable base frame made of MS channel which shall be installed on suitable cement concrete foundation with necessary reinforcement including vibration isolation arrangement as per recommendations of manufacturer and site conditions. (e) Fuel Tank: Day service fuel tank (Free Standing type) of minimum 900 litres capacity fabricated out of 3 mm thick M.S. sheet complete with all standard accessories and fuel piping between fuel tank and diesel engine with MS class 'C' pipes of suitable dia. complete with valves, level indications, stand & accessories including foundation complete as required as per specifications. (f) Exhaust System: Dry Exhaust manifold with residential exhaust silencer and catalytic convertor including supplying & fixing Stainless Steel Expansion Joints, Corrugated bellows suitable for 320 KVA DG Sets to fit in exhaust pipe. (g) Starting System: 12V / 24V DC starting system (or as per manufacturer / OEM standards) comprising of starter motors, voltage regulator and arrangement for initial excitation complete with suitable nos. of batteries with MS battery stand, external battery charging panel etc. as required as per OEM standards. (h) Acoustic Enclosure : Acoustic and weather proof enclosure with arrangement for fresh air intake for cooling of the engine & alternator, extraction, discharging hot air in to the atmosphere as per specifications. (i) Approvals : Prepration of necessary drawing, Co-ordination and approval from Central Electrical Authority (CEA) / Pollution control board standards as per requirement. | 2.00 | Each |  | 2794313.00 | 5588626.00 | 2800000.00 | 5600000.00 | 2690400.00 | 5380800.00 | 2845000.00 | 5690000.00 | 3470642.50 | 6941285.00 | 2395000.00 | 4790000.00 | 4790000.00 | VOID FIRE CONSULTANTS
2.00 | Supplying and fixing exhaust gas piping (suitable for 320 KVA D.G. Set) of size 250 mm nominal dia welded black MS pipe (6 mm thick) conforming to IS:3589 cut to required lengths and installed with necessary bends, supports and clamps, anti-vibration mountings, insulation of exhaust system with loosely bound resin (LBR) mattress / mineral wool/ Rockwool of 50 mm thick, wiremesh & 0.6 mm thick aluminum cladding for the complete portion etc. as required as per specifications. | 20.00 | Meter |  | 10500.00 | 210000.00 | 6150.00 | 123000.00 | 5500.00 | 110000.00 | 4500.00 | 90000.00 | 10350.00 | 207000.00 | 8800.00 | 176000.00 | 90000.00 | Awasthi Electric Works
3.00 | Providing & fixing for MS support structure including suitable civil foundation for exhaust gas pipes of DG Sets along horizontal and vertical runs and monkey ladder upto the height (as per CPCB norms) including cutting, welding etc and applying two coats of red oxide and two coats of synthetic enameled paint of colour and shade as directed by AAI. The design of the support structure shall be done by the contractor and shall be as per CPCB norms. Design shall be got approved from the AAI before execution as required. | 400.00 | Kg |  | 157.50 | 63000.00 | 145.00 | 58000.00 | 136.80 | 54720.00 | 220.00 | 88000.00 | 103.50 | 41400.00 | 180.00 | 72000.00 | 41400.00 | Virtus Techno
4.00 | Fabricating, Installing, Testing and Commissioning of Automatic Mains Failure (AMF) control panel having 50 kA short circuit breaking capacity, suitable for 320 KVA Silent Type DG set complete with relays, timers, set of CTs for metering & protection and energy analyser to indicate current, phase & line voltages, frequency, power factor, KWH, KVARH & provision for overload, short circuit, restricted earth fault, under frequency, interlocking arrangment etc. Panel shall be totally enclosed , dust and vermin proof, front patern, free floor standing type with four pole by pass arrangment including the following (Including dismantaling of Existing AMF panel and installation of new panel at the same location: (a) ACB Mains : (i) 630 A, 4-pole Microprocessor based release (for O/C, E/F & Shunt Trip) motorised electrically operated EOD tpye ACB having 50 kA short circuit breaking capacity with suitable 4P contractor for Main supply - 01 set (b) ACB Alternator : (i) 630 A, 4-pole Microprocessor based release (for O/C, E/F & Shunt Trip) motorised electrically operated EOD tpye ACB having 50 kA short circuit breaking capacity with suitable 4P contractor for DG supply - 01 set (c ) Microprocessor based AMF Module incorporating : (i) Supply Failure Timer. (ii) Restoration Timer. (iii) 3 Impulse automatic engine Start / Stop logic. (iv) Mains / Generator Voltage & Frequency Sensing. (v)Provision for over load,Short circuit,restricted earth fault,under frequency etc. (d) Metering : (i) Combined meter for Voltage / Ampere / Frequency. (ii) Combined meter for KW / Power Factor / KVA. (iii) Electronic KWH Meter. (iv) 3 sets of CT's 15 P 10 accuracy for protection and 15 VA class-I for metering. (v) Control MCB's (e ) Indicationd (LED Type) (i) DG ON (ii) Load on DG (iii) Mains ON (iv) Load on Mains (v) Battery Charger ON (vi) Auto/Manual/Test/Off selector switch. (f) Push Buttons (AMF Module by pass mode) : (i) Engine STRAT / STOP (ii) Generator breaker CLOSE / TRIP (iii) Mains breaker CLOSE / TRIP (iv) Fault ACCEPT / RESET (g) Battery Charger : (i) SMPS Based Battery Charger Unit complete with transformer / rectifier, suitable DC Voltmeter and Ammeter, selector switch for Trickle, Off and Boost, current adjustment etc. (h) Over Current & Earth fault Relay (EC2 of C&S make or equivalent) (i) Audio / visual annunciation for - High Water temprature, Low Lubricating Oil Pressure, Engine Over Speed, Engine Fails to Start, Full Load / Maximum Load warning. (j) By Pass Arrangment (to by pass the AMF panel) - On Load 630A change Over Switch for AMF panel By pass arrangment-2 Nos | 2.00 | Each |  | 630000.00 | 1260000.00 | 340000.00 | 680000.00 | 804270.00 | 1608540.00 | 825000.00 | 1650000.00 | 585022.25 | 1170044.50 | 478000.00 | 956000.00 | 680000.00 | AYESHA ENTERPRISES
5.00 | Supply of 3.5 Core x 300 Sqmm size 1.1 KV grade XLPE insulated, PVC sheathed, armoured Aluminium conductor cable conforming to IS 7098 (Part 1) amended upto date as required. | 400.00 | Meter |  | 1470.00 | 588000.00 | 1590.00 | 636000.00 | 1208.40 | 483360.00 | 1525.00 | 610000.00 | 1376.14 | 550456.00 | 1990.00 | 796000.00 | 483360.00 | Ascent Electrification Engineers
6.00 | Supplying of 12 core X 2.5 Sqmm of 1.1 kV grade PVC insulated copper conductor armoured stranded Control Cable conforming to IS: 1554 complete as required and as per specifications. | 140.00 | Meter |  | 630.00 | 88200.00 | 299.00 | 41860.00 | 392.16 | 54902.40 | 525.00 | 73500.00 | 433.49 | 60688.60 | 830.00 | 116200.00 | 41860.00 | AYESHA ENTERPRISES
7.00 | Supplying and making end termination with brass compression gland and aluminium lugs for 3.5 core X 300 sq. mm (70 mm) size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. | 12.00 | Each | 100.00 | 3675.00 | 44100.00 | 850.00 | 10200.00 | 1710.00 | 20520.00 | 1200.00 | 14400.00 | 2587.50 | 31050.00 | 3850.00 | 46200.00 | 10200.00 | AYESHA ENTERPRISES
8.00 | Supplying and making indoor Control Cable end Termination of 12 core X 2.5 Sqmm sizes 650V grade LT XLPE insulated, HR PVC sheathed, stranded copper conductor, Armoured cables, including cost of tinned copper heavy duty crimping lugs, Single compression heavy duty glands, insulation tape, Name Plate at Both Ends and all necessary material to complete the termination. | 4.00 | Each | 100.00 | 1575.00 | 6300.00 | 170.00 | 680.00 | 1710.00 | 6840.00 | 300.00 | 1200.00 | 1552.50 | 6210.00 | 700.00 | 2800.00 | 680.00 | AYESHA ENTERPRISES
9.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of o size above 185 sq. mm and upto 400 sq. mm in the existing RCC/ HUME/ METAL/HDPE pipe as required. | 80.00 | Meter |  | 367.50 | 29400.00 | 150.00 | 12000.00 | 79.80 | 6384.00 | 120.00 | 9600.00 | 138.00 | 11040.00 | 350.00 | 28000.00 | 6384.00 | Ascent Electrification Engineers
10.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of size above 185 sq. mm and upto 400 sq. mm in the existing masonry open duct as required. | 280.00 | Meter |  | 262.50 | 73500.00 | 135.00 | 37800.00 | 79.80 | 22344.00 | 100.00 | 28000.00 | 138.00 | 38640.00 | 250.00 | 70000.00 | 22344.00 | Ascent Electrification Engineers
11.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of upto size upto 35 sq. mm in the existing RCC/ HUME/ METAL/HDPE/in existing trench pipe as required. | 100.00 | Meter |  | 210.00 | 21000.00 | 90.00 | 9000.00 | 51.30 | 5130.00 | 40.00 | 4000.00 | 92.00 | 9200.00 | 200.00 | 20000.00 | 4000.00 | Awasthi Electric Works
12.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of size upto 35 sq. mm in the existing masonry open duct as required. | 20.00 | Meter | 100.00 | 157.50 | 3150.00 | 50.00 | 1000.00 | 51.30 | 1026.00 | 30.00 | 600.00 | 92.00 | 1840.00 | 100.00 | 2000.00 | 600.00 | Awasthi Electric Works
13.00 | Earthing with copper earth plate 600 mm X 600 mm X 3 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with charcoal/ coke and salt as required. | 4.00 | Set | 100.00 | 21000.00 | 84000.00 | 20000.00 | 80000.00 | 18981.00 | 75924.00 | 20000.00 | 80000.00 | 21275.00 | 85100.00 | 16500.00 | 66000.00 | 66000.00 | VOID FIRE CONSULTANTS
14.00 | Supplying and laying 25 mm X 5 mm G.I strip at 0.50 meter below ground as strip earth electrode, including connection/ terminating with G.I. nut, bolt, spring, washer etc. as required. (Jointing shall be done by overlapping and with 2 sets of G.I. nut bolt & spring washer spaced at 50 mm) | 150.00 | Meter |  | 420.00 | 63000.00 | 350.00 | 52500.00 | 132.24 | 19836.00 | 250.00 | 37500.00 | 207.00 | 31050.00 | 195.00 | 29250.00 | 19836.00 | Ascent Electrification Engineers
15.00 | Providing and fixing 6 SWG dia G.I. wire on surface or in recess for loop earthing along with existing surface/ recessed conduit / submain wiring / cable as required. | 200.00 | Meter |  | 52.50 | 10500.00 | 55.00 | 11000.00 | 17.21 | 3442.00 | 30.00 | 6000.00 | 36.80 | 7360.00 | 62.00 | 12400.00 | 3442.00 | Ascent Electrification Engineers
16.00 | Providing, laying and fixing following dia G.I. pipe (medium class) in ground complete with G.I. fittings including trenching (75 cm deep)and re-filling etc as required. 50 mm | 100.00 | Meter |  | 315.00 | 31500.00 | 625.00 | 62500.00 | 513.00 | 51300.00 | 450.00 | 45000.00 | 451.95 | 45195.00 | 860.00 | 86000.00 | 31500.00 | FUJI TECHNICAL SERVICES PVT. LTD.
17.00 | Supply of DWC HDPE Pipe of size 90 mm dia (OD-90 mm & ID-76 mm nominal), as per IS:4984 of complete as required. | 70.00 | Meter |  | 1260.00 | 88200.00 | 170.00 | 11900.00 | 102.60 | 7182.00 | 125.00 | 8750.00 | 207.00 | 14490.00 | 365.00 | 25550.00 | 7182.00 | Ascent Electrification Engineers
18.00 | Laying of 90 mm dia (OD-90 mm & ID-76 mm nominal) pipe direct in ground (below 75 cm) including excavation of suitable trench and refilling the trench etc complete as required. | 70.00 | Meter |  | 367.50 | 25725.00 | 140.00 | 9800.00 | 96.90 | 6783.00 | 200.00 | 14000.00 | 172.50 | 12075.00 | 280.00 | 19600.00 | 6783.00 | Ascent Electrification Engineers
19.00 | Supplying and laying 25 mm X 5 mm copper strip at 0.50 metre below ground as strip earth electrode, including connection/terminating with nut, bolt, spring, washer etc. as required. (Jointing shall be done by overlapping and with 2 sets of brass nut bolt & spring washer spaced at 50mm) | 100.00 | Meter |  | 1312.50 | 131250.00 | 980.00 | 98000.00 | 1103.98 | 110398.00 | 1300.00 | 130000.00 | 1345.50 | 134550.00 | 1830.00 | 183000.00 | 98000.00 | AYESHA ENTERPRISES
| Total in Figures |  |  |  |  | 8409451.00 |  | 7535240.00 |  | 8029431.40 |  | 8580550.00 |  | 9398674.10 |  | 7497000.00
Lowest Amount Quoted BY: VOID FIRE CONSULTANTS(7497000.00)

## BOQ Summary
BOQ Summary Details Tender Title: Replacement of existing DG sets by 02 Nos. 320 KVA DG sets at Jamnagar Airport. Tender ID: 2025_AAI_244547_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | VOID FIRE CONSULTANTS (BID ID -893039) | 7497000.00 | L1
| 2 | AYESHA ENTERPRISES (BID ID -893893) | 7535240.00 | L2
| 3 | Ascent Electrification Engineers (BID ID -891489) | 8029431.40 | L3
| 4 | FUJI TECHNICAL SERVICES PVT. LTD. (BID ID -893851) | 8409451.00 | L4
| 5 | Awasthi Electric Works (BID ID -893990) | 8580550.00 | L5
| 6 | Virtus Techno (BID ID -889999) | 9398674.10 | L6