## BoQ1
Government eProcurement System Created By: Ambrish Singh Created Date/Time: 23-Sep-2025 05:29 PM Tender Title: Shifting of DVOR at LBSI Airport, Varanasi, SH- Electrical Works Tender ID: 2025_AAI_244584_1
Tender Inviting Authority: Asstt. General Manager (Engg.-E), LBSI Airport Varanasi.
Name of Work:“Shifting of DVOR at LBSI Airport, Varanasi; SH: Electrical Works”
Contract No: 2025_AAI_244584_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Awasthi Electric Works (GSTN-09ABAPA1866D1Z5) BID ID -897604 |  | Nabalok Das (GSTN-NA) BID ID -897482 |  | SAURABH ENTERPRISES (GSTN-NA) BID ID -897062
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Wiring for light point/ fan point/ exhaust fan point/ call bell point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in surface / recessed steel (MS) conduit, with modular switch, modular plate, suitable GI box and earthing the point with 1.5 sq.mm. FRLS PVC insulated copper conductor single core cable etc as required. Group C | 37.00 | POINT |  | 1200.00 | 44400.00 | 1100.00 | 40700.00 | 1450.00 | 53650.00 | 40700.00 | Nabalok Das
2.00 | Wiring for circuit/ submain wiring alongwith earth wire with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface/ recessed steel (MS) conduit as required 2 X 2.5 sq. mm + 1 X 2.5 sq. mm earth wire | 100.00 | Mtrs |  | 250.00 | 25000.00 | 270.00 | 27000.00 | 200.00 | 20000.00 | 20000.00 | SAURABH ENTERPRISES
3.00 | Wiring for light/ power plug with 2X4 sq. mm FRLS PVC insulated copper conductor single core cable in surface/ recessed steel (MS) conduit alongwith 1 No 4 sq. mm FRLS PVC insulated copper conductor single core cable for loop earthing as required | 150.00 | Mtrs |  | 300.00 | 45000.00 | 333.00 | 49950.00 | 375.00 | 56250.00 | 45000.00 | Awasthi Electric Works
4.00 | Wiring for light/ power plug with 4X4 sq. mm FRLS PVC insulated copper conductor single core cable in surface/ recessed steel (MS) conduit alongwith 2 Nos 4 sq. mm FRLS PVC insulated copper conductor single core cable for loop earthing as required. | 100.00 | Mtrs |  | 550.00 | 55000.00 | 550.00 | 55000.00 | 450.00 | 45000.00 | 45000.00 | SAURABH ENTERPRISES
5.00 | Wiring for circuit/ submain wiring alongwith earth wire with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface/ recessed steel (MS) conduit as required. 4X16 Sqmm +2X6Sqmm | 25.00 | Mtrs |  | 1400.00 | 35000.00 | 1200.00 | 30000.00 | 1150.00 | 28750.00 | 28750.00 | SAURABH ENTERPRISES
6.00 | Supply and drawing of CAT6 , unarmored , copper conductor, plyethelyne insulated , twisted pairs (UTP) LAN (Computer) cable in existing 25 mm Metal/PVC conduit complete as required. | 50.00 | Mtrs |  | 60.00 | 3000.00 | 57.00 | 2850.00 | 65.00 | 3250.00 | 2850.00 | Nabalok Das
7.00 | Supplying and fixing of following sizes of PVC conduit along with accessories in surface/recess including cutting the wall and making good the same in case of recessed conduit as required. 25 mm dia | 650.00 | Mtrs |  | 95.00 | 61750.00 | 145.00 | 94250.00 | 125.00 | 81250.00 | 61750.00 | Awasthi Electric Works
8.00 | Supplying and fixing suitable size GI box with modular plate and cover in front on surface or in recess, including providing and fixing 6 pin 5/6 & 15/16 amps modular socket outlet and 15/16 amps modular switch, connections etc. as required. | 30.00 | Each |  | 450.00 | 13500.00 | 586.00 | 17580.00 | 170.00 | 5100.00 | 5100.00 | SAURABH ENTERPRISES
9.00 | Supply and fixing of following moduler switch/socket/accessories on the existing moduler plate and switch box i/c connection but excluding moduler plate etc. as required. a) Telephone/ Cat6A socket outlet | 2.00 | Each |  | 475.00 | 950.00 | 500.00 | 1000.00 | 150.00 | 300.00 | 300.00 | SAURABH ENTERPRISES
10.00 | Supply and fixing of following moduler switch/socket/accessories on the existing moduler plate and switch box i/c connection but excluding moduler plate etc. as required. b) 01 module blanking plate | 10.00 | Each |  | 30.00 | 300.00 | 400.00 | 4000.00 | 90.00 | 900.00 | 300.00 | Awasthi Electric Works
11.00 | Supply and fixing of following moduler switch/socket/accessories on the existing moduler plate and switch box i/c connection but excluding moduler plate etc. as required. c) Two module fan regulator | 6.00 | Each |  | 485.00 | 2910.00 | 580.00 | 3480.00 | 100.00 | 600.00 | 600.00 | SAURABH ENTERPRISES
12.00 | Supplying & fixing suitable size GI box wih modular plate and cover in front on surface or in recess including providing and fixing 25 A modular socket outlet and 25 A modular SP MCB, "C" curve including connections, painting etc. as required. | 7.00 | Each |  | 850.00 | 5950.00 | 430.00 | 3010.00 | 210.00 | 1470.00 | 1470.00 | SAURABH ENTERPRISES
13.00 | Supplying and fixing following size/ modules, GI box along with modular base & cover plate for modular switches in recess etc as required. 1 or 2 Module (75 mmX75 mm) | 5.00 | Each |  | 225.00 | 1125.00 | 155.00 | 775.00 | 70.00 | 350.00 | 350.00 | SAURABH ENTERPRISES
14.00 | Supplying and fixing following size/ modules, GI box along with modular base & cover plate for modular switches in recess etc as required. 3 Module (100 mmX75 mm) | 5.00 | Each |  | 250.00 | 1250.00 | 190.00 | 950.00 | 85.00 | 425.00 | 425.00 | SAURABH ENTERPRISES
15.00 | Supplying and fixing following size/ modules, GI box along with modular base & cover plate for modular switches in recess etc as required. 4 Module (125 mmX75 mm) | 5.00 | Each |  | 280.00 | 1400.00 | 225.00 | 1125.00 | 90.00 | 450.00 | 450.00 | SAURABH ENTERPRISES
16.00 | Supplying and fixing following size/ modules, GI box along with modular base & cover plate for modular switches in recess etc as required. 8 Module (125 mmX125 mm) | 5.00 | Each |  | 550.00 | 2750.00 | 220.00 | 1100.00 | 180.00 | 900.00 | 900.00 | SAURABH ENTERPRISES
17.00 | Supplying and fixing of following ways surface/ recess mounting, vertical type, 415 V, TPN MCB distribution board of sheet steel, dust protected, duly powder painted, inclusive of 200 A tinned copper bus bar, common neutral link, earth bar, din bar for mounting MCBs (but without MCBs and incomer ) as required . (Note : Vertical type MCB TPDB is normally used where 3 phase outlets are required.) 4 way (4+12), Double door | 2.00 | Each |  | 6500.00 | 13000.00 | 8900.00 | 17800.00 | 3800.00 | 7600.00 | 7600.00 | SAURABH ENTERPRISES
18.00 | Supplying and fixing following rating, four poles, (three phase and neutral) 415 Volts, 10kA MCB in the existing MCB DB complete with connections, testing and commissioning etc. as required. 63A | 2.00 | Each |  | 1500.00 | 3000.00 | 1500.00 | 3000.00 | 1550.00 | 3100.00 | 3000.00 | Nabalok Das, Awasthi Electric Works
19.00 | Supplying and fixing following rating, Four pole, (Three phase and neutral), 415 volts, residual current circuit breaker (RCCB), having a sensitivity current 300 mA in the existing MCB DB complete with connections, testing and commissioning etc. as required. 63 A | 2.00 | Each |  | 2900.00 | 5800.00 | 3500.00 | 7000.00 | 3500.00 | 7000.00 | 5800.00 | Awasthi Electric Works
20.00 | Supplying and fixing 5 A to 32 A rating, 240/415 V, 10 kA, “C” curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required. Single pole | 24.00 | Each |  | 200.00 | 4800.00 | 150.00 | 3600.00 | 200.00 | 4800.00 | 3600.00 | Nabalok Das
21.00 | Supplying and fixing single pole blanking plate in the existing MCB DB complete etc. as required. | 24.00 | Each |  | 20.00 | 480.00 | 32.00 | 768.00 | 40.00 | 960.00 | 480.00 | Awasthi Electric Works
22.00 | Supplying and fixing telephone junction box with 10 pair termination socket in wall / ground with suitable arrangement. | 2.00 | Each |  | 950.00 | 1900.00 | 3700.00 | 7400.00 | 90.00 | 180.00 | 180.00 | SAURABH ENTERPRISES
23.00 | Supply and installation of Surface/ recessed mounted 2X2 LED light fixture having luminous efficacy not less than 100 Lumens/watt, lumen output not less than 2400 Lumen, life >= 50,000 burning hours, with extruded aluminium/CRCA/Standard alloy housing, CRI>=80, THD<10%,integrated driver,IK rating >=04, surge protection conforming to relevant IS standard/IEC for LED driver (inbuilt): EN61000-4-5, suitable for operation on 140V-270V, 50 Hz supply with all accessories etc. complete as required. | 19.00 | Each |  | 2000.00 | 38000.00 | 3200.00 | 60800.00 | 1475.00 | 28025.00 | 28025.00 | SAURABH ENTERPRISES
24.00 | Supply and installation of LED round panel downlight having luminous efficacy not less than 100 Lumens/watt, lumen output not less than 1200 Lumen, life >= 50000 burning hours, with extruded aluminium/CRCA/Standard alloy housing, CRI>=80, THD<=20,integrated driver, surge protection conforming to relevant IS standard/IEC for LED driver (inbuilt): EN61000-4-5, suitable for operation on 140V-270V, 50 Hz supply with all accessories etc. complete as required. | 2.00 | Each |  | 1050.00 | 2100.00 | 2800.00 | 5600.00 | 650.00 | 1300.00 | 1300.00 | SAURABH ENTERPRISES
25.00 | Supply and installation of LED street light luminaire having efficiency of LED light fitting (Efficacy) not less than 110 lumens/watt,lumen output not less then 4950 lumens with lenses consisting of high pressure die cast/extruded aluminum housing,heat resistant toughened glass/ polycarbonate cover, CRI>=80, THD<10%, life >= 50000 burning hours, integrated driver, IP category >=65, with surge protection conforming to relevant IS standard/IEC suitable for operation on 140V-270V, 50 Hz AC supply with all accessories complete as required & as specified. | 7.00 | Each |  | 2200.00 | 15400.00 | 5300.00 | 37100.00 | 1550.00 | 10850.00 | 10850.00 | SAURABH ENTERPRISES
26.00 | Supply, Installation, Testing and Commissioning of 9 Watt Emergency Rechargeable wall mounted LED Light with Auto ON feature during power failure suitable to operate on 230V, 50 Hz single phase AC supply, complete as required. | 3.00 | Each |  | 7500.00 | 22500.00 | 4300.00 | 12900.00 | 950.00 | 2850.00 | 2850.00 | SAURABH ENTERPRISES
27.00 | Supply, Installation, Testing and Commissioning of 1200 mm sweep, BEE 5 star rated, ceiling fan with Brush Less Direct Current (BLDC) Motor, class of insulation: B, 3 nos. blades, 30 cm long down rod, 2 nos. canopies, shackle kit, safety rope, copper winding, Power Factor not less than 0.9, Service Value (CM/M/W) minimum 6.00, Air delivery minimum 210 Cum/Min , 350 RPM (tolerance as per IS : 374 2019), THD less than 10%, remote or electronic regulator unit for speed control and all remaining accessories including safety pin, nut bolts, washers, fan box (fixing at the time of roof casting in coordination with Civil works) temperature rise=75 degree C (max.), insulation resistance more than 2 mega ohm, suitable for 230 V, 50 Hz, single phase AC Supply, earthing etc. complete as required. | 6.00 | Each |  | 2500.00 | 15000.00 | 4500.00 | 27000.00 | 2800.00 | 16800.00 | 15000.00 | Awasthi Electric Works
28.00 | Supply, Installation, Testing and Commissioning of exhaust fan up to 450 mm sweep in the existing opening, including making good the damage, connection, testing, commissioning etc. as required | 3.00 | Each |  | 3500.00 | 10500.00 | 3500.00 | 10500.00 | 2500.00 | 7500.00 | 7500.00 | SAURABH ENTERPRISES
29.00 | Installation, testing and commissioning of pre-wired, fluorescent fitting / compact fluorescent fitting/ LED fittings of all types, complete with all accessories and tube etc. directly on ceiling/ wall, including connection with 1.5 sq. mm FRLS PVC insulated, copper conductor, single core cable and earthing and clamp and holders (as per requirement) etc. as required. | 28.00 | Each |  | 125.00 | 3500.00 | 1000.00 | 28000.00 | 125.00 | 3500.00 | 3500.00 | SAURABH ENTERPRISES, Awasthi Electric Works
30.00 | SITC of 2 TR Inverter type Split Air-Conditioner of BEE 5 Star rating Hi-wall split 2 Ton non ductible fan coil unit (Indoor Unit), Copper Condensing unit (Outdoor Unit) with fan and High Energy Efficiency compressor, with remote controller and works with R410A/R407C/R 134A gas, suitable for operation on 1 Phase, 230 +/- 10%V, 50Hz AC supply etc. complete as required i/c holder of remote . The supply of unit shall include the copper pipings, Interconnecting Power cables between the Indoor and Outdoor Unit as per the standard manufacturer design (i.e. Copper pipings of not less than 3 Mtrs), suitable Outdoor uint stands (apx. 1 mtr height) and initial charge of gas etc. complete as required. | 7.00 | SET |  | 47500.00 | 332500.00 | 49500.00 | 346500.00 | 74613.00 | 522291.00 | 332500.00 | Awasthi Electric Works
31.00 | Providing of extra refrigerant piping, cabling (More than standard length) , insulating with foam between indoor and outdoor units etc. as required. | 35.00 | Mtrs |  | 1500.00 | 52500.00 | 670.00 | 23450.00 | 1995.00 | 69825.00 | 23450.00 | Nabalok Das
32.00 | Providing and fixing of extra drain CPVC / UPVC pipe for condensate water from indoor unit to nearest drain point including coupling , elbow etc. as required. | 35.00 | Mtrs |  | 120.00 | 4200.00 | 260.00 | 9100.00 | 475.00 | 16625.00 | 4200.00 | Awasthi Electric Works
33.00 | Supply, installation, testing and commissioning of wall mounting type, single phase, automatic line voltage stabilzer, suitable operation on 170 volts to 270 volts AC input, 200 volts to 240 volts AC output, single phase, 50Hz AC power supply with built in time delay, high voltage cut off, and low voltage cut off at 145 volts and input/output/trip indications and suitable for application of 2 TR Air conditioning unit etc. as required. | 7.00 | Each |  | 5500.00 | 38500.00 | 8500.00 | 59500.00 | 6500.00 | 45500.00 | 38500.00 | Awasthi Electric Works
34.00 | Supply of XLPE insulated and PVC sheathed aluminium conductor armoured cable of 1 KV grade conforming to IS : 7098 with upto date amendments etc.,as required.of following sizes : a) 3.5C X 300 Sq.mm | 400.00 | Mtrs |  | 1550.00 | 620000.00 | 1475.00 | 590000.00 | 1525.00 | 610000.00 | 590000.00 | Nabalok Das
35.00 | Supply of PVC insulated and PVC sheathed Copper conductor armoured cable of 1 KV grade conforming to IS : 1554 (Par : -I)/1988 with upto date amendments etc.,as required.of following sizes :2C x 1.5 sqmm | 50.00 | Mtrs |  | 90.00 | 4500.00 | 130.00 | 6500.00 | 105.00 | 5250.00 | 4500.00 | Awasthi Electric Works
36.00 | Supplying and fixing of 32mm dia G.I. pipe (medium class) for installation of street light fiting including bending the pipe to the required shape and clamp arrangement complete as required.(length of 1 mtr) | 7.00 | Each |  | 850.00 | 5950.00 | 1800.00 | 12600.00 | 850.00 | 5950.00 | 5950.00 | SAURABH ENTERPRISES, Awasthi Electric Works
37.00 | Supplying and Laying of following size HDPE pipe ISI marked along with all accessories like socket, bend, couplers etc. conforming to IS 4984, PE 80, PN 6 complete with fitting and cutting, jointing etc.direct in ground (75 cm below ground level) including excavation and refilling the trench but excluding sand cushioning and protective covering etc., complete as required (a) 125 mm dia | 350.00 | Mtrs |  | 550.00 | 192500.00 | 174.00 | 60900.00 | 550.00 | 192500.00 | 60900.00 | Nabalok Das
38.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/ HUME/ METAL/HDPE pipe as required. (a) Above 185 sq. mm and upto 400sqmm | 35.00 | Mtrs |  | 125.00 | 4375.00 | 300.00 | 10500.00 | 115.00 | 4025.00 | 4025.00 | SAURABH ENTERPRISES
39.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in masonnary open duct etc as required. (a) Above 185 sq. mm and upto 400sqmm | 15.00 | Mtrs |  | 100.00 | 1500.00 | 100.00 | 1500.00 | 95.00 | 1425.00 | 1425.00 | SAURABH ENTERPRISES
40.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. (a) 3.5 x 300 sqmm cable | 6.00 | SET |  | 1250.00 | 7500.00 | 700.00 | 4200.00 | 650.00 | 3900.00 | 3900.00 | SAURABH ENTERPRISES
41.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. (a) 4X16 Sqmm (28mm) + 2X6Sqmm(19mm) | 4.00 | SET |  | 350.00 | 1400.00 | 250.00 | 1000.00 | 150.00 | 600.00 | 600.00 | SAURABH ENTERPRISES
42.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on wall surface as required.Upto 35 sq. mm (clamped with 1mm thick saddle) | 180.00 | SET |  | 80.00 | 14400.00 | 160.00 | 28800.00 | 95.00 | 17100.00 | 14400.00 | Awasthi Electric Works
43.00 | Earthing with G.I. earth plate 600 mm X 600 mm X 6 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of atleast 2.7 metre long etc. with charcoal/ coke and salt as required. | 2.00 | Mtrs |  | 14000.00 | 28000.00 | 8700.00 | 17400.00 | 12500.00 | 25000.00 | 17400.00 | Nabalok Das
44.00 | Supplying and laying 25 mm X 5 mm GI strip at 0.50 meter below ground as strip earth electrode, including connection/ terminating with nut, bolt, spring, washer etc. as required. (Jointing shall be done by overlapping and with 2 sets of brass nut bolt & spring washer spaced at 50 mm) | 20.00 | SET |  | 300.00 | 6000.00 | 1500.00 | 30000.00 | 250.00 | 5000.00 | 5000.00 | SAURABH ENTERPRISES
45.00 | Providing and fixing 25 mm X 5 mm GI strip in 40 mm dia G.I. pipe from earth electrode including connection with brass nut, bolt, spring, washer excavation and re-filling etc. as required. | 20.00 | Mtrs |  | 600.00 | 12000.00 | 1200.00 | 24000.00 | 650.00 | 13000.00 | 12000.00 | Awasthi Electric Works
46.00 | Providing and fixing 25 mm X 5 mm GI strip on surface or in recess for connections etc. as required. | 20.00 | Mtrs |  | 225.00 | 4500.00 | 350.00 | 7000.00 | 425.00 | 8500.00 | 4500.00 | Awasthi Electric Works
47.00 | Supply and Installation of MOV based 40KA Surge Protection module for output(Two Phase, Incoming & Outgoing) with Rated voltage MCOV 5000V in the fire proof metal enclosure. | 1.00 | Mtrs |  | 70000.00 | 70000.00 | 35000.00 | 35000.00 | 45000.00 | 45000.00 | 35000.00 | Nabalok Das
48.00 | SITC of out door feeder pillar made out of 14 SWG MS sheet,of size 600mm x450mm x300mm, having four frangible legs of suitable length each of angle iron 35mm X 35mm x 5 mm size ( leg shound be 300 mm above from floor level) , TPN aluminum busbars of rating 200A, painting and writing i/c danger plate, fixing with cement concrete (1:2:4) and also making the cement concrete bed (1:4:8) of radius one meter around the feeder pillar etc. as per site requirement. | 2.00 | Each |  | 24000.00 | 48000.00 | 24000.00 | 48000.00 | 15500.00 | 31000.00 | 31000.00 | SAURABH ENTERPRISES
49.00 | SITC of Dust & vermin proof Outdoor type double door Floor Mounted panel Ingress protection of IP54 of suitable size on angel iron frame/ flate iron frame work and to withstand rough usage. The panel shall be fabricated with 14 SWG MS sheet complete with all accessories suitable angle/ channels frame, gland plates, painting etc. including supplying and fixing of following accessories and making inter connection, earth connection, neutral link, etc.as per the drawing and site requirement. The panel should supplied with suitable aerosol based Fire Protection System as per OEM.Incomer200A, MCCB, 4P, 35-37 KA (Icu= 100% Ics) with extended rotary handle and spreaders - 02 Nos.Multi function meter (Shows Voltage, Current & Frequency) with 3 line LCD Display of size 96 x 96 mm. - 02 Nos.Indication Lamp R, Y & B (LED Type) -02 setBuscoupler 200A, MCCB, 4P, 35-37 KA (Icu= 100% Ics) with extended rotary handle and spreaders - 01 No.Outgoing63A, MCCB, 4P, 25 KA (Icu= 100% Ics) with extended rotary handle - 06 Nos.Indication Lamp R & G (LED type) - 06 SetOther300A Copper busbar, 3 Phase & 100% NeutralMechanical key lock (3 Lock +2 Key)Necessary CT & Control wiring arrangement Power terminal and other accessoriesTPN automatic change over switch with controller, 200A , 415V,50Hz, 4 Pole etc as per site requirement- 01 NosThree Phase Surge Protection Device (SPD) having nominal dischage 100kA (8/20 us) Maximum discharge current 15kA (10/350 us),Peak 150kA (8/20 us) Lightning impulse value current 40kA (10/350 us) with protection level of 1.9kV including all accessories for installing on the mains power entry point at the busbar shall be of modular type. -02 Nos. | 1.00 | SET |  | 367500.00 | 367500.00 | 360000.00 | 360000.00 | 364099.00 | 364099.00 | 360000.00 | Nabalok Das
50.00 | SITC of TPN automatic change over switch with current limiter , 80A /63A , 415V,50Hz, etc as per site requirement. | 1.00 | Each |  | 27500.00 | 27500.00 | 45000.00 | 45000.00 | 45000.00 | 45000.00 | 27500.00 | Awasthi Electric Works
51.00 | Supplying, installation, testing & commissioning of smoke detector with builtin LED and mounting base complete with all connections etc. as required. | 13.00 | Each |  | 1000.00 | 13000.00 | 2300.00 | 29900.00 | 4000.00 | 52000.00 | 13000.00 | Awasthi Electric Works
52.00 | Supplying, installation, testing & commissioning of heat detector with rate of rise cum fixed temperature (dual thermistor) type with mounting base complete with all connection etc. as required. | 2.00 | Each |  | 1250.00 | 2500.00 | 5500.00 | 11000.00 | 6500.00 | 13000.00 | 2500.00 | Awasthi Electric Works
53.00 | Supplying, installation, testing & commissioning of Conventional Type Main Control and Indicating panel made out of 16 SWG MS sheet to accommodate the following items duly powder coated in approved colour with louvers for ventilation, locking arrangement, audio and visual indication for fire alarm and auto dialer system (working on IP based system), monitoring system including connections, interconnections etc complete as required. Atleast 4 zone panel for fire alarm system 100 watt amplifier racks suitable for operation on 230V AC/24V DC supply conforming to IEC-268-3 complete with all accessories as required | 1.00 | NO |  | 1800.00 | 1800.00 | 65000.00 | 65000.00 | 55000.00 | 55000.00 | 1800.00 | Awasthi Electric Works
54.00 | SITC of conventional flasher sounder unit | 1.00 | NO |  | 7250.00 | 7250.00 | 6500.00 | 6500.00 | 5000.00 | 5000.00 | 5000.00 | SAURABH ENTERPRISES
55.00 | Supplying & laying of 2x1.5 sqmm fire alarm armoured cable, 600/1000V rated with annealed copper conductor having XLPE insulation, steel wire armouring & FRLS outer sheath complete as required. | 250.00 | Mtrs |  | 130.00 | 32500.00 | 250.00 | 62500.00 | 120.00 | 30000.00 | 30000.00 | SAURABH ENTERPRISES
56.00 | SITC of NOVAC 1230 clean agent gas | 60.00 | NO |  | 2150.00 | 129000.00 | 1020.00 | 61200.00 | 2500.00 | 150000.00 | 61200.00 | Nabalok Das
57.00 | SITC of 80 litre cylinder complete with valve, pipe , mounting accessories, control valve with manual and electrical operated level and solenoid. | 1.00 | NO |  | 87000.00 | 87000.00 | 34000.00 | 34000.00 | 290000.00 | 290000.00 | 34000.00 | Nabalok Das
58.00 | SITC of seamless pipe ASTM A-106(Sch 40) complete with all fittings painting with one coat of red oxide and 2 coats of enamel paint; piping to be fixed on ceiling with MS suspended supports, clamps anchor fastners, cutting chases / holes in valve ceiling and making good the same as required for the suitable sizes. | 1.00 | KG |  | 7500.00 | 7500.00 | 1500.00 | 1500.00 | 5000.00 | 5000.00 | 1500.00 | Nabalok Das
59.00 | SITC of manual abort / release station | 2.00 | NO |  | 7500.00 | 15000.00 | 32000.00 | 64000.00 | 6500.00 | 13000.00 | 13000.00 | SAURABH ENTERPRISES
60.00 | SITC of 1.5 hp Pressure booster pump (25X25mm) for existing water supply, working on single phase power supply alongwith uPVC pipes (apx 200m, 25mm) and necessary fittings | 1.00 | JOB |  | 18000.00 | 18000.00 | 38000.00 | 38000.00 | 25000.00 | 25000.00 | 18000.00 | Awasthi Electric Works
61.00 | Design , Supply, installation ,testing & commisioning of cubical type panel made out of CRCA sheet of 2 mm thick,totally enclosed IP 42 free standing floor mounting for operation on 3 phase and neutral 415 V ,50 Hz AC supply with incomer of 63 Amp MCCB and metering consisting of CTs with protection fuse suitable for the opreration 4 nos. of AC of 2 Tr to 3 Tr with provision of timer and contactor of suitable ratings for sequence logic to operate any two at a time but any A/C should not run more than 6 hours with push button with element and automanual switch with each AC. Metering :1 No. 3 phase digital ameter with 3 Nos. CT 5 VA class 1.0 and control cicuit wiring with HRC control Fuse complete as required and 1 No. 3 phase Voltmeter. Incoming: 63 A MCCB 1 no, indicating light LED type 3 Nos. Outgoing: 20 A DP MCB, C series 4 Nos. | 1.00 | Job |  | 105000.00 | 105000.00 | 60000.00 | 60000.00 | 50000.00 | 50000.00 | 50000.00 | SAURABH ENTERPRISES
| Total in Figures |  |  |  |  | 2697140.00 |  | 2708788.00 |  | 3112700.00
Lowest Amount Quoted BY: Awasthi Electric Works(2697140.00)

## BOQ Summary
BOQ Summary Details Tender Title: Shifting of DVOR at LBSI Airport, Varanasi, SH- Electrical Works Tender ID: 2025_AAI_244584_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Awasthi Electric Works (BID ID -897604) | 2697140.00 | L1
| 2 | Nabalok Das (BID ID -897482) | 2708788.00 | L2
| 3 | SAURABH ENTERPRISES (BID ID -897062) | 3112700.00 | L3