## BoQ1
Government eProcurement System Created By: Vikas Kumar Tripathi Created Date/Time: 10-Oct-2025 04:22 PM Tender Title: Procurement and Replacement of LT Cables of A and B Block at RGB New Delhi. Tender ID: 2025_AAI_245763_1
Tender Inviting Authority: Senior Manager . (Engg. – Elect)- IMU, AAI, CHQ, R.G. Bhawan, New Delhi-110003
Name of Work: Procurement and Replacement of LT Cables of A&B Block at Rajiv Gandhi Bhawan, New Delhi.
Tender ID:- (2025_AAI_245763_1)
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | HIMALAYA GENERATORS (GSTN-09AEDPA0988G1ZL) BID ID -899565 |  | S.L. ELECTROMECH PVT. LTD. (GSTN-07AAACR1317E2ZW) BID ID -900944 |  | Master Electric Store (GSTN-07AAHPB6825H1ZU) BID ID -901482 |  | Awasthi Electric Works (GSTN-09ABAPA1866D1Z5) BID ID -901507 |  | Manish Electricals (GSTN-23ABLPM9012E1ZW) BID ID -901518 |  | ABHISHEK INTEGRATIONS LIMITED (GSTN-NA) BID ID -901589 |  | Virtus Techno (GSTN-NA) BID ID -901028 |  | Krishsons International Engineers And Consultants (I) Pvt. Ltd (GSTN-NA) BID ID -900449 |  | AIR DESIGN SOLUTIONS (GSTN-NA) BID ID -901419
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply of following sizes of XLPE insulated PVC sheathed, aluminium conductor, armoured, power cable of 1.1 KV grade conforming to IS 7098 (Part I), 1988 amended up to date.
1.01 | 3.5C x 35 sq. mm | 350.00 | Mtr. |  | 250.00 | 87500.00 | 320.00 | 112000.00 | 280.00 | 98000.00 | 210.00 | 73500.00 | 212.00 | 74200.00 | 216.00 | 75600.00 | 194.06 | 67921.00 | 210.00 | 73500.00 | 244.00 | 85400.00 | 67921.00 | Virtus Techno
1.02 | 3.5C x 120 sq. mm | 450.00 | Mtr. |  | 650.00 | 292500.00 | 732.00 | 329400.00 | 745.00 | 335250.00 | 610.00 | 274500.00 | 619.00 | 278550.00 | 620.00 | 279000.00 | 556.58 | 250461.00 | 610.00 | 274500.00 | 697.00 | 313650.00 | 250461.00 | Virtus Techno
1.03 | 3.5C x 240 sq. mm | 1900.00 | Mtr. |  | 1150.00 | 2185000.00 | 1345.00 | 2555500.00 | 1454.00 | 2762600.00 | 1140.00 | 2166000.00 | 1155.00 | 2194500.00 | 1174.00 | 2230600.00 | 1048.72 | 1992568.00 | 1178.00 | 2238200.00 | 1314.00 | 2496600.00 | 1992568.00 | Virtus Techno
2.00 | Supply of following sizes of PVC insulated, copper conductor, power cable of 1.1 KV grade conforming to IS 12444:2020 amended up to date.
2.01 | 4C x 4 sq. mm | 750.00 | Mtr. |  | 300.00 | 225000.00 | 227.00 | 170250.00 | 285.00 | 213750.00 | 240.00 | 180000.00 | 276.00 | 207000.00 | 223.00 | 167250.00 | 208.70 | 156525.00 | 200.00 | 150000.00 | 215.00 | 161250.00 | 150000.00 | Krishsons International Engineers And Consultants (I) Pvt. Ltd
2.02 | 4C x 6 sq. mm | 50.00 | Mtr. |  | 500.00 | 25000.00 | 418.00 | 20900.00 | 358.00 | 17900.00 | 350.00 | 17500.00 | 403.00 | 20150.00 | 328.00 | 16400.00 | 320.63 | 16031.50 | 290.00 | 14500.00 | 368.00 | 18400.00 | 14500.00 | Krishsons International Engineers And Consultants (I) Pvt. Ltd
3.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/HUME/METAL pipe as required.
3.01 | upto 35 sqmm | 10.00 | Mtr. |  | 30.00 | 300.00 | 70.00 | 700.00 | 15.00 | 150.00 | 30.00 | 300.00 | 30.00 | 300.00 | 25.00 | 250.00 | 72.00 | 720.00 | 15.00 | 150.00 | 60.00 | 600.00 | 150.00 | Krishsons International Engineers And Consultants (I) Pvt. Ltd, Master Electric Store
3.02 | Above 95 sqmm and upto 185 sqmm. | 50.00 | Mtr. |  | 40.00 | 2000.00 | 90.00 | 4500.00 | 30.00 | 1500.00 | 80.00 | 4000.00 | 50.00 | 2500.00 | 60.00 | 3000.00 | 120.00 | 6000.00 | 30.00 | 1500.00 | 60.00 | 3000.00 | 1500.00 | Krishsons International Engineers And Consultants (I) Pvt. Ltd, Master Electric Store
3.03 | Above 185 sqmm and upto 400 sqmm | 500.00 | Mtr. |  | 50.00 | 25000.00 | 120.00 | 60000.00 | 50.00 | 25000.00 | 130.00 | 65000.00 | 60.00 | 30000.00 | 70.00 | 35000.00 | 120.00 | 60000.00 | 50.00 | 25000.00 | 180.00 | 90000.00 | 25000.00 | HIMALAYA GENERATORS, Krishsons International Engineers And Consultants (I) Pvt. Ltd, Master Electric Store
4.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing masonry open duct as required.
4.01 | upto 35 sqmm | 10.00 | Mtr. |  | 30.00 | 300.00 | 70.00 | 700.00 | 15.00 | 150.00 | 30.00 | 300.00 | 30.00 | 300.00 | 25.00 | 250.00 | 72.00 | 720.00 | 10.00 | 100.00 | 60.00 | 600.00 | 100.00 | Krishsons International Engineers And Consultants (I) Pvt. Ltd
4.02 | Above 95 sqmm and upto 185 sqmm | 300.00 | Mtr. |  | 40.00 | 12000.00 | 90.00 | 27000.00 | 20.00 | 6000.00 | 50.00 | 15000.00 | 50.00 | 15000.00 | 60.00 | 18000.00 | 96.00 | 28800.00 | 25.00 | 7500.00 | 150.00 | 45000.00 | 6000.00 | Master Electric Store
4.03 | Above 185 sqmm and upto 400 sqmm | 300.00 | Mtr. |  | 50.00 | 15000.00 | 120.00 | 36000.00 | 25.00 | 7500.00 | 100.00 | 30000.00 | 60.00 | 18000.00 | 70.00 | 21000.00 | 120.00 | 36000.00 | 40.00 | 12000.00 | 180.00 | 54000.00 | 7500.00 | Master Electric Store
5.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on wall surface/cable tray as required.
5.01 | upto 35 sqmm (clamped with 1mm thick saddle) | 300.00 | Mtr. |  | 30.00 | 9000.00 | 70.00 | 21000.00 | 20.00 | 6000.00 | 60.00 | 18000.00 | 60.00 | 18000.00 | 25.00 | 7500.00 | 96.00 | 28800.00 | 20.00 | 6000.00 | 84.00 | 25200.00 | 6000.00 | Krishsons International Engineers And Consultants (I) Pvt. Ltd, Master Electric Store
5.02 | Above 95 sqmm and upto 185 sqmm (clamped with 25/40x3mm MS flat clamp) | 200.00 | Mtr. |  | 40.00 | 8000.00 | 90.00 | 18000.00 | 60.00 | 12000.00 | 150.00 | 30000.00 | 105.00 | 21000.00 | 60.00 | 12000.00 | 132.00 | 26400.00 | 33.00 | 6600.00 | 150.00 | 30000.00 | 6600.00 | Krishsons International Engineers And Consultants (I) Pvt. Ltd
5.03 | Above 185 sqmm and upto 400 sqmm (clamped with 40x3mm MS flat clamp) | 950.00 | Mtr. |  | 50.00 | 47500.00 | 120.00 | 114000.00 | 70.00 | 66500.00 | 230.00 | 218500.00 | 150.00 | 142500.00 | 70.00 | 66500.00 | 144.00 | 136800.00 | 40.00 | 38000.00 | 210.00 | 199500.00 | 38000.00 | Krishsons International Engineers And Consultants (I) Pvt. Ltd
6.00 | Supplying and making end termination with brass double compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
6.01 | 4 x 35 sqmm (32mm) | 15.00 | Each |  | 500.00 | 7500.00 | 430.00 | 6450.00 | 1000.00 | 15000.00 | 400.00 | 6000.00 | 400.00 | 6000.00 | 495.00 | 7425.00 | 1020.00 | 15300.00 | 200.00 | 3000.00 | 594.00 | 8910.00 | 3000.00 | Krishsons International Engineers And Consultants (I) Pvt. Ltd
6.02 | 3.5 x 120 sq. mm (45mm) | 10.00 | Each |  | 600.00 | 6000.00 | 678.00 | 6780.00 | 1500.00 | 15000.00 | 800.00 | 8000.00 | 900.00 | 9000.00 | 1210.00 | 12100.00 | 1680.00 | 16800.00 | 300.00 | 3000.00 | 1411.00 | 14110.00 | 3000.00 | Krishsons International Engineers And Consultants (I) Pvt. Ltd
6.03 | 3.5 x 240 sq. mm (62mm) | 30.00 | Each |  | 1000.00 | 30000.00 | 1120.00 | 33600.00 | 2900.00 | 87000.00 | 1150.00 | 34500.00 | 1200.00 | 36000.00 | 1650.00 | 49500.00 | 2160.00 | 64800.00 | 500.00 | 15000.00 | 2305.00 | 69150.00 | 15000.00 | Krishsons International Engineers And Consultants (I) Pvt. Ltd
7.00 | Supplying and making end termination with copper lugs for following size of PVC insulated and PVC sheathed copper conductor cable of 1.1 KV grade as required.
7.01 | 4C x 4 sq. mm | 110.00 | Each |  | 200.00 | 22000.00 | 706.00 | 77660.00 | 5.00 | 550.00 | 250.00 | 27500.00 | 250.00 | 27500.00 | 44.00 | 4840.00 | 420.00 | 46200.00 | 70.00 | 7700.00 | 343.00 | 37730.00 | 550.00 | Master Electric Store
7.02 | 4 x 6 sq. mm | 10.00 | Each |  | 250.00 | 2500.00 | 906.00 | 9060.00 | 5.00 | 50.00 | 250.00 | 2500.00 | 350.00 | 3500.00 | 48.00 | 480.00 | 480.00 | 4800.00 | 70.00 | 700.00 | 360.00 | 3600.00 | 50.00 | Master Electric Store
8.00 | SITC of floor mounted, outdoor type, IP-54 rated factory built sheet steel enclosed construction LT PANEL (PTTA) compartmentalized design (Form 3B) and covered with CRCA sheet steel of 2mm thick for doors/covers, 3mm thick for gland plates, cleaning & finishing complete with seven tank process for powder coating in approved shade with short circuit with stand capacity of 25KA for 1sec., bus bar and inter-connection with solid aluminium strips, neutral links. Cable alleys, cable gland plates in two half, danger notice plates, etc. and mounted with the following switch gears as per technical specifications etc. complete as required. Earthing stud and detachable gland plate at bottom/top and rubber gasket for doors with locking arrangement. including Top Canopy for rain Protection, and providing iron base frame of size 50x50x5mm with height 750MM cable entry provision etc complete as required. 1) All MCCBs of current rating 250 Amps and above shall be provided with microprocessor based releases and those of rating below 250 Amps shall be provided with thermal magnetic releases or as specified in BOQ. Breaker Release shall provide protection against O/L, S/C & E/F. 2) All MCCBs shall be having Ics = 100% Icu 3) All MCCBs shall be provided with front rotary handle and spreader links. (A) INCOMER 200Amp FP Moulded Case Circuit Breaker with thermal magnetic releases of (25kA Ics Value) complete-1 Nos. 0 to 500 Volt digital voltmeter 96mm x 96mm with selector switch. Suitable Size digital ammeter 96mm x 96mm with selector switch & CT's. of suitable ratio. 1 Set of Phase indicating lamps with Single Pole MCB. 1 Set of ON / OFF indicating lamps with Single Pole MCB. Intelligent digital multi function meter of class 0.5 to read V, A, F, KVA, KW, KVAR, KWH, KVAH, PF, Hz etc. with communication facility (RS 485 port), THD and individual order harmonics upto 31st Order. LED/ LCD display with required Nos CTs of suitable ratio of 15 VA & class 0.5 including control circuit wiring with 2 Amp protection MCB. (B) BUSBARS TPN Aluminium busbars of minimum of 250 Amps capacity having 100% neutral bus as that of phase with heat shrinkable coloured sleeves. (C) OUTGOING 20 Amp FP MCB type-C -15 Nos. 32 Amp FP MCB type-C -01 Nos. 100 Amp FP Moulded Case Circuit Breaker type of (25kA Ics Value) -01 Nos. | 2.00 | Each |  | 175000.00 | 350000.00 | 350000.00 | 700000.00 | 215400.00 | 430800.00 | 160000.00 | 320000.00 | 210000.00 | 420000.00 | 282590.00 | 565180.00 | 276096.00 | 552192.00 | 114350.00 | 228700.00 | 103200.00 | 206400.00 | 206400.00 | AIR DESIGN SOLUTIONS
9.00 | Supplying, Installation, Testing & Commissioning of following size of recessed type wall mounted sheet steel IP 43 double door DB as per IEC 61439-3 with minimum 200 A Copper Busbar for each phase with 02 Neutral bar, 02 Earthbar and Cable ties for Cable management, Fully insulated busbar & shrouded Neutral bars, prefitted masking sheet, powder painted including earthing, complete as required. 1. 8 Way TPN Vertical Type DB with followings 2. INCOMING : 100A 4P MCCB of 25 kA Thermal magnetic with inbuilt protection & Earth fault relay. 3. OUTGOING : 32A TP MCB "C" Curve - 8 Nos. | 2.00 | Each |  | 45000.00 | 90000.00 | 25000.00 | 50000.00 | 18500.00 | 37000.00 | 89000.00 | 178000.00 | 48500.00 | 97000.00 | 55188.00 | 110376.00 | 22200.00 | 44400.00 | 49000.00 | 98000.00 | 36000.00 | 72000.00 | 37000.00 | Master Electric Store
10.00 | Supply and fixing of 4Way-4Pole Metal Enclosure, protective housing unit used to encase MCBs for electrical installations. | 49.00 | Each |  | 750.00 | 36750.00 | 1058.00 | 51842.00 | 1012.00 | 49588.00 | 500.00 | 24500.00 | 496.00 | 24304.00 | 440.00 | 21560.00 | 445.50 | 21829.50 | 440.00 | 21560.00 | 3354.00 | 164346.00 | 21560.00 | Krishsons International Engineers And Consultants (I) Pvt. Ltd, ABHISHEK INTEGRATIONS LIMITED
11.00 | Supplying and fixing of 32A Triple pole and neutral., 240/415 volts, 10 kA, "C" curve, miniature circuit breaker suitable for inductive load in the existing MCB DB complete with connections, testing and commissioning etc. as required. | 49.00 | Each |  | 900.00 | 44100.00 | 1295.00 | 63455.00 | 950.00 | 46550.00 | 850.00 | 41650.00 | 1400.00 | 68600.00 | 1265.00 | 61985.00 | 927.60 | 45452.40 | 860.00 | 42140.00 | 3060.00 | 149940.00 | 41650.00 | Awasthi Electric Works
12.00 | Supplying and installation of 600mm width x 50mm depth x 2mm thickness perforated hot dipped Galvanised Iron cable tray with cover (Galvanisation thickness not less than 50 microns) and perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with G.I suspenders including G.I bolts, nuts & support etc. as required. | 1520.00 | Mtr. |  | 1950.00 | 2964000.00 | 1735.00 | 2637200.00 | 1331.00 | 2023120.00 | 2575.00 | 3914000.00 | 2150.00 | 3268000.00 | 2954.00 | 4490080.00 | 2580.00 | 3921600.00 | 2515.00 | 3822800.00 | 2159.00 | 3281680.00 | 2023120.00 | Master Electric Store
13.00 | Supplying and installation of 600mm width x 50mm depth x 2mm thickness of perforated hot dipped Galvanised Iron cable tray bend with cover (Galvanisation thickness not less than 50 microns) and perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with G.I suspenders including G.I bolts, nuts & support etc. as required. | 50.00 | Each |  | 3000.00 | 150000.00 | 3455.00 | 172750.00 | 1850.00 | 92500.00 | 4900.00 | 245000.00 | 2050.00 | 102500.00 | 5004.00 | 250200.00 | 5040.00 | 252000.00 | 5099.00 | 254950.00 | 3540.00 | 177000.00 | 92500.00 | Master Electric Store
14.00 | Supplying and laying/fixing of DWC pipe of 120mm size as site requirement. | 100.00 | Mtr. |  | 200.00 | 20000.00 | 290.00 | 29000.00 | 225.00 | 22500.00 | 290.00 | 29000.00 | 350.00 | 35000.00 | 385.00 | 38500.00 | 216.00 | 21600.00 | 180.00 | 18000.00 | 538.00 | 53800.00 | 18000.00 | Krishsons International Engineers And Consultants (I) Pvt. Ltd
15.00 | Supply and Installation of DLP plastic U-PVC trunking of following items i/c accessories as required.
15.01 | Plastic trunking without cover 105 mm X 50 mm | 200.00 | Mtr. |  | 350.00 | 70000.00 | 706.00 | 141200.00 | 1052.00 | 210400.00 | 1100.00 | 220000.00 | 750.00 | 150000.00 | 613.00 | 122600.00 | 192.00 | 38400.00 | 640.00 | 128000.00 | 733.00 | 146600.00 | 38400.00 | Virtus Techno
15.02 | Plastic trunking cover suitable for 105 mm X 50 mm | 200.00 | Mtr. |  | 200.00 | 40000.00 | 706.00 | 141200.00 | 200.00 | 40000.00 | 300.00 | 60000.00 | 380.00 | 76000.00 | 613.00 | 122600.00 | 96.00 | 19200.00 | 270.00 | 54000.00 | 366.00 | 73200.00 | 19200.00 | Virtus Techno
16.00 | Dismantling of XLPE power cable of 1.1 KV grade of 3.5CX185/3.5CX240sqmm size laid in the existing RCC/HUME/METAL pipe/masonry duct/walls/cable trays and submit the cable with proper dressing at AAI store as per direction of Engineer-In-Charge. | 1900.00 | Each |  | 50.00 | 95000.00 | 80.00 | 152000.00 | 125.00 | 237500.00 | 70.00 | 133000.00 | 50.00 | 95000.00 | 35.00 | 66500.00 | 60.00 | 114000.00 | 40.00 | 76000.00 | 90.00 | 171000.00 | 66500.00 | ABHISHEK INTEGRATIONS LIMITED
| Total in Figures |  |  |  |  | 6861950.00 |  | 7742147.00 |  | 6859858.00 |  | 8336250.00 |  | 7440404.00 |  | 8856276.00 |  | 7986320.40 |  | 7621100.00 |  | 8152666.00
Lowest Amount Quoted BY: Master Electric Store(6859858.00)

## BOQ Summary
BOQ Summary Details Tender Title: Procurement and Replacement of LT Cables of A and B Block at RGB New Delhi. Tender ID: 2025_AAI_245763_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Master Electric Store (BID ID -901482) | 6859858.00 | L1
| 2 | HIMALAYA GENERATORS (BID ID -899565) | 6861950.00 | L2
| 3 | Manish Electricals (BID ID -901518) | 7440404.00 | L3
| 4 | Krishsons International Engineers And Consultants (I) Pvt. Ltd (BID ID -900449) | 7621100.00 | L4
| 5 | S.L. ELECTROMECH PVT. LTD. (BID ID -900944) | 7742147.00 | L5
| 6 | Virtus Techno (BID ID -901028) | 7986320.40 | L6
| 7 | AIR DESIGN SOLUTIONS (BID ID -901419) | 8152666.00 | L7
| 8 | Awasthi Electric Works (BID ID -901507) | 8336250.00 | L8
| 9 | ABHISHEK INTEGRATIONS LIMITED (BID ID -901589) | 8856276.00 | L9