## BoQ1
Government eProcurement System Created By: Amit Kumar Layek Created Date/Time: 16-Oct-2025 10:42 AM Tender Title: Design Supply Installation Testing and Commissioning of On grid 60 KWp Rooftop Solar Plant at CISF Barrack in AAI Residential Colony M B B Airport Agartala Tender ID: 2025_AAI_245933_1
Tender Inviting Authority: AGM (E-E)
Name of Work:Design, Supply, Installation, Testing and Commissioning of Ongrid 60 KWp Rooftop Solar Plant at CISF Barrack in AAI Residential Colony, M.B.B. Airport, Agartala.
Contract No: 2025_AAI_245933_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Swastik Enterprises (GSTN-19ADPPB7776G1Z1) BID ID -898192 |  | MATESHWARI ENTERPRISES (GSTN-08AQUPJ7022P1Z2) BID ID -898649 |  | Agni Green Power Ltd. (GSTN-19AACCA2122Q1ZL) BID ID -893595 |  | MADHAV SOLAR ENERGY LIMITED (GSTN-NA) BID ID -900081 |  | Variant Infratech Private Limited (GSTN-NA) BID ID -899630 |  | Aesthetik Renewables Private Limited (GSTN-NA) BID ID -898072 |  | Virtus Techno (GSTN-NA) BID ID -900051 |  | ILIOS TECHNOLOGY (GSTN-NA) BID ID -891730
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Design, Supply, Installation, Testing and Commissioning of ongrid 60 KWp Rooftop Solar Photo voltaic Power Plant conforming to MNRE specifications as amended, consisting of Mono Crystalline silicon solarcells, netmetering facility, necessary protections, SPDs, DC and AC cables, data / control cables, earthings, safety system for reverse power protection , water cleaning system for cleaning of SPV Modules, fixed in anodized aluminium frame complete as required including elevated GI structural support systems of suitable strength to withstand the speed for the wind zone of the location with following components complete in all respect as per site conditions.Glint & Glare Hazard Analysis and submission of report to AAI is also in the scope of work. a) Solar Photo voltaic Module of minimum capacity 540Wp or above, manufactured in India,having RF identification tag, conforming to IS14286/IEC61215,IS/IEC61730-Part-1,IS/IEC61730-Part-2 ammended up to datec. Solar Photovoltaic Module conversion efficiency shall not be less than 16.5%. PV modules used in solar power plants / systems must be warranted for their output peak watt capacity, which should not be less than 90% at the end of 10years and 80% at the end of 25 years. b) Grid interactive Power Conditioning Unit (PCU) of 350-800 VDC Input voltage range and 400VAC, threephase, 4wire, 50Hz+/-2.5Hz, output voltage suitable to generate AC Power with efficiency not less than 97%, total harmonic distortion less than 3% and suitable for ambient temperature from 0 to 50 degree C.The PCU shall adjust the voltage and frequency level to suit the Grid Voltage Frequency. c) Data Monitoring System complete with all accessories. d) Fixing of Array junction box & Main junction box with IP65 protection and termination arrangement for incoming and outgoing cable along with glands, lugs and other accessories etc. as required. e) Lightning and surge voltage protection. f) Connections & Interconnections by supplying & fixing required size XLPE insulated copper conductor 1.1 kV grade armoured power and control cables between solar modules, main power cable to grid supply PCU unit along with supplying & fixing of necessary channel /conduit lugs and other accessories etc. as required. | 1.00 | Job | 100.00 | 2176350.00 | 2176350.00 | 3000000.00 | 3000000.00 | 2825425.00 | 2825425.00 | 4622000.00 | 4622000.00 | 3189500.00 | 3189500.00 | 3331062.00 | 3331062.00 | 3540000.00 | 3540000.00 | 2215200.00 | 2215200.00 | 2176350.00 | Swastik Enterprises
2.10 | Comprehensive Maintenace (After defect liability period of two years) of ongrid 60 KWp Rooftop Solar Photo voltaic Power Plant including all associated systems/acessories complete taken as part of SITC in item no. 1 of various makes to ensure serviceability and unintrupted smooth operation alongwith providing & replacement of faulty components, all types of repairing works, attending breakdown along with supply of required spares, consumables, cleaning, including providing manpower for maintenan including monthly visit of qualified workmen of Agency for preventive maintenenece complete in all respect as per OEM stadard practice. For first Year | 12.00 | Months | 100.00 | 2800.00 | 33600.00 | 8000.00 | 96000.00 | 2805.00 | 33660.00 | 30000.00 | 360000.00 | 5000.00 | 60000.00 | 7104.00 | 85248.00 | 12500.00 | 150000.00 | 4500.00 | 54000.00 | 33600.00 | Swastik Enterprises
2.20 | For Second Year | 12.00 | Months | 10.00 | 2800.00 | 33600.00 | 8000.00 | 96000.00 | 3085.00 | 37020.00 | 31666.00 | 379992.00 | 5000.00 | 60000.00 | 7104.00 | 85248.00 | 14000.00 | 168000.00 | 5000.00 | 60000.00 | 33600.00 | Swastik Enterprises
2.30 | For Third Year | 12.00 | Months | 10.00 | 2800.00 | 33600.00 | 8000.00 | 96000.00 | 3394.00 | 40728.00 | 33334.00 | 400008.00 | 5000.00 | 60000.00 | 7104.00 | 85248.00 | 16500.00 | 198000.00 | 5500.00 | 66000.00 | 33600.00 | Swastik Enterprises
2.40 | For Fourth Year | 12.00 | Months | 10.00 | 2800.00 | 33600.00 | 8000.00 | 96000.00 | 3735.00 | 44820.00 | 35000.00 | 420000.00 | 5000.00 | 60000.00 | 7104.00 | 85248.00 | 18000.00 | 216000.00 | 6000.00 | 72000.00 | 33600.00 | Swastik Enterprises
2.50 | For Fifth Year | 12.00 | Months | 10.00 | 2800.00 | 33600.00 | 8000.00 | 96000.00 | 4105.00 | 49260.00 | 36666.00 | 439992.00 | 5000.00 | 60000.00 | 7104.00 | 85248.00 | 19500.00 | 234000.00 | 6500.00 | 78000.00 | 33600.00 | Swastik Enterprises
| Total in Figures |  |  |  |  | 2344350.00 |  | 3480000.00 |  | 3030913.00 |  | 6621992.00 |  | 3489500.00 |  | 3757302.00 |  | 4506000.00 |  | 2545200.00
Lowest Amount Quoted BY: Swastik Enterprises(2344350.00)

## BOQ Summary
BOQ Summary Details Tender Title: Design Supply Installation Testing and Commissioning of On grid 60 KWp Rooftop Solar Plant at CISF Barrack in AAI Residential Colony M B B Airport Agartala Tender ID: 2025_AAI_245933_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Swastik Enterprises (BID ID -898192) | 2344350.00 | L1
| 2 | ILIOS TECHNOLOGY (BID ID -891730) | 2545200.00 | L2
| 3 | Agni Green Power Ltd. (BID ID -893595) | 3030913.00 | L3
| 4 | MATESHWARI ENTERPRISES (BID ID -898649) | 3480000.00 | L4
| 5 | Variant Infratech Private Limited (BID ID -899630) | 3489500.00 | L5
| 6 | Aesthetik Renewables Private Limited (BID ID -898072) | 3757302.00 | L6
| 7 | Virtus Techno (BID ID -900051) | 4506000.00 | L7
| 8 | MADHAV SOLAR ENERGY LIMITED (BID ID -900081) | 6621992.00 | L8