## BoQ1
Government eProcurement System Created By: ARUN KUMAR K Created Date/Time: 29-Oct-2025 01:21 PM Tender Title: Provision of Standby LT Panel and allied works at ATS Complex, KIA, Bangalore Tender ID: 2025_AAI_246097_1
Tender Inviting Authority: Asst.General Manager (Engg. – Electrical), AAI, ATS Complex, Alpha-1, Kempegowda International Airport, Bengaluru
Name of work : Provision of Standby LT Panel and allied works at ATS Complex, KIA, Bengalore.
Contract No: 2025_AAI_246097_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | AKEY ELECTRO TECHNIQUES (GSTN-29AAHFA1063A1Z0) BID ID -909821 |  | Awasthi Electric Works (GSTN-09ABAPA1866D1Z5) BID ID -910113 |  | SARASWAT ENGINEERING SERVICES (GSTN-27AAZFS6239C1ZO) BID ID -910131 |  | DEEPAKELECTRICALS (GSTN-33ALUPD3531C1ZI) BID ID -910190 |  | KALKI ELECTRICALS (GSTN-29AGGPD2370J1ZE) BID ID -910222 |  | Virtus Techno (GSTN-NA) BID ID -910133 |  | RAMESH ELECTRICALS (GSTN-NA) BID ID -909746 |  | Krishsons International Engineers And Consultants (I) Pvt. Ltd (GSTN-NA) BID ID -909256
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | SH I: SITC OF LT PANEL AND ASSOCIATED WORKS Design, Fabrication, Supply, Installation, Testing and Commissioning of Cubicle type LT Panel (TTA Type) conforming to IEC 61439-1&2 and of Form 4b construction, indoor type with IP 42 protection class, suitable for 415V ± 10%, 3 Phase, 4 wire, 50 Hz, AC supply system, fabricated in compartmentalized modular design from CRCA sheet steel of 2mm thick for frame work and covers, 3 mm thick for gland plates i/c cleaning and finishing complete with 7 tank process for powder coating in approved shade, having TPN copper busbars of high conductivity with DMC/SMC busbar supports and shortcircuit withstand capacity as per design subject to minimum 50 kA for 1 sec, bottom base channel of MS section not less than 100mm x 50mm x 5mm thick, fabrication shall be done in transportable sections, entire panel shall have a common Copper earth busbar of size as per IS 3043 subject to a minimum 50mm x 6mm at the rear with 2 nos earth stud, solid/flexible connections from main busbar to switchgears with required size of Copper conductors/busbars and control wiring with 2.5 sqmm PVC insulated copper conductor cable (FRLS), cable alleys, cable gland plates in two half, required auxillary relays/trip alarm contacts, SPDs, Linear Pneumatic Heat Detection Tube suppression system, Hooter with Annunciation, switchgears and accessories as detailed below and as per specifications. INCOMING : (i) 800A, 50kA (Ics=100% Icu rating), Microprocessor based Four Pole MCCB with adjustable Overload, Short Circuit and in-built Earth Fault Protection along with all accessories - 02 Set. (ii) Three phase Digital Multifunction Meter with communication facility along with three nos of CTs of 800/5A, 15 VA, Class 1.0 etc. and control MCB's - 02 set. (iii) Set of LED type indicating lamps for R,Y,B, ON, OFF & TRIP with control MCB's - 02 set (iv) Type 1+2, 80/100kA, Three phase & neutral, Surge Protection Devices (SPDs) with potential-free contacts and suitable rating control MCB/fuse – 02 Sets BUSCOUPLER : (i) 800A, Four Pole MCCB (without protection release) along with all accessories - 01 Set. (ii) Set of LED type indicating lamps for ON & OFF with control MCB's - 02 set MECHANICAL & ELECTRICAL INTERLOCK : Mechanical Interlocking arrangement between incomers and buscoupler with 3 lock and 2 key - 1 set BUSBARS : FP Copper extensible type Bus Bar of Minimum 1000 Amps capacity - 01 Set. OUTGOINGS : (i) 400A, 36kA (Ics=100% Icu rating), Microprocessor based Four Pole MCCB with adjustable Overload, Short Circuit and in-built Earth Fault Protection along with all accessories - 04 Set. (ii) 250A, 36kA (Ics=100% Icu rating), Microprocessor based Four Pole MCCB with adjustable Overload, Short Circuit and In-Built Earth Fault Protection along with all accessories - 06 Set. (iii) Three phase Digital Comprehensive Power & Energy Meter with communication facility, three nos of suitable ratio CTs, 15 VA, Class 1.0 etc. and Control MCB's - 10 set. (iv) Set of LED type indicating lamps for ON, OFF & TRIP with control MCB's - 10 set ADDITIONAL PROVISIONS : (i) Linear Pneumatic Heat Detection Tube suppression system with suitable capacity cylinders along with clean agent (FK-5-1-12), Direct Low Pressure (DLP) assembly with automatic valve, push-in connectors, mounting brackets, end-of-line adapter, low pressure switch for monitoring activation, master control unit, pressure switches, buzzers and electronic hooters, including all necessary accessories and wiring to make the system functional with PESO / BIS / VDS / UL Components (Gas, tube, pressure switch, and end of line) / LPCB approved as per Specification.– 01 Set (ii) Hooter with Annunciation : Common Hooter for annunciation during incoming / outgoing feeder trips and SPD fault including silence/reset push button, indicator lamp, and all necessary accessories - 01 Set (iii) Panel illuminating lamp, Space heater with thermostat and MCB - As required. | 1.00 | Each |  | 1935150.00 | 1935150.00 | 1675000.00 | 1675000.00 | 2272425.00 | 2272425.00 | 1850000.00 | 1850000.00 | 2100000.00 | 2100000.00 | 2409250.00 | 2409250.00 | 1945524.00 | 1945524.00 | 2080000.00 | 2080000.00 | 1675000.00 | Awasthi Electric Works
2.00 | Supply and Installation of Indoor type Busbar Junction Box made out of weather proof powder coated Sheet steel enclosure complete with cable entry provision, earthing terminals etc. The junction box shall be provided with one set (RYBN) of aluminum busbar of following capacity with provision for connecting Aluminium power cables of upto 3.5CX300 Sq.mm size with all accessories etc suitable for wall mounting etc complete as required as per site requirements.
2.10 | 400A | 2.00 | Each |  | 38800.00 | 77600.00 | 35000.00 | 70000.00 | 7639.00 | 15278.00 | 8000.00 | 16000.00 | 20000.00 | 40000.00 | 161000.00 | 322000.00 | 27325.00 | 54650.00 | 18240.00 | 36480.00 | 15278.00 | SARASWAT ENGINEERING SERVICES
2.20 | 200A | 3.00 | Each |  | 18915.00 | 56745.00 | 17000.00 | 51000.00 | 6346.00 | 19038.00 | 5500.00 | 16500.00 | 16000.00 | 48000.00 | 109250.00 | 327750.00 | 15625.00 | 46875.00 | 15480.00 | 46440.00 | 16500.00 | DEEPAKELECTRICALS
3.00 | Supply, Installation, Testing & Commissioning of following capacity of Four Pole Manual Changeover switch in suitable sheet steel enclosure including rotary handle, spreader terminals, provision for cable entry etc. complete as required.
3.10 | 250A | 2.00 | Each |  | 32495.00 | 64990.00 | 18000.00 | 36000.00 | 34081.00 | 68162.00 | 20000.00 | 40000.00 | 32000.00 | 64000.00 | 27173.92 | 54347.85 | 32543.00 | 65086.00 | 32880.00 | 65760.00 | 36000.00 | Awasthi Electric Works
3.20 | 125A | 3.00 | Each |  | 29585.00 | 88755.00 | 13000.00 | 39000.00 | 34081.00 | 102243.00 | 12000.00 | 36000.00 | 24000.00 | 72000.00 | 17770.38 | 53311.12 | 29361.00 | 88083.00 | 44280.00 | 132840.00 | 36000.00 | DEEPAKELECTRICALS
4.00 | SH II : Supply and laying of LT Cables Supplying of following sizes of XLPE insulated and PVC sheathed, steel strip armoured Copper conductor power cable of 1.1 KV grade confirming to IS:7098 (Part-I) of following sizes.
4.10 | 3.5 C x 185 Sq.mm | 144.00 | Mtr |  | 7731.00 | 1113264.00 | 8475.00 | 1220400.00 | 7680.00 | 1105920.00 | 9500.00 | 1368000.00 | 9600.00 | 1382400.00 | 949.99 | 136798.02 | 8452.00 | 1217088.00 | 7920.00 | 1140480.00 | 136798.02 | Virtus Techno
4.20 | 4 C X 10 Sq.mm | 25.00 | Mtr |  | 509.00 | 12725.00 | 550.00 | 13750.00 | 522.00 | 13050.00 | 550.00 | 13750.00 | 600.00 | 15000.00 | 239.84 | 5996.10 | 570.00 | 14250.00 | 488.00 | 12200.00 | 5996.10 | Virtus Techno
5.00 | Supplying of following sizes of XLPE insulated and PVC sheathed, steel strip armoured Aluminium conductor power cable of 1.1 KV grade confirming to IS:7098 (Part-I) of following sizes.
5.10 | 3.5 C x 95 Sq.mm | 165.00 | Mtr |  | 470.00 | 77550.00 | 550.00 | 90750.00 | 478.00 | 78870.00 | 450.00 | 74250.00 | 600.00 | 99000.00 | 511.65 | 84421.67 | 614.00 | 101310.00 | 381.00 | 62865.00 | 62865.00 | Krishsons International Engineers And Consultants (I) Pvt. Ltd
5.20 | 3.5 C x 50 Sqmm | 175.00 | Mtr |  | 267.00 | 46725.00 | 300.00 | 52500.00 | 271.00 | 47425.00 | 350.00 | 61250.00 | 360.00 | 63000.00 | 326.23 | 57090.60 | 357.00 | 62475.00 | 226.00 | 39550.00 | 39550.00 | Krishsons International Engineers And Consultants (I) Pvt. Ltd
5.30 | 3.5 C x 35Sqmm | 15.00 | Mtr |  | 204.00 | 3060.00 | 230.00 | 3450.00 | 206.00 | 3090.00 | 300.00 | 4500.00 | 250.00 | 3750.00 | 255.88 | 3838.12 | 273.00 | 4095.00 | 173.00 | 2595.00 | 2595.00 | Krishsons International Engineers And Consultants (I) Pvt. Ltd
6.00 | Supplying and installing the following size of perforated hot-dipped galvanized iron (GI) cable tray, with perforations not more than 17.5% in convenient sections, joined with connectors, bends, tees etc, duly suspended from the ceiling using MS angle supports/GI suspenders at suitable intervals, including GI bolts, nuts and all required accessories etc., complete as per site requirements.
6.10 | 600 mm width × 50 mm depth × 2.0 mm thickness | 30.00 | Mtr |  | 2910.00 | 87300.00 | 1900.00 | 57000.00 | 2765.00 | 82950.00 | 1800.00 | 54000.00 | 2600.00 | 78000.00 | 1405.01 | 42150.38 | 1050.00 | 31500.00 | 2200.00 | 66000.00 | 31500.00 | RAMESH ELECTRICALS
6.20 | 450 mm width × 50 mm depth × 2.0 mm thickness | 18.00 | Mtr |  | 2134.00 | 38412.00 | 1600.00 | 28800.00 | 2237.00 | 40266.00 | 1200.00 | 21600.00 | 2400.00 | 43200.00 | 1141.09 | 20539.58 | 950.00 | 17100.00 | 1900.00 | 34200.00 | 17100.00 | RAMESH ELECTRICALS
7.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 kV grade of following size in the existing masonry open duct as required.
7.10 | Above 95 sq. mm and upto 185 sq. mm | 47.00 | Mtr |  | 58.00 | 2726.00 | 70.00 | 3290.00 | 181.00 | 8507.00 | 80.00 | 3760.00 | 100.00 | 4700.00 | 135.70 | 6377.90 | 150.00 | 7050.00 | 53.00 | 2491.00 | 2491.00 | Krishsons International Engineers And Consultants (I) Pvt. Ltd
8.00 | Laying and fixing of one number PVC insulated and PVC sheathed /XLPE power cable of 1.1 KV grade of following size on wall surface/existing cable tray as required.
8.10 | Upto 35 sq. mm (clamped with 1mm thick saddle) | 40.00 | Mtr |  | 49.00 | 1960.00 | 60.00 | 2400.00 | 65.00 | 2600.00 | 45.00 | 1800.00 | 100.00 | 4000.00 | 138.00 | 5520.00 | 65.00 | 2600.00 | 30.00 | 1200.00 | 1200.00 | Krishsons International Engineers And Consultants (I) Pvt. Ltd
8.20 | Above 35 sq. mm and upto 95 sq. mm (clamped with 25x3mm MS flat clamp) | 380.00 | Mtr |  | 97.00 | 36860.00 | 125.00 | 47500.00 | 106.00 | 40280.00 | 45.00 | 17100.00 | 140.00 | 53200.00 | 115.00 | 43700.00 | 125.00 | 47500.00 | 60.00 | 22800.00 | 17100.00 | DEEPAKELECTRICALS
8.30 | Above 95 sq. mm and upto 185 sq. mm (clamped with 25/40x3mm MS flat clamp) | 128.00 | Mtr |  | 121.00 | 15488.00 | 150.00 | 19200.00 | 146.00 | 18688.00 | 65.00 | 8320.00 | 200.00 | 25600.00 | 115.00 | 14720.00 | 220.00 | 28160.00 | 80.00 | 10240.00 | 8320.00 | DEEPAKELECTRICALS
9.00 | Supplying and making end termination with brass compression gland and copper lugs for following size of PVC insulated and PVC sheathed / XLPE copper conductor cable of 1.1 KV grade as required. (Note :- Bi-metallic strips to be used wherever required)
9.10 | 3.5C x 185 Sq.mm | 12.00 | Set |  | 3347.00 | 40164.00 | 1600.00 | 19200.00 | 2329.00 | 27948.00 | 850.00 | 10200.00 | 2600.00 | 31200.00 | 1955.00 | 23460.00 | 4555.00 | 54660.00 | 1000.00 | 12000.00 | 10200.00 | DEEPAKELECTRICALS
9.20 | 3.5C x 50 Sq.mm | 5.00 | Set |  | 679.00 | 3395.00 | 450.00 | 2250.00 | 743.00 | 3715.00 | 350.00 | 1750.00 | 660.00 | 3300.00 | 977.50 | 4887.50 | 1050.00 | 5250.00 | 800.00 | 4000.00 | 1750.00 | DEEPAKELECTRICALS
9.30 | 3.5C x 35 Sq.mm | 3.00 | Set |  | 631.00 | 1893.00 | 350.00 | 1050.00 | 553.00 | 1659.00 | 350.00 | 1050.00 | 500.00 | 1500.00 | 862.50 | 2587.50 | 950.00 | 2850.00 | 700.00 | 2100.00 | 1050.00 | Awasthi Electric Works, DEEPAKELECTRICALS
9.40 | 4C X 10 Sq.mm | 2.00 | Set |  | 364.00 | 728.00 | 225.00 | 450.00 | 389.00 | 778.00 | 300.00 | 600.00 | 400.00 | 800.00 | 632.50 | 1265.00 | 600.00 | 1200.00 | 500.00 | 1000.00 | 450.00 | Awasthi Electric Works
10.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. (Note :- Bi-metallic strips to be used wherever required)
10.10 | 3.5C x 185 Sqmm | 4.00 | Set |  | 2231.00 | 8924.00 | 1100.00 | 4400.00 | 1271.00 | 5084.00 | 650.00 | 2600.00 | 2000.00 | 8000.00 | 1495.00 | 5980.00 | 4155.00 | 16620.00 | 600.00 | 2400.00 | 2400.00 | Krishsons International Engineers And Consultants (I) Pvt. Ltd
10.20 | 3.5C x 150 Sqmm | 2.00 | Set |  | 2037.00 | 4074.00 | 850.00 | 1700.00 | 878.00 | 1756.00 | 550.00 | 1100.00 | 1600.00 | 3200.00 | 1265.00 | 2530.00 | 3500.00 | 7000.00 | 500.00 | 1000.00 | 1000.00 | Krishsons International Engineers And Consultants (I) Pvt. Ltd
10.30 | 3.5C x 95 Sqmm | 18.00 | Set |  | 1620.00 | 29160.00 | 700.00 | 12600.00 | 653.00 | 11754.00 | 500.00 | 9000.00 | 1000.00 | 18000.00 | 931.50 | 16767.00 | 1500.00 | 27000.00 | 400.00 | 7200.00 | 7200.00 | Krishsons International Engineers And Consultants (I) Pvt. Ltd
10.40 | 3.5C x 50 Sq.mm | 14.00 | Set |  | 679.00 | 9506.00 | 500.00 | 7000.00 | 519.00 | 7266.00 | 450.00 | 6300.00 | 600.00 | 8400.00 | 690.00 | 9660.00 | 900.00 | 12600.00 | 300.00 | 4200.00 | 4200.00 | Krishsons International Engineers And Consultants (I) Pvt. Ltd
10.50 | 3.5C x 35 Sq.mm | 2.00 | Set |  | 582.00 | 1164.00 | 425.00 | 850.00 | 410.00 | 820.00 | 400.00 | 800.00 | 500.00 | 1000.00 | 575.00 | 1150.00 | 800.00 | 1600.00 | 250.00 | 500.00 | 500.00 | Krishsons International Engineers And Consultants (I) Pvt. Ltd
11.00 | SH III : SITC of DB Supplying and fixing of 8 way Double door, surface/ recess mounting, vertical type, 415 V, TPN MCB distribution board of sheet steel, dust protected, duly powder painted, inclusive of 200 A tinned copper bus bar, common neutral link, earth bar, din bar for mounting MCBs (but without MCBs and incomer) as required | 2.00 | Each |  | 9943.00 | 19886.00 | 12500.00 | 25000.00 | 33707.00 | 67414.00 | 17000.00 | 34000.00 | 6000.00 | 12000.00 | 21965.00 | 43930.00 | 4121.00 | 8242.00 | 4000.00 | 8000.00 | 8000.00 | Krishsons International Engineers And Consultants (I) Pvt. Ltd
12.00 | Supplying and fixing of following rating, 240/415 V, 10 kA, "C" curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required.
12.10 | 6-32A, Single pole | 12.00 | Each |  | 204.00 | 2448.00 | 200.00 | 2400.00 | 211.00 | 2532.00 | 150.00 | 1800.00 | 200.00 | 2400.00 | 341.55 | 4098.60 | 170.00 | 2040.00 | 160.00 | 1920.00 | 1800.00 | DEEPAKELECTRICALS
12.20 | 40A, Triple pole | 12.00 | Each |  | 1334.00 | 16008.00 | 1400.00 | 16800.00 | 1474.00 | 17688.00 | 1200.00 | 14400.00 | 1600.00 | 19200.00 | 1529.50 | 18354.00 | 1430.00 | 17160.00 | 1185.00 | 14220.00 | 14220.00 | Krishsons International Engineers And Consultants (I) Pvt. Ltd
12.30 | 63A, Four Pole | 2.00 | Each |  | 1707.00 | 3414.00 | 1700.00 | 3400.00 | 1869.00 | 3738.00 | 1900.00 | 3800.00 | 1800.00 | 3600.00 | 1880.25 | 3760.50 | 1915.00 | 3830.00 | 1625.00 | 3250.00 | 3250.00 | Krishsons International Engineers And Consultants (I) Pvt. Ltd
13.00 | SH IV: Earthing and Insulation Mats Earthing with copper earth plate 600 mm X 600 mm X 3 mm thick including all accessories and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with charcoal/ coke and salt, excavation and refilling etc complete as required as per specifications. | 2.00 | set |  | 26190.00 | 52380.00 | 24000.00 | 48000.00 | 23053.00 | 46106.00 | 17000.00 | 34000.00 | 32000.00 | 64000.00 | 20470.00 | 40940.00 | 38500.00 | 77000.00 | 18000.00 | 36000.00 | 34000.00 | DEEPAKELECTRICALS
14.00 | Providing and fixing 25 mm X 5 mm copper strip in 40 mm dia G.I. pipe from earth electrode including connection with brass nut, bolt,spring, washer excavation and re-filling etc. as required | 30.00 | Mtr |  | 2008.00 | 60240.00 | 1600.00 | 48000.00 | 1978.00 | 59340.00 | 1500.00 | 45000.00 | 2000.00 | 60000.00 | 1437.50 | 43125.00 | 1920.00 | 57600.00 | 1900.00 | 57000.00 | 43125.00 | Virtus Techno
15.00 | Providing and fixing 25 mm X 5 mm copper strip on surface or in recess for connections etc. as required. | 30.00 | Mtr |  | 1552.00 | 46560.00 | 1280.00 | 38400.00 | 1405.00 | 42150.00 | 1400.00 | 42000.00 | 1700.00 | 51000.00 | 1437.50 | 43125.00 | 1320.00 | 39600.00 | 1500.00 | 45000.00 | 38400.00 | Awasthi Electric Works
16.00 | Supply and fixing 2.0 mm (nominal ± 10%) thick and 1 mtr wide synthetic insulation mat suitable for 3.3 KV grade as per IS: 15652:2006 with upto date amendments along with suitable adhesive / sealing material i/c sealing of all joints and corners as per manufacturer specifications etc. as required. | 30.00 | Sq. Mtr |  | 1455.00 | 43650.00 | 1425.00 | 42750.00 | 911.00 | 27330.00 | 1300.00 | 39000.00 | 1200.00 | 36000.00 | 1150.00 | 34500.00 | 1250.00 | 37500.00 | 650.00 | 19500.00 | 19500.00 | Krishsons International Engineers And Consultants (I) Pvt. Ltd
| Total in Figures |  |  |  |  | 4002904.00 |  | 3684290.00 |  | 4245870.00 |  | 3834230.00 |  | 4419450.00 |  | 3887931.44 |  | 4105098.00 |  | 3975431.00
Lowest Amount Quoted BY: Awasthi Electric Works(3684290.00)

## BOQ Summary
BOQ Summary Details Tender Title: Provision of Standby LT Panel and allied works at ATS Complex, KIA, Bangalore Tender ID: 2025_AAI_246097_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Awasthi Electric Works (BID ID -910113) | 3684290.00 | L1
| 2 | DEEPAKELECTRICALS (BID ID -910190) | 3834230.00 | L2
| 3 | Virtus Techno (BID ID -910133) | 3887931.44 | L3
| 4 | Krishsons International Engineers And Consultants (I) Pvt. Ltd (BID ID -909256) | 3975431.00 | L4
| 5 | AKEY ELECTRO TECHNIQUES (BID ID -909821) | 4002904.00 | L5
| 6 | RAMESH ELECTRICALS (BID ID -909746) | 4105098.00 | L6
| 7 | SARASWAT ENGINEERING SERVICES (BID ID -910131) | 4245870.00 | L7
| 8 | KALKI ELECTRICALS (BID ID -910222) | 4419450.00 | L8