## BoQ1
Government eProcurement System Created By: Vivek Singh Created Date/Time: 13-Nov-2025 12:20 PM Tender Title: Provision of Apron flood lighting, perimeter Security lighting, Boom Barrier and allied works etc at Agra Airport Tender ID: 2025_AAI_246698_1
Tender Inviting Authority: SM (EE), AAI, Agra
Name of Work: Development of New Integrated Civil Enclave at Agra Airport. SH : Provision of Apron flood lighting, perimeter Security lighting, Boom Barrier and allied works etc
Contract No: 2025_AAI_246698_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Master Electric Store (GSTN-07AAHPB6825H1ZU) BID ID -903421 |  | SAURABH ENTERPRISES (GSTN-NA) BID ID -900299 |  | MANKHA ELECTROTECH PRIVATE LIMITED (GSTN-NA) BID ID -903859 |  | Unique Electro Engineers Pvt. Ltd. (GSTN-NA) BID ID -899837
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.01 | Design, supply, erection and commissioing of High mast flood lighting system of 20 mtr nominal height, suitable for wind velocity of 47m/s as per IS-875, with hot dip galvanized mast, having 2 sections and material of construction of S355 grade as per BS EN 10025 (with base plate welded to the bottom sections), complete with luminaires carriage, luminares as per lighting design to meet ICAO standards, head frame, steel wire rope, non corrosive pulley, control gear boxes, electric driven integral power tool, power & control cables etc. as required along with the following, complete as required as per technical specifications including making of necessary foundation as per site conditions and manufacturer's recommenation. a) Luminaires carriage to hold all required LED light fittings for meeting lux requirement in apron area plus two additional light fittings for redundancy including all accessories, counter weights and self balance as required etc. b) Raising and lowering mechanism consisting of suitable double drum winch assembly, head frame assembly with self-fabricating bearing and stainless steel shaft, non-corrosive, pulley & stainless steel wire ropes of minimum 6 mm dia 316 Grade SS hoisting (7/19 construction) etc. completes with internally mounted electric driven 3 phase, 415 volts, 50 Hz operated integral power tool installed inside the base compartment for its operation and with manual operation provision. | 6.00 | job | 1.00 | 347500.00 | 2085000.00 | 100000.00 | 600000.00 | 198402.00 | 1190412.00 | 284182.00 | 1705092.00 | 600000.00 | SAURABH ENTERPRISES
1.02 | c) Supply, Laying and fixing of 2 runs of flexible round sheath multi-core trailing cables of suitable size from junction box to lantern carriage including wiring of all fittings with all wiring materials like PVC insulated PVC sheathed flexible cable of suitable copper conductor cores of 1.5 sq. mm, lugs, MCB etc as required & 2 Nos Aviation obstruction lights. d) Supply of foundation bolts manufactured from special steel along with nuts, washers, suitable size anchor plate and template. e) Design, casting of open raft type RCC foundation suitable for soil bearing capacity at site. The minimum M25 grade concrete for the high mast considering the safe soil bearing capacity at site as 10T/sqmtr at 2 meter depth job including all materials and labour and as per site conditions. (The foundation design should be vetted form reputed IIT/ NIT/ any reputed Govt technical institution for withstanding the desired wind pressure along with desired fittings for meeting required lux level at apron). f) Heavy gauge hot dip galvanized lightening arrester and its necessary connections at the top. g) Supply & installation of outdoor stand mounted feeder pillar, IP54 with 32A TPN MCCB, 25kA with Ics=100%Icu incomer, single dial time switch, contactor for the automatic switching of luminaries, power tool control with 2 nos. 9A contactors, lowering and raising mechanism through push button, Incoming cable end termination upto 35sq.mm and outgoing going cable of min 4C x 16 sq. mm between feeder piller and high mast for power & 2.5 sq. mm for motor terminals. h) SITC of 02 Nos LED Aviation obstruction lights.
2.00 | Supply and installation of 500 W LED flood light luminares in powder coated single piece die cast aluminium housing with heat sink and heat resistant glass cover etc with all accessories for above mentioned high masts operating on 240VAC + 10%, 50Hz supply. The luminaries shall have Lumen efficacy of LED >110 lm/W, IP66 rating etc complete as required & as per technical specifications. | 42.00 | job | 1.00 | 14875.00 | 624750.00 | 26000.00 | 1092000.00 | 14060.00 | 590520.00 | 17105.00 | 718410.00 | 590520.00 | MANKHA ELECTROTECH PRIVATE LIMITED
3.00 | Design, manufacturer and supply of 6 mtrs. long tubular GI pole (class-A), 65mm dia with base plate of size 220x220x12mm welded with the base of pole for fixing on foundation bolts complete as reqd, suitable for installation on a precast foundation with supply of 4 nos. of foundation bolt (M16x450 mm long "J" type bolt, EN 8 grade) & anchor plate for structural stability as specified | 90.00 | job | 1.00 | 8365.00 | 752850.00 | 12000.00 | 1080000.00 | 7620.00 | 685800.00 | 18671.00 | 1680390.00 | 685800.00 | MANKHA ELECTROTECH PRIVATE LIMITED
4.00 | Supply of GI double pole arm bracket, with each arm of 40mm nominal dia, min 1000mm long overhang with clamps suitable to mount on GI pole as above for fixing street LED fitting complete as required. | 90.00 | each | 1.00 | 1250.00 | 112500.00 | 1500.00 | 135000.00 | 1446.00 | 130140.00 | 2300.00 | 207000.00 | 112500.00 | Master Electric Store
5.00 | Supply of GI single pole arm, 50mm dia, 2250mm long with bend of requried shape, with clamps suitable to mount on wall for fixing street LED fitting complete as required | 30.00 | each | 1.00 | 1050.00 | 31500.00 | 2500.00 | 75000.00 | 1086.00 | 32580.00 | 1650.00 | 49500.00 | 31500.00 | Master Electric Store
6.00 | Supply of IP55 rated SMC box of min. size 300mm x 200 mm x 100mm including providing and fixing 1 no. 10 amp DP MCB and 4way Terminal block connector suitable for cable termination upto 25sqmm, complete as required. | 120.00 | each | 1.00 | 1250.00 | 150000.00 | 2500.00 | 300000.00 | 816.00 | 97920.00 | 1200.00 | 144000.00 | 97920.00 | MANKHA ELECTROTECH PRIVATE LIMITED
7.00 | Supply and fixing of GI pipe (class-A) 65mm nominal dia of required length on wall/pole with suitable MS clamps etc complete as required. | 150.00 | mtr | 1.00 | 650.00 | 97500.00 | 575.00 | 86250.00 | 960.00 | 144000.00 | 650.00 | 97500.00 | 86250.00 | SAURABH ENTERPRISES
8.00 | Erection, testing and commissioning of street light pole with height 6 mtr & double pole arm bracket with all accessories/clamps including installation of LED light & its connection from connector of pole/Junction box to fitting by 3C X 1.5 sqmm cable, casting of M-25 grade cement concrete foundation of size 500mm x 500mm x 750 mm including excavation of pit of required size, allignment of anchor plate, foundation bolts (supplied with pole to match with pole base plate),i/c providing and fixing of 02 nos. of DWC pipe of size 40 mm OD conforming to IS-16205, part-24 in the foundation for loop-in-loop-out cables to the pole complete as required and as specified. | 90.00 | job | 1.00 | 2950.00 | 265500.00 | 2000.00 | 180000.00 | 5343.00 | 480870.00 | 2500.00 | 225000.00 | 180000.00 | SAURABH ENTERPRISES
9.00 | Fixing of pole arm on wall with clamps and installing LED fittings on the same complete with electrical connection by 3Cx1.5sqmm cable between Junction box and LED light. | 30.00 | job | 1.00 | 200.00 | 6000.00 | 400.00 | 12000.00 | 600.00 | 18000.00 | 600.00 | 18000.00 | 6000.00 | Master Electric Store
10.00 | Supply and installation of min. 60 W LED flood light luminares in powder coated single piece die cast aluminium housing with heat sink and heat resistant glass cover etc with all accessories for above mentioned poles/pole arm, operating on 240VAC + 10%, 50Hz supply. The luminaries shall have Lumen efficacy of LED >110 lm/W, IP66 rating etc complete as required & as specified in technical specifications. | 120.00 | job | 1.00 | 2050.00 | 246000.00 | 4500.00 | 540000.00 | 1626.00 | 195120.00 | 2400.00 | 288000.00 | 195120.00 | MANKHA ELECTROTECH PRIVATE LIMITED
11.00 | Supply and installation of min. 30 W LED flood light luminares in powder coated single piece die cast aluminium housing with heat sink and heat resistant glass cover etc with all accessories for above mentioned poles/pole arm, operating on 240VAC + 10%, 50Hz supply. The luminaries shall have Lumen efficacy of LED >110 lm/W, IP66 rating etc complete as required & as specified in technical specifications. | 30.00 | job | 1.00 | 1350.00 | 40500.00 | 3000.00 | 90000.00 | 1167.00 | 35010.00 | 1816.00 | 54480.00 | 35010.00 | MANKHA ELECTROTECH PRIVATE LIMITED
12.00 | Supply installation, testing & commissioning of complete electro-mechanical automatic boom barrier system min. IP 65 rated comprising of following: (i) Drive mechanism: Consisting of suitable Drive motor unit, arrangement for manual operation at the time of power failure or emergency, fault protection, counter balance system, suitable to be operated on AC 230V + 10%, 50 Hz supply. (ii) Aluminium boom with arm length of 7mtr, Boom is to be painted with alternate Red & White strips and provided with a reflective "STOP" sign in the center & bands of reflective tape for night warning- 01 No. (iii) Flashing light & boom LED light - 01 set (iv) Boom stand - 1 set (v) Photo cell pair for obstacle detection and auto-reverse function on contact. (vi) Boom operation via wireless remote control (upto 30mtr)- 01 set and wired push-button control - 01 set (vii) Necessary control cabling and fixing up to 30 meters for wire control operation. (viii) Foundation work for drive unit as per manufacture requirement. | 4.00 | each | 1.00 | 143588.00 | 574352.00 | 170000.00 | 680000.00 | 84003.00 | 336012.00 | 679500.00 | 2718000.00 | 336012.00 | MANKHA ELECTROTECH PRIVATE LIMITED
13.00 | Supply, Installation, Testing and Commissioning of CPCB IV compliant ‘Silent Type’ Diesel Generating set alongwith having Prime Power Rating of 40 KVA, 415 volts at 1500 RPM, 0.8 lagging power factor at 415 V suitable for 50 Hz, 3 phase system & for 0.85 load factor consisting of the followings: | 1.00 | job | 1.00 | 498000.00 | 498000.00 | 100000.00 | 100000.00 | 612005.00 | 612005.00 | 791762.00 | 791762.00 | 100000.00 | SAURABH ENTERPRISES
13.01 | (a) Diesel engine 4 stroke liquid cooled, electric start of suitable BHP at 1500 RPM suitable for above output of alternator at 40 degree C, 50% RH & at 1000 meter MSL and conforming to BS 5514, BS 649, IS 10000, capable of taking 10 % over loading for one hour after 12 hours of continuous operation. The engine will be fitted complete with all the required accessories. (b) Engine mounted Instrument Panel fitted with and having digital display for following: (i) Start stop with key (ii) Water temperature indication (iii) Lubrication oil pressure indication (iv) Lubrication oil temperature indication (v) Battery charging indication (vi) RPM indication (vii) Over speed indication (viii) Low lub, oil trip indication (ix) Engine Hour indication
13.02 | (c) Alternator: Synchronous alternator rated at 40 KVA, 415 volts at 1500 RPM, 3 phase 50 Hz, AC supply with 0.8 lagging power factor at 40 Degree C, 50% RH & at 1000 meter MSL. The alternator shall be having SPDP enclosure, brushless, continuous duty, self excited and self regulated through AVR conforming to IS: 4722/BS 2613 suitable for tropical condiitions and with class -F/H insulation. (d) Base Frame: Both the engine and alternator shall be mounted on suitable base frame made of MS channel with necessary reinforcement and vibration isolation arrangement as per recommendation of manufacturer. (e) Exhaust System: Dry Exhaust manifold with hospital exhaust silencer and catalytic converter. (f) Starting System: 12V/24V DC starting system comprising of starter motors: voltage regulator andarrangement for initial excitation complete with suitable no. of batteries as required as per specification.
13.03 | (g) Accoustic and weather proof enclosure with arrangement for fresh air intake for cooling of the engine & alternator, extraction, discharging hot air in to the atmosphere as per specifications.Works includes complete SITC Job including required works as per O.E.M guidelines like providing & fixing C channel etc. complete in all respects as required at site.
14.00 | Fabricating, Installation, Testing & Commissioning of automatic mains failure control panel made out of 1.6 mm thick CRCA sheet including microprocessor based AMF module suitable for 40 KVA silent type DG set complete with relays, timers, set of CTs for metering & protection and digital multifunction meter to indicate currents, phase and line voltages frequency, power factor, KWH, KVARH & provision for overload, short circuit, restricted earth fault, under frequency, control cabling from AMF panel to diesel engine and elsewhere if required, all complete and inter locking including by pass arrangement etc and the following: | 1.00 | job | 1.00 | 112500.00 | 112500.00 | 100000.00 | 100000.00 | 600000.00 | 600000.00 | 145000.00 | 145000.00 | 100000.00 | SAURABH ENTERPRISES
14.01 | (a) 80 Amp, 4 pole, power contactor - 02 Nos. (b) 2 Nos. 80 Amp, 4 pole MCCB, ICU= 100% ICs - 02 Nos. (c) Auto/By-pass Manual/Test/Off selector switch. (d) Microprocessor based AMF module with provision for over load, short circuit, resticted earth fault, under frequency. (e) 3 Sets of current transformers for protection and for metering. (f) Digital multi fuction meter. (g) Indicating lamps for load on mains and load on set DG on, battery charger on. (h) Control Fuse for instruments. (i) Battery charger, complete with transformer/ rectifier, D.C. voltmeter and ammeter, selector switch for trickle, off and boost and current adjustment. (j) Main supply failure monitor. (k) Supply failure timer. (l) Restoration timer. (m) Control unit with three impulse automatic engine start/stop and failure to start lockout. (n) Impulse counter with locking and reset facility. (o) ON/OFF/Control circuit switch with indicator.
14.02 | (p) Audio annunciation for (i) High water temperature. (ii) Low lubricating oil pressure. (iii) Engine over speed. (iv) Engine fails to start. (v) Under and over voltage (vi) Full load/maximum load warning.
15.00 | Making PCC foundation complete with 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size) for the above DG Set canopy of suitable size as per OEM standards complete as required. | 1.00 | job | 1.00 | 30000.00 | 30000.00 | 25000.00 | 25000.00 | 10005.00 | 10005.00 | 18000.00 | 18000.00 | 10005.00 | MANKHA ELECTROTECH PRIVATE LIMITED
16.00 | Design, fabrication, supply, installation, testing and commissioning of outdoor type cubical feeder pillar double door, weather and vermin proof, powder coated, fabricated with 2mm thick CRCA Sheet Steel, 3mm thick sheet steel for gland plate, Degree of Protection of enclosure shall be IP-54, suitable for operation on 3 phase and neutral, 415 V,50 HZ AC system. Entire panel shall have a common GI earth bar of size 50mmx5mm at the rear with two number earth stud. Cable entry will be from bottom. Control Wiring should be done by FRLS PVC insulated 2.5 Sq.mm solid copper conductor cable. The feeder pillar shall consist of following switch gears- MCCBs shall be with adjustable thermal ((80%-100%) and magnetic release having overload protection, short circuit adjustable setting & (Ics = Icu) i/c accessories as per specification and providing metering instruments (Voltmeter, Ammeter), LED Indicators, etc. complete as required. | 1.00 | job | 1.00 | 115400.00 | 115400.00 | 95000.00 | 95000.00 | 156300.00 | 156300.00 | 85000.00 | 85000.00 | 85000.00 | Unique Electro Engineers Pvt. Ltd.
16.01 | Incomer- 63A, 25 KA, FP MCCB, rotary handle, adjustable Thermal release and CT operated digital multi-function meter, On/off LED indication, RYB Phase LED indication lamp with suitable control MCBs - 01 Nos. Bus Bars- 1 Set of min. 80 Amp rated TPN bus bars of high conductivity electrolytic grade aluminum with 100% neutral size & Heat shrinkable color coded insulation sleeves Outgoings- i) 40 Amp, 25 KA, FP MCCB - 2 Nos. ii) 16 Amp, 10kA, TPN MCB with timer switch control - 1 set Control: 4 Pole Contactor with a thermal rating of 25A - 1 no. Time Switch with Daily dial, suitable for operation on 230 Volt, Single phase, 50 Hz, AC Supply - 1 No. Auto-Manual Selector switch - 1 Nos. On/ Off Push Buttons-1 Nos with LED indication. On/off LED indication, RYB Phase LED indication lamp with suitable control MCBs - 02 nos.
17.00 | Design, manufacturing, supply, installation, testing and commissioning of outdoor type cubical feeder pillar double door, weather and vermin proof, powder coated, fabricated with 2mm thick CRCA Sheet Steel, 3mm thick sheet steel for gland plate, Degree of Protection of enclosure shall be IP-54.suitable for operation on 3 phase and neutral, 415 V,50 HZ AC system. Entire panel shall have a common GI earth bar of size 50mmx5mm at the rear with two number earth stud. Cable entry will be from bottom. Control Wiring should be done by FRLS PVC insulated 2.5 Sq.mm solid copper conductor cable. The feeder pillar shall consist of following switchgears - MCCBs shall be with adjustable thermal ((80%-100%) and magnetic release having overload protection, short circuit adjustable setting & (Ics = Icu) i/c accessories as per specification and providing metering instruments (Voltmeter, Ammeter), LED Indicators, etc. complete as required. | 1.00 | job | 1.00 | 165800.00 | 165800.00 | 100000.00 | 100000.00 | 185220.00 | 185220.00 | 72000.00 | 72000.00 | 72000.00 | Unique Electro Engineers Pvt. Ltd.
17.01 | Incomer- 40A, 25 KA, FP MCCB, on/off indication, RYB Phase LED indication lamp with suitable control MCBs and CT operated digital multi function meter - 01 Nos. Bus bars - 1 Set of 63 Amp TPN bus bars of high conductivity electrolytic grade aluminum with 100% neutral size & Heat shrinkable color coded insulation sleeves Outgoings- i) 32Amp, 25kA, TPN MCCB with on/off LED indication - 03 no. ii) 20Amp, 10kA, TPN MCB - 03 nos. iii) 20Amp, 10kA, SPN MCB - 04 nos. iv) 16Amp, 10kA, TPN MCB with timer switch control - 1 set Control: 4 Pole Contactor with a thermal rating of 25A - 1 no. Time Switch with Daily dial, suitable for operation on 230 Volt, Single phase, 50 Hz, AC Supply - 1 No. Auto-Manual Selector switch - 1 Nos. On/ Off Push Buttons-1 Nos with LED indication.
18.00 | Design, manufacturing, supply, installation, testing and commissioning of outdoor type cubical feeder pillar double door, weather and vermin proof, powder coated, fabricated with 2mm thick CRCA Sheet Steel, 3mm thick sheet steel for gland plate, Degree of Protection of enclosure shall be IP-54.suitable for operation on 3 phase and neutral, 415 V,50 HZ AC system. Entire panel shall have a common GI earth bar of size 50mmx5mm at the rear with two number earth stud. Cable entry will be from bottom. Control Wiring should be done by FRLS PVC insulated 2.5 Sq.mm solid copper conductor cable. The feeder pillar shall consist of following switchgears - MCCBs shall be with adjustable thermal ((80%-100%) and magnetic release having overload protection, short circuit adjustable setting & (Ics = Icu) i/c accessories as per specification and providing metering instruments (Voltmeter, Ammeter), LED Indicators, etc. complete as required. | 1.00 | job | 1.00 | 109580.00 | 109580.00 | 100000.00 | 100000.00 | 77100.00 | 77100.00 | 165000.00 | 165000.00 | 77100.00 | MANKHA ELECTROTECH PRIVATE LIMITED
18.01 | Incomer- 32A, 25 KA, FP MCCB, on/off indication, RYB Phase LED indication lamp with suitable control MCBs and CT operated digital multi function meter - 01 Nos. Bus bars - 1 Set of 40 Amp TPN bus bars of high conductivity electrolytic grade aluminum with 100% neutral size & Heat shrinkable color coded insulation sleeves Outgoings- i) 20Amp, 10kA, TPN MCB - 04 nos. ii) 16Amp, 10kA, TPN MCB with timer switch control - 1 set Control: 4 Pole Contactor with a thermal rating of 25A - 1 no. Time Switch with Daily dial, suitable for operation on 230 Volt, Single phase, 50 Hz, AC Supply - 1 No. Auto-Manual Selector switch - 1 Nos. On/ Off Push Buttons-1 Nos with LED indication.
19.00 | Design, manufacturing, supply, installation, testing and commissioning of outdoor type cubical feeder pillar double door, weather and vermin proof, powder coated, fabricated with 2mm thick CRCA Sheet Steel, 3mm thick sheet steel for gland plate, Degree of Protection of enclosure shall be IP-54.suitable for operation on 3 phase and neutral, 415 V,50 HZ AC system. Entire panel shall have a common GI earth bar of size 50mmx5mm at the rear with two number earth stud. Cable entry will be from bottom. Control Wiring should be done by FRLS PVC insulated 2.5 Sq.mm solid copper conductor cable. The feeder pillar shall consist of following switchgears - MCCBs shall be with adjustable thermal ((80%-100%) and magnetic release having overload protection, short circuit adjustable setting & (Ics = Icu) i/c accessories as per specification and providing metering instruments (Voltmeter, Ammeter for both incomer), LED Indicators, etc. complete as required. | 1.00 | job | 1.00 | 81500.00 | 81500.00 | 50000.00 | 50000.00 | 690000.00 | 690000.00 | 168000.00 | 168000.00 | 50000.00 | SAURABH ENTERPRISES
19.01 | Incomer- 32A, 25 KA, FP MCCB, on/off indication, RYB Phase LED indication lamp with suitable control MCBs and CT operated digital multi function meter - 01 Nos. Bus bars - 1 Set of 40 Amp TPN bus bars of high conductivity electrolytic grade aluminum with 100% neutral size & Heat shrinkable color coded insulation sleeves Outgoings- i) 20Amp, 10kA, TPN MCB - 02 nos. ii) 16Amp, 10kA, TPN MCB with timer switch control - 1 set Control: 4 Pole Contactor with a thermal rating of 25A - 1 no. Time Switch with Daily dial, suitable for operation on 230 Volt, Single phase, 50 Hz, AC Supply - 1 No. Auto-Manual Selector switch - 1 Nos. On/ Off Push Buttons-1 Nos with LED indication.
20.00 | Design, fabrication, supply, installation, testing and commissioning of outdoor type cubical feeder pillar double door, weather and vermin proof, powder coated, fabricated with 2mm thick CRCA Sheet Steel, 3mm thick sheet steel for gland plate, Degree of Protection of enclosure shall be IP-54, suitable for operation on 3 phase and neutral, 415 V,50 HZ AC system. Entire panel shall have a common GI earth bar of size 50mmx5mm at the rear with two number earth stud. Cable entry will be from bottom. Control Wiring should be done by FRLS PVC insulated 2.5 Sq.mm solid copper conductor cable. The feeder pillar shall consist of following switch gears- MCCBs shall be with adjustable thermal ((80%-100%) and magnetic release having overload protection, short circuit adjustable setting & (Ics = Icu) i/c accessories as per specification and providing metering instruments (Voltmeter, Ammeter), LED Indicators, etc. complete as required. | 1.00 | job | 1.00 | 385400.00 | 385400.00 | 122285.00 | 122285.00 | 510000.00 | 510000.00 | 160000.00 | 160000.00 | 122285.00 | SAURABH ENTERPRISES
20.01 | Incomer- 100A, 36 KA, FP MCCB, rotary handle, CT operated digital multi-function meter, On/off LED indication, RYB Phase LED indication lamp with suitable control MCBs, with electrical & mechanical interlocking b/w incomers and bus coupler - 02 Nos. Bus Coupler- 100A, 36 KA, FP MCCB, rotary handle, On/off LED indication, RYB Phase LED indication lamp with suitable control MCBs - 01 No. Bus Bars- 1 Set of min. 125 Amp rated TPN bus bars of high conductivity electrolytic grade aluminum with 100% neutral size & Heat shrinkable color coded insulation sleeves Outgoings- i) 32Amp, 25 KA, TPN MCCB - 7 Nos. ii) 40Amp, 25 KA, TPN MCCB - 3 Nos. iii) 20Amp, 10kA, TPN MCB - 1 Nos. On/off LED indication, RYB Phase LED indication lamp with suitable control MCBs - 10 nos.
21.00 | Design, fabrication, supply, installation, testing and commissioning of outdoor type cubical feeder pillar double door, weather and vermin proof, powder coated, fabricated with 2mm thick CRCA Sheet Steel, 3mm thick sheet steel for gland plate, Degree of Protection of enclosure shall be IP-54, suitable for operation on 3 phase and neutral, 415 V,50 HZ AC system. Entire panel shall have a common GI earth bar of size 50mmx5mm at the rear with two number earth stud. Cable entry will be from bottom. Control Wiring should be done by FRLS PVC insulated 2.5 Sq.mm solid copper conductor cable. The feeder pillar shall consist of following switch gears- MCCBs shall be with adjustable thermal ((80%-100%) and magnetic release having overload protection, short circuit adjustable setting & (Ics = Icu) i/c accessories as per specification and providing metering instruments, LED Indicators, etc. complete as required. | 2.00 | job | 1.00 | 82540.00 | 165080.00 | 64500.00 | 129000.00 | 85703.00 | 171406.00 | 178000.00 | 356000.00 | 129000.00 | SAURABH ENTERPRISES
21.01 | Incomer- 40A, 25kA, FP MCCB, CT operated digital multi-function meter, On/off LED indication, RYB Phase LED indication lamp with suitable control MCBs, with electrical & mechanical interlocking b/w incomers and bus coupler - 01 Nos. Bus Bars- 1 Set of min. 63 Amp rated TPN bus bars of high conductivity electrolytic grade aluminum with 100% neutral size & Heat shrinkable color coded insulation sleeves Outgoings- ii) 25Amp, 25kA, TPN MCCB - 1 no. iii) 20Amp, 10kA, TPN MCB - 3 nos. On/off LED indication, RYB Phase LED indication lamp with suitable control MCBs - 1 no.
22.00 | Supply of elevated type Omni-directional Blue colour, medium intensity LED type Taxiway Edge Light fitting suitable for Taxiway, Apron Edge Lights suitable for operation at 6.6 Amps, series circuit supply, complete with Omni-directional, Lens clamping mechanism, breakable coupling, gasket, two pin secondary leads, base plate with SS Hardware and other accessories including integrated encapsulated electronic module complete as required. Conforming to latest ICAO / CAR requirement/FAA as per specifications complete as required. | 40.00 | each | 1.00 | 5580.00 | 223200.00 | 6500.00 | 260000.00 | 9105.00 | 364200.00 | 9800.00 | 392000.00 | 223200.00 | Master Electric Store
23.00 | Supply of 4kVA Indoor type air cooled constant current regulator of micro processor controlled, thyristor type suitable for remote as well as local control operations on input voltage 230/415 volts, 50Hz AC supply with 6.6A output having 5 steps brightness control with variation of current output and able to communicate with PC or PLC controlled system, with digital output ammeter (0-10A), over current, overvoltage, open circuit and earth fault protection and digital earth leakage meter, two stage earth leakage detector, positive back indication equipments, LED/LCD display, suitable for operation with halogen/LED type AGL Circuits etc complete as required confirming to technical specifications. | 2.00 | each | 1.00 | 239500.00 | 479000.00 | 50000.00 | 100000.00 | 222000.00 | 444000.00 | 185000.00 | 370000.00 | 100000.00 | SAURABH ENTERPRISES
24.00 | Supply of 15W, 6.6/6.6 Amps, 5kV, 50 Hz series Isolating Transformers encapsulated in polyester resin, finally moulded in neoprene type rubber and with primary and secondary connections confirming to specification as required. | 40.00 | each | 1.00 | 3500.00 | 140000.00 | 4500.00 | 180000.00 | 6000.00 | 240000.00 | 8200.00 | 328000.00 | 140000.00 | Master Electric Store
25.00 | Supply of 5 KV grade copper conductor XLPE insulated, polyethylene sheathed single core, unscreened airfield lighting cable conforming to as specified in particular specifications of the following sizes as required- a) 6 sqmm | 1500.00 | mtr | 1.00 | 123.00 | 184500.00 | 250.00 | 375000.00 | 96.00 | 144000.00 | 240.00 | 360000.00 | 144000.00 | MANKHA ELECTROTECH PRIVATE LIMITED
26.00 | Supply of following sizes 5 KV grade, field mounted & resin filled Plug and Receptacle suitable for 5 KV grade single core copper conductor screened cable etc as required. a) 6sqmm | 40.00 | set | 1.00 | 800.00 | 32000.00 | 700.00 | 28000.00 | 2643.00 | 105720.00 | 1750.00 | 70000.00 | 28000.00 | SAURABH ENTERPRISES
27.00 | Installation, testing & commissioning of Elevated type taxiway light fixtures on existing transformer housing boxes I/c installation of isolating transformers, lamps, making cable connections etc. complete as required. | 34.00 | each | 1.00 | 1000.00 | 34000.00 | 50.00 | 1700.00 | 369.00 | 12546.00 | 1500.00 | 51000.00 | 1700.00 | SAURABH ENTERPRISES
28.00 | Installation, testing and commissioning of 4 kVA CCR along with connection of 5 KV grade 6 sq mm AFL primary cable, termination of power cable, OFC, earthing connection etc as required | 2.00 | each | 1.00 | 12500.00 | 25000.00 | 5000.00 | 10000.00 | 150000.00 | 300000.00 | 20000.00 | 40000.00 | 10000.00 | SAURABH ENTERPRISES
29.00 | Laying of one number PVC insulated & PVC sheathed copper conductor AFL cable of grade 5 KV of size not exceeding 6sqmm in the existing cable duct / masonry trench/ RCC/HUME/METAL/HDPE pipes etc. as required. | 1500.00 | mtr | 1.00 | 20.00 | 30000.00 | 5.00 | 7500.00 | 96.00 | 144000.00 | 50.00 | 75000.00 | 7500.00 | SAURABH ENTERPRISES
30.00 | Numbering of Airfield Light Fixtures on the base/ top surface/ RCC foundation of light fixture with good quality of black color enamel paint with yellow background etc. complete as required. | 34.00 | each | 1.00 | 300.00 | 10200.00 | 100.00 | 3400.00 | 60.00 | 2040.00 | 100.00 | 3400.00 | 2040.00 | MANKHA ELECTROTECH PRIVATE LIMITED
31.00 | Numbering of Airfield Light Fixtures on the base/ top surface/ RCC foundation of light fixture with good quality of black color enamel paint with yellow background etc. complete as required.
31.01 | 3 x 4 sq mm armoured cable | 600.00 | mtr | 1.00 | 85.00 | 51000.00 | 200.00 | 120000.00 | 96.00 | 57600.00 | 180.00 | 108000.00 | 51000.00 | Master Electric Store
31.02 | 3.5 x 25 sq mm armoured cable | 7850.00 | mtr | 1.00 | 180.00 | 1413000.00 | 400.00 | 3140000.00 | 195.00 | 1530750.00 | 220.00 | 1727000.00 | 1413000.00 | Master Electric Store
31.03 | 3.5x 120 Sq mm armoured cable | 1550.00 | mtr | 1.00 | 670.00 | 1038500.00 | 750.00 | 1162500.00 | 717.00 | 1111350.00 | 380.00 | 589000.00 | 589000.00 | Unique Electro Engineers Pvt. Ltd.
31.04 | 3.5x 150 Sq mm armoured cable | 1650.00 | mtr | 1.00 | 770.00 | 1270500.00 | 800.00 | 1320000.00 | 852.00 | 1405800.00 | 420.00 | 693000.00 | 693000.00 | Unique Electro Engineers Pvt. Ltd.
32.00 | Supply of DWC HDPE pipe following sizes, ISI marked along with all accessories like socket, bend, couplers etc. conforming to IS-16205, part-24 complete as required.
32.01 | 160 mm OD | 500.00 | mtr | 1.00 | 210.00 | 105000.00 | 200.00 | 100000.00 | 195.00 | 97500.00 | 265.00 | 132500.00 | 97500.00 | MANKHA ELECTROTECH PRIVATE LIMITED
32.02 | 90 mm OD | 3200.00 | mtr | 1.00 | 110.00 | 352000.00 | 210.00 | 672000.00 | 114.00 | 364800.00 | 155.00 | 496000.00 | 352000.00 | Master Electric Store
32.03 | 50 mm OD | 7850.00 | mtr | 1.00 | 45.00 | 353250.00 | 70.00 | 549500.00 | 51.00 | 400350.00 | 110.00 | 863500.00 | 353250.00 | Master Electric Store
32.04 | 40 mm OD | 2100.00 | mtr | 1.00 | 30.00 | 63000.00 | 60.00 | 126000.00 | 42.00 | 88200.00 | 100.00 | 210000.00 | 63000.00 | Master Electric Store
33.00 | Laying of DWC HDPE pipe of following sizes along with all accessories like socket, bend, couplers etc. complete with fitting and cutting, jointing etc. direct in ground (75 cm below ground level) including excavation and refilling the trench but excluding sand cushioning and protective covering etc., complete as required.
33.01 | 160 mm OD | 500.00 | mtr | 1.00 | 80.00 | 40000.00 | 50.00 | 25000.00 | 87.00 | 43500.00 | 250.00 | 125000.00 | 25000.00 | SAURABH ENTERPRISES
33.02 | 90 mm OD | 3200.00 | mtr | 1.00 | 60.00 | 192000.00 | 50.00 | 160000.00 | 78.00 | 249600.00 | 195.00 | 624000.00 | 160000.00 | SAURABH ENTERPRISES
33.03 | 50 mm OD | 7850.00 | mtr | 1.00 | 50.00 | 392500.00 | 50.00 | 392500.00 | 60.00 | 471000.00 | 150.00 | 1177500.00 | 392500.00 | SAURABH ENTERPRISES, Master Electric Store
33.04 | 40 mm OD | 2100.00 | mtr | 1.00 | 40.00 | 84000.00 | 50.00 | 105000.00 | 60.00 | 126000.00 | 150.00 | 315000.00 | 84000.00 | Master Electric Store
34.00 | Supplying and laying of 100 mm dia GI pipe, Class 'B' for crossing of roads & pathways i/c cutting, jointing with GI coupler, fittings etc. as required direct in ground including excavation and refilling of trench and making good the same, complete as required. | 30.00 | mtr | 1.00 | 1100.00 | 33000.00 | 1000.00 | 30000.00 | 1905.00 | 57150.00 | 1600.00 | 48000.00 | 30000.00 | SAURABH ENTERPRISES
35.00 | Supplying and laying of 150 mm dia GI pipe, Class 'B' for crossing of roads & pathways i/c cutting, jointing with GI coupler, fittings etc. as required direct in ground including excavation and refilling of trench and making good the same, complete as required. | 660.00 | mtr | 1.00 | 1650.00 | 1089000.00 | 1500.00 | 990000.00 | 2670.00 | 1762200.00 | 1800.00 | 1188000.00 | 990000.00 | SAURABH ENTERPRISES
36.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/HUME/METAL/HDPE pipes as required.
36.01 | Upto 35 sq. mm | 8400.00 | mtr | 1.00 | 9.00 | 75600.00 | 10.00 | 84000.00 | 33.00 | 277200.00 | 70.00 | 588000.00 | 75600.00 | Master Electric Store
36.02 | Above 95 sq. mm and upto 185 sq. mm | 3100.00 | mtr | 1.00 | 14.00 | 43400.00 | 20.00 | 62000.00 | 60.00 | 186000.00 | 150.00 | 465000.00 | 43400.00 | Master Electric Store
37.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing cable duct / masonry trench as required. A) Above 95 sq. mm and upto 185 sq. mm | 100.00 | mtr | 1.00 | 50.00 | 5000.00 | 20.00 | 2000.00 | 96.00 | 9600.00 | 150.00 | 15000.00 | 2000.00 | SAURABH ENTERPRISES
38.00 | Supplying and making straight through joint with heat shrinkable jointing kit including ferrules and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
38.01 | 3.5 x 25 sq mm armoured cable | 10.00 | each | 1.00 | 1850.00 | 18500.00 | 1000.00 | 10000.00 | 3300.00 | 33000.00 | 1507.00 | 15070.00 | 10000.00 | SAURABH ENTERPRISES
38.02 | 3.5x 120 Sq mm armoured cable | 3.00 | each | 1.00 | 3400.00 | 10200.00 | 1500.00 | 4500.00 | 6000.00 | 18000.00 | 2946.00 | 8838.00 | 4500.00 | SAURABH ENTERPRISES
38.03 | 3.5x 150 Sq mm armoured cable | 3.00 | each | 1.00 | 3300.00 | 9900.00 | 2000.00 | 6000.00 | 8700.00 | 26100.00 | 2946.00 | 8838.00 | 6000.00 | SAURABH ENTERPRISES
39.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
39.01 | 3½ X 25 sq. mm (25mm) | 250.00 | each | 1.00 | 90.00 | 22500.00 | 300.00 | 75000.00 | 150.00 | 37500.00 | 540.00 | 135000.00 | 22500.00 | Master Electric Store
39.02 | 3½ X 120 sq. mm (45mm) | 6.00 | each | 1.00 | 580.00 | 3480.00 | 1000.00 | 6000.00 | 303.00 | 1818.00 | 1554.00 | 9324.00 | 1818.00 | MANKHA ELECTROTECH PRIVATE LIMITED
39.03 | 3½ X 150 sq. mm (50mm) | 12.00 | each | 1.00 | 600.00 | 7200.00 | 1000.00 | 12000.00 | 330.00 | 3960.00 | 1784.00 | 21408.00 | 3960.00 | MANKHA ELECTROTECH PRIVATE LIMITED
40.00 | Supply of 3Cx 240 sqmm XLPE insulated PVC sheathed aluminium conductor armoured Power cable of 11 KV grade (11 KV earthed system) conforming to IS: 7098 (part-II) amended up to date. | 450.00 | mtr | 1.00 | 1785.00 | 803250.00 | 1500.00 | 675000.00 | 1725.00 | 776250.00 | 2070.00 | 931500.00 | 675000.00 | SAURABH ENTERPRISES
41.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 11 KV grade of following size in the existing RCC/HUME/ METAL/HDPE pipe as required. A) Above 120 sqmm and upto 400 sqmm | 450.00 | mtr | 1.00 | 80.00 | 36000.00 | 50.00 | 22500.00 | 222.00 | 99900.00 | 250.00 | 112500.00 | 22500.00 | SAURABH ENTERPRISES
42.00 | Suppy and making indoor cable end termination with heat shrinkable jointing kit complete with all accessories including lugs suitable for 3 core X 240 sqmm XLPE aluminium conductor cable of 11 KV (UE) grade as required. | 2.00 | each | 1.00 | 15500.00 | 31000.00 | 15000.00 | 30000.00 | 9006.00 | 18012.00 | 16249.00 | 32498.00 | 18012.00 | MANKHA ELECTROTECH PRIVATE LIMITED
43.00 | Supply and fixing 8 way, double door SPN , Sheet steel, MCB distribution board, 240V, on surface/recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required | 6.00 | each | 1.00 | 2050.00 | 12300.00 | 1500.00 | 9000.00 | 3300.00 | 19800.00 | 2055.00 | 12330.00 | 9000.00 | SAURABH ENTERPRISES
44.00 | Supplying and fixing 5 A to 32 A rating, 240/415 V, 10 kA, "C" curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required.
44.01 | Single pole | 30.00 | each | 1.00 | 150.00 | 4500.00 | 250.00 | 7500.00 | 114.00 | 3420.00 | 219.00 | 6570.00 | 3420.00 | MANKHA ELECTROTECH PRIVATE LIMITED
44.02 | Triple pole | 6.00 | each | 1.00 | 350.00 | 2100.00 | 1500.00 | 9000.00 | 555.00 | 3330.00 | 1554.00 | 9324.00 | 2100.00 | Master Electric Store
45.00 | Wiring for light point/ fan point/ exhaust fan point/ call bell point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in surface / recessed steel conduit, with modular switch, modular plate, suitable GI box and earthing the point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable etc. as required. a) Group B | 30.00 | point | 1.00 | 1150.00 | 34500.00 | 1500.00 | 45000.00 | 1500.00 | 45000.00 | 2651.00 | 79530.00 | 34500.00 | Master Electric Store
46.00 | Wiring for twin control light point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in surface / recessed steel conduit, 2 way modular switch, modular plate, suitable GI box and earthing the point with 1.5 sq.mm. FRLS PVC insulated copper conductor single core cable etc. as required. | 10.00 | point | 1.00 | 1050.00 | 10500.00 | 1500.00 | 15000.00 | 2220.00 | 22200.00 | 3534.00 | 35340.00 | 10500.00 | Master Electric Store
47.00 | Wiring for circuit/ submain wiring alongwith earth wire with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface/ recessed steel conduit as required.
47.01 | 2 X 2.5 sq. mm + 1 X 2.5 sq. mm earth wire | 250.00 | mtr | 1.00 | 290.00 | 72500.00 | 200.00 | 50000.00 | 456.00 | 114000.00 | 274.00 | 68500.00 | 50000.00 | SAURABH ENTERPRISES
47.02 | 2 X 4 sq. mm + 1 X 4 sq. mm earth wire | 250.00 | mtr | 1.00 | 400.00 | 100000.00 | 250.00 | 62500.00 | 600.00 | 150000.00 | 340.00 | 85000.00 | 62500.00 | SAURABH ENTERPRISES
48.00 | Supplying and fixing following size/ modules, GI box alongwith modular base & cover plate for modular switches in recess etc. as required.
48.01 | 3 Module (100mmX75mm) | 12.00 | each | 1.00 | 100.00 | 1200.00 | 400.00 | 4800.00 | 505.00 | 6060.00 | 201.00 | 2412.00 | 1200.00 | Master Electric Store
48.02 | 6 Module (200mmX75mm) | 12.00 | each | 1.00 | 180.00 | 2160.00 | 500.00 | 6000.00 | 555.00 | 6660.00 | 321.00 | 3852.00 | 2160.00 | Master Electric Store
49.00 | Supplying and fixing suitable size GI box with modular plate and cover in front on surface or in recess, including providing and fixing 6 pin 5/6 & 15/16 A modular socket outlet and 15/16 A modular switch, connections etc. as required. | 12.00 | each | 1.00 | 350.00 | 4200.00 | 1000.00 | 12000.00 | 1104.00 | 13248.00 | 477.00 | 5724.00 | 4200.00 | Master Electric Store
50.00 | Supplying and fixing following modular switch/ socket on the existing modular plate & switch box including connections but excluding modular plate etc. as required.
50.01 | 5/6 A switch | 6.00 | each | 1.00 | 80.00 | 480.00 | 100.00 | 600.00 | 150.00 | 900.00 | 52.00 | 312.00 | 312.00 | Unique Electro Engineers Pvt. Ltd.
50.02 | 2 way 5/6 A switch | 6.00 | each | 1.00 | 120.00 | 720.00 | 120.00 | 720.00 | 240.00 | 1440.00 | 122.00 | 732.00 | 720.00 | SAURABH ENTERPRISES, Master Electric Store
50.03 | 15/16 A switch | 6.00 | each | 1.00 | 120.00 | 720.00 | 150.00 | 900.00 | 303.00 | 1818.00 | 122.00 | 732.00 | 720.00 | Master Electric Store
50.04 | 3 pin 5/6 A socket outlet | 6.00 | each | 1.00 | 120.00 | 720.00 | 200.00 | 1200.00 | 240.00 | 1440.00 | 110.00 | 660.00 | 660.00 | Unique Electro Engineers Pvt. Ltd.
50.05 | 6 pin 15/16 A socket outlet | 6.00 | each | 1.00 | 150.00 | 900.00 | 200.00 | 1200.00 | 384.00 | 2304.00 | 174.00 | 1044.00 | 900.00 | Master Electric Store
51.00 | Supply and installation of 4 feet long 18/20W surface mounted LED fitting suitable to operate on 240 V AC, 50 Hz AC supply complete as required. | 25.00 | each | 1.00 | 450.00 | 11250.00 | 400.00 | 10000.00 | 429.00 | 10725.00 | 1505.00 | 37625.00 | 10000.00 | SAURABH ENTERPRISES
52.00 | Supply and installation of 400mm dia sweep wall fan Oscillating type complete with built in String type speed regulator and mounting arrangement complete, as required | 6.00 | each | 1.00 | 2500.00 | 15000.00 | 3500.00 | 21000.00 | 2733.00 | 16398.00 | 2800.00 | 16800.00 | 15000.00 | Master Electric Store
53.00 | Supply and installation of 300 dia sweep, 1375 rpm heavy duty exhaust fan complete, as required. | 6.00 | each | 1.00 | 4050.00 | 24300.00 | 4500.00 | 27000.00 | 4560.00 | 27360.00 | 2400.00 | 14400.00 | 14400.00 | Unique Electro Engineers Pvt. Ltd.
54.00 | Supply and installation of 250W LED manual rotating search light with under deck control arrangement (UDCA), height of UDCA 1.5mtr or as per requirement, suitable for installaing on control/watch towers, complete with LED driver, suitable to operate on 230V + 10%, 50Hz supply complete, as required similar to | 6.00 | each | 1.00 | 51500.00 | 309000.00 | 37000.00 | 222000.00 | 54600.00 | 327600.00 | 9900.00 | 59400.00 | 59400.00 | Unique Electro Engineers Pvt. Ltd.
55.00 | Excavation for cable trenches in soft soil cum including getting out the excavated soil and disposal of surplus excavated soil as directed within a lead of 50 metres. | 800.00 | cum | 1.00 | 160.00 | 128000.00 | 300.00 | 240000.00 | 150.00 | 120000.00 | 205.00 | 164000.00 | 120000.00 | MANKHA ELECTROTECH PRIVATE LIMITED
56.00 | Excavation for cable trenches in hard rock cum including getting out the excavated soil and disposal of surplus excavated soil as directed within a lead of 50 metres. | 10.00 | cum | 1.00 | 1500.00 | 15000.00 | 500.00 | 5000.00 | 330.00 | 3300.00 | 550.00 | 5500.00 | 3300.00 | MANKHA ELECTROTECH PRIVATE LIMITED
57.00 | Filling available excavated earth (excluding rock) in trenches, sides cum of foundations etc. in layers not exceeding 20cm in depth, consolidating each deposited layer by ramming and watering, lead uo to 50 metres. | 700.00 | cum | 1.00 | 50.00 | 35000.00 | 100.00 | 70000.00 | 258.00 | 180600.00 | 150.00 | 105000.00 | 35000.00 | Master Electric Store
58.00 | Supply and fixing of RCC half round pipe of nominal dia 100mm for cable protection etc. complete as required. | 400.00 | mtr | 1.00 | 320.00 | 128000.00 | 300.00 | 120000.00 | 870.00 | 348000.00 | 500.00 | 200000.00 | 120000.00 | SAURABH ENTERPRISES
59.00 | Supplying and fixing cable route marker with 10cm x 10cm x 5 cm thick GI plate with inscription thereon, boilted/welded to 35mm x 35mm x 6mm angle iron, 60 cm long and fixing the same in ground as required. | 20.00 | each | 1.00 | 600.00 | 12000.00 | 800.00 | 16000.00 | 600.00 | 12000.00 | 350.00 | 7000.00 | 7000.00 | Unique Electro Engineers Pvt. Ltd.
60.00 | Providing and laying in position cement concrete of grade- 1:4:8 (1 cement: 4 coarse sand: 8 graded stone aggregate 40mm nominal size) | 7.00 | cum | 1.00 | 6500.00 | 45500.00 | 8000.00 | 56000.00 | 4002.00 | 28014.00 | 4800.00 | 33600.00 | 28014.00 | MANKHA ELECTROTECH PRIVATE LIMITED
61.00 | Brick work with common burnt clay F.P.S. (non modular) bricks of class designation 7.5 in foundation and plinth in cement mortar 1:4 (1 cement: 4 coarse sand) | 65.00 | cum | 1.00 | 4500.00 | 292500.00 | 5000.00 | 325000.00 | 330.00 | 21450.00 | 6500.00 | 422500.00 | 21450.00 | MANKHA ELECTROTECH PRIVATE LIMITED
62.00 | 12mm cement plaster of mix 1:4 (1 cement: 4 coarse sand) | 220.00 | sqm | 1.00 | 220.00 | 48400.00 | 100.00 | 22000.00 | 150.00 | 33000.00 | 200.00 | 44000.00 | 22000.00 | SAURABH ENTERPRISES
63.00 | Providing and placing in position 100 mm thick Precast RCC Rectangular Covers on masonary chambers of various sizes, of M-25 grade cement concretefor RCC work, including cost of centering, shuttering, reinforcementof 8 mm dia TMT bars of Fe 500 grade @ maximum 100mm c/c on both ways , neat cement punning on finished surface, properly encased on all edges with 1.6 mm thick , 100 mm wide MS sheet duly painted over priming coat , reinforcement to be welded at edges with MS sheet and providing 2 Nos. 12 mm dia bar for hooks etc i/c cost of cartage, all leads & lift, handling at site etc. all complete as per direction of Engineer-in-Charge. | 40.00 | sqm | 1.00 | 1500.00 | 60000.00 | 1200.00 | 48000.00 | 3300.00 | 132000.00 | 1600.00 | 64000.00 | 48000.00 | SAURABH ENTERPRISES
64.00 | Earthing with G.I. earth pipe 4.5 metre long, 40 mm dia including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe etc. with charcoal/ coke and salt as required. | 52.00 | job | 1.00 | 4890.00 | 254280.00 | 6000.00 | 312000.00 | 10500.00 | 546000.00 | 6855.00 | 356460.00 | 254280.00 | Master Electric Store
65.00 | Supplying and laying 6 SWG G.I. wire at 0.50 metre below ground level for conductor earth electrode, including connection/ termination with GI thimble etc. as required. | 6000.00 | mtr | 1.00 | 19.00 | 114000.00 | 25.00 | 150000.00 | 51.00 | 306000.00 | 51.00 | 306000.00 | 114000.00 | Master Electric Store
66.00 | Providing and fixing 25 mm X 5 mm G.I. strip on surface or in recess for connections etc. as required. | 50.00 | mtr | 1.00 | 120.00 | 6000.00 | 100.00 | 5000.00 | 240.00 | 12000.00 | 255.00 | 12750.00 | 5000.00 | SAURABH ENTERPRISES
67.00 | Providing and laying earth connection from earth electrode with 6 SWG dia G.I. Wire in 15 mm dia G.I. pipe from earth electrode including connection with G.I. thimble excavation and re-filling as required. | 30.00 | mtr | 1.00 | 115.00 | 3450.00 | 150.00 | 4500.00 | 330.00 | 9900.00 | 290.00 | 8700.00 | 3450.00 | Master Electric Store
68.00 | Earthing with copper earth plate 600mm x 600mm x 3mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 mtr long etc. with charcoal/coke and salt as required. | 2.00 | job | 1.00 | 16500.00 | 33000.00 | 20000.00 | 40000.00 | 15000.00 | 30000.00 | 26500.00 | 53000.00 | 30000.00 | MANKHA ELECTROTECH PRIVATE LIMITED
69.00 | Providing and fixing 25 mm x 5 mm copper strip on surface or in recess for connections etc. as required. | 20.00 | mtr | 1.00 | 1156.00 | 23120.00 | 1500.00 | 30000.00 | 1257.00 | 25140.00 | 1890.00 | 37800.00 | 23120.00 | Master Electric Store
70.00 | Providing and fixing 25 mm x 5 mm copper strip in 40 mm dia G.l. pipe from earth electrode including connection with brass nut, bolt, spring, washer excavation and re-filling etc. as required. | 10.00 | mtr | 1.00 | 1600.00 | 16000.00 | 1800.00 | 18000.00 | 1860.00 | 18600.00 | 700.00 | 7000.00 | 7000.00 | Unique Electro Engineers Pvt. Ltd.
71.00 | Dismantling of existing street light pole upto 7.5mtr height, including light fixture, disconneting existing cable connections and submitting the dismantled items to AAI/IAF store. | 20.00 | job | 1.00 | 200.00 | 4000.00 | 1000.00 | 20000.00 | 501.00 | 10020.00 | 1500.00 | 30000.00 | 4000.00 | Master Electric Store
72.00 | Dismantling of existing street light pole arm installed on wall including light fixture, disconneting existing cable connections and submitting the dismantled items to AAI/IAF store. | 30.00 | job | 1.00 | 50.00 | 1500.00 | 1000.00 | 30000.00 | 303.00 | 9090.00 | 1000.00 | 30000.00 | 1500.00 | Master Electric Store
| Total in Figures |  |  |  |  | 17177192.00 |  | 18555555.00 |  | 20576883.00 |  | 24522607.00
Lowest Amount Quoted BY: Master Electric Store(17177192.00)

## BOQ Summary
BOQ Summary Details Tender Title: Provision of Apron flood lighting, perimeter Security lighting, Boom Barrier and allied works etc at Agra Airport Tender ID: 2025_AAI_246698_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Master Electric Store (BID ID -903421) | 17177192.00 | L1
| 2 | SAURABH ENTERPRISES (BID ID -900299) | 18555555.00 | L2
| 3 | MANKHA ELECTROTECH PRIVATE LIMITED (BID ID -903859) | 20576883.00 | L3
| 4 | Unique Electro Engineers Pvt. Ltd. (BID ID -899837) | 24522607.00 | L4