## BoQ1
Government eProcurement System Created By: Jagannath singh Deshmukh Created Date/Time: 29-Oct-2025 12:06 PM Tender Title: Construction of MSSR at Rajkot International Airport. SH Provision of Automatic Gas based Fire suppression system and associated works at Rajkot International Airport. Tender ID: 2025_AAI_247395_1
Tender Inviting Authority:Asst.General Manager (E-E)
Name of Work: “Construction of MSSR at Rajkot International Airport. SH: Provision of Automatic Gas based Fire suppression system and associated works at Rajkot International Airport."
Contract No: 2025_AAI_247395_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | advent electric technologies pvt. ltd. (GSTN-07AAJCA2055K1ZN) BID ID -901838 |  | CENTRE TAP ENGINEERING (GSTN-24AGPPP8172K1ZP) BID ID -910977 |  | PYROGUARD ENGINEERS PRIVATE LIMITED (GSTN-07AACCP9466E1Z7) BID ID -911937 |  | SVS Buildwel Pvt Ltd (GSTN-07AALCS7473H1ZU) BID ID -912069 |  | Vasu Infosec Pvt Ltd (GSTN-27AABCV6080D1ZE) BID ID -912308 |  | Kalpataru Industries (GSTN-NA) BID ID -911902
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Design, manufacturing, supply, installation, testing and commissioning of Automatic Gas Suppression System including supply of PESO approved Cylinder, complete with UL / VDS / PESO Approved valve assembly and arrangement for supervisory switch connection for monitoring cylinder pressure, a pressure guage with a safety burst disc, electronic control head / Solenoid, pressure operated control head, flexible hose, strap, NRV, Pressure Switch and a safety cap, required nos. of Nozzles (UL / VDS listed), supply and laying of seamless MS pipe red painted with all fittings and supports, Manifold, Gas Release Panel, manual gas release & abort station, Fire Alarm System,batteries etc. complete as required. - Job includes supply and filling of clean agent suitable for fire class A,B & C etc. as required. CLEAN AGENT (FK-5-1-12) / Inert Gas with Zero Ozone Depletion Potential (ODP), Colourless gas and odour less. (Gas Quantity would be as per the design volume given below and as per the UL / VDS certification.) - The Cylinder, Volume of Gas, Nos. of Nozzles, piping design and pressure calculations using manufacturer design software for a given dimension of room duly approved by manufacturer (OEM) shall be submitted prior to starting of the works. Gas suppression System for following rooms and given approximate volume a) Equipment room - L= 13.00 Mtr, B = 9.85 Mtr, H = 4.0 Mtr b) UPS Room - L= 3.26 Mtr, B = 4.0 Mtr, H = 3.5 Mtr c) Battery Room no 1 - L= 3.33 Mtr, B = 4.0 Mtr, H = 3.5 Mtr d) Battery Room no 2 - L= 3.33 Mtr, B = 4.0 Mtr, H = 3.5 Mtr - Each location shall have its own gas suppression system. - Job includes physical testing for any one of the locations to test the performance of the fire supression system. | 1.00 | Job |  | 2000000.00 | 2000000.00 | 2300000.00 | 2300000.00 | 2146530.00 | 2146530.00 | 1430000.00 | 1430000.00 | 2570350.00 | 2570350.00 | 1972867.00 | 1972867.00 | 1430000.00 | SVS Buildwel Pvt Ltd
1.10 | SITC of 10 Kg Modular Cylinder (Filled with FK 5-1-12 Gas) in Antenna Motor Room having approximate dimensions as L= 2.2 Mtr, B = 2.2 Mtr, H = 2.2 Mtr. | 1.00 | Job |  | 24500.00 | 24500.00 | 100000.00 | 100000.00 | 13800.00 | 13800.00 | 13000.00 | 13000.00 | 33700.00 | 33700.00 | 30927.00 | 30927.00 | 13000.00 | SVS Buildwel Pvt Ltd
2.00 | SITC of 2 cross zone fire alarm control panel with batteries and all other accessories etc. complete as required. The panel shall be capable of activating gas releasing control module upon activation of smoke and/or heat detectors for operating the Gas based fire suppression system. | 4.00 | Each |  | 18000.00 | 72000.00 | 15000.00 | 60000.00 | 27210.00 | 108840.00 | 15600.00 | 62400.00 | 31700.00 | 126800.00 | 29000.00 | 116000.00 | 60000.00 | CENTRE TAP ENGINEERING
3.00 | SITC of Autodialer complete with all necessary accessories including connections etc. as required as per site requirement. | 1.00 | Each |  | 3000.00 | 3000.00 | 10000.00 | 10000.00 | 9680.00 | 9680.00 | 6500.00 | 6500.00 | 7000.00 | 7000.00 | 20300.00 | 20300.00 | 3000.00 | advent electric technologies pvt. ltd.
4.00 | SITC of conventional photo electric smoke detector complete with base. | 26.00 | Each |  | 1050.00 | 27300.00 | 2000.00 | 52000.00 | 960.00 | 24960.00 | 1170.00 | 30420.00 | 1500.00 | 39000.00 | 1750.00 | 45500.00 | 24960.00 | PYROGUARD ENGINEERS PRIVATE LIMITED
5.00 | SITC of addressable manual call point complete as required. | 2.00 | Each |  | 2600.00 | 5200.00 | 5000.00 | 10000.00 | 3340.00 | 6680.00 | 1170.00 | 2340.00 | 3780.00 | 7560.00 | 4250.00 | 8500.00 | 2340.00 | SVS Buildwel Pvt Ltd
6.00 | SITC of conventional flasher sounder unit | 5.00 | Each |  | 450.00 | 2250.00 | 3000.00 | 15000.00 | 710.00 | 3550.00 | 1690.00 | 8450.00 | 3780.00 | 18900.00 | 2760.00 | 13800.00 | 2250.00 | advent electric technologies pvt. ltd.
7.00 | SITC of Response Indicators on surface/recessed MS box having two LED, metallic cover complete with all connections etc. as required. | 10.00 | Each |  | 200.00 | 2000.00 | 500.00 | 5000.00 | 100.00 | 1000.00 | 72.00 | 720.00 | 330.00 | 3300.00 | 195.00 | 1950.00 | 720.00 | SVS Buildwel Pvt Ltd
8.00 | Supply of PVC/ XLPE insulated and PVC sheathed annealed Copper conductor Fire alarm armoured cable of 600/1000 V grade, having steel wire armoring and FRLS outer sheath conforming to IS : 7098 (Part :- I)/1988 with upto date amendments etc. as required of following sizes : a) 2 x 1.5 sqmm | 400.00 | Mtr |  | 140.00 | 56000.00 | 150.00 | 60000.00 | 80.00 | 32000.00 | 143.00 | 57200.00 | 170.00 | 68000.00 | 195.00 | 78000.00 | 32000.00 | PYROGUARD ENGINEERS PRIVATE LIMITED
9.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in masonary open duct etc as required. a) upto 35 sq. mm | 80.00 | Mtr |  | 75.00 | 6000.00 | 100.00 | 8000.00 | 50.00 | 4000.00 | 845.00 | 67600.00 | 80.00 | 6400.00 | 395.00 | 31600.00 | 4000.00 | PYROGUARD ENGINEERS PRIVATE LIMITED
10.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on wall surface/ Cable tray etc as required. a) upto 35 sq. mm | 320.00 | Mtr |  | 75.00 | 24000.00 | 150.00 | 48000.00 | 40.00 | 12800.00 | 845.00 | 270400.00 | 80.00 | 25600.00 | 475.00 | 152000.00 | 12800.00 | PYROGUARD ENGINEERS PRIVATE LIMITED
| Total in Figures |  |  |  |  | 2222250.00 |  | 2668000.00 |  | 2363840.00 |  | 1949030.00 |  | 2906610.00 |  | 2471444.00
Lowest Amount Quoted BY: SVS Buildwel Pvt Ltd(1949030.00)

## BOQ Summary
BOQ Summary Details Tender Title: Construction of MSSR at Rajkot International Airport. SH Provision of Automatic Gas based Fire suppression system and associated works at Rajkot International Airport. Tender ID: 2025_AAI_247395_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | SVS Buildwel Pvt Ltd (BID ID -912069) | 1949030.00 | L1
| 2 | advent electric technologies pvt. ltd. (BID ID -901838) | 2222250.00 | L2
| 3 | PYROGUARD ENGINEERS PRIVATE LIMITED (BID ID -911937) | 2363840.00 | L3
| 4 | Kalpataru Industries (BID ID -911902) | 2471444.00 | L4
| 5 | CENTRE TAP ENGINEERING (BID ID -910977) | 2668000.00 | L5
| 6 | Vasu Infosec Pvt Ltd (BID ID -912308) | 2906610.00 | L6