## BoQ1
Government eProcurement System Created By: Ram Mohan S Created Date/Time: 15-Oct-2025 03:36 PM Tender Title: Extension and re-configuration of Apron Bays for Code-C type of aircraft and allied infrastructure at Hubballi Airport - Electrical works Tender ID: 2025_AAI_247901_1
Tender Inviting Authority: DY. GENERAL MANAGER (ENGG-ELECTRICAL)-II, AAI, HUBBALLI AIRPORT
Name of Work: Extension and Re-configuration of Apron Bays for Code 'C' type of aircraft and allied infrastructure at Hubballi Airport - SH: - Electrical Works
Contract No: 2025_AAI_247901_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Manish Electricals (GSTN-23ABLPM9012E1ZW) BID ID -910095 |  | Balaji Engineering (GSTN-33ADGPV2628A1ZV) BID ID -910208
[5 empty] | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply of following size unarmoured, XLPE insulated & PVC/PE sheathed stranded tinned copper conductor airfield lighting cable of 5 KV grade conforming to IS 7098 Part -II with all amendments upto date.
1.10 | 1 x 6 Sq.mm | 11196.00 | Mtrs |  | 154.00 | 1724184.00 | 140.00 | 1567440.00 | 1567440.00 | Balaji Engineering
1.20 | 1 x 16 Sq.mm | 1722.00 | Mtrs |  | 400.00 | 688800.00 | 350.00 | 602700.00 | 602700.00 | Balaji Engineering
2.00 | Supply of following size armoured, XLPE insulated & PE/PVC sheathed stranded aluminimum conductor cable of 1.1 KV grade conforming to IS 7098 - Part I with all amendments upto date.
2.10 | 4C x 4 Sq.mm | 330.00 | Mtrs |  | 120.00 | 39600.00 | 100.00 | 33000.00 | 33000.00 | Balaji Engineering
2.20 | 4C x 16 Sq.mm | 2156.00 | Mtrs |  | 300.00 | 646800.00 | 250.00 | 539000.00 | 539000.00 | Balaji Engineering
2.30 | 3.5 x 95 Sq.mm | 440.00 | Mtrs |  | 750.00 | 330000.00 | 700.00 | 308000.00 | 308000.00 | Balaji Engineering
2.40 | 3.5 x 120 Sq.mm | 1071.00 | Mtrs |  | 950.00 | 1017450.00 | 900.00 | 963900.00 | 963900.00 | Balaji Engineering
3.00 | Supply of following size armoured, XLPE insulated & PE/PVC sheathed copper conductor control cable conforming to IS 7098 - Part I with all amendments upto date.
3.10 | 19 core x 2.5 Sq.mm | 1176.00 | Mtrs |  | 1200.00 | 1411200.00 | 1000.00 | 1176000.00 | 1176000.00 | Balaji Engineering
3.20 | 4 core x 2.5 Sq.mm | 2156.00 | Mtrs |  | 400.00 | 862400.00 | 300.00 | 646800.00 | 646800.00 | Balaji Engineering
4.00 | Supply of 1.1 KV grade flexible secondary lead with EPR insulated PCP/TPE sheathed of size 2 x 2.5 Sq.mm stranded copper conductor for AGL confirming to relevant IS with up to date ammendments as required | 357.00 | Mtrs |  | 300.00 | 107100.00 | 200.00 | 71400.00 | 71400.00 | Balaji Engineering
5.00 | Supply of 5 KV grade plug and receptacle of type-I class "B" connector suitable for field attachment for following size XLPE insulated PVC sheathed single core copper conductor AFL cable conforming to the relevant IS specification etc. complete as required.
5.10 | 1 x 6 Sq.mm | 108.00 | Nos |  | 900.00 | 97200.00 | 700.00 | 75600.00 | 75600.00 | Balaji Engineering
5.20 | 1 x 16 Sq.mm | 9.00 | Nos |  | 900.00 | 8100.00 | 700.00 | 6300.00 | 6300.00 | Balaji Engineering
6.00 | Supply of elevated type medium intensity LED type taxi way edge light fittings suitable for taxi way edge lighting that uses LED with driver unit (Intensity variation should be there according to CCR intensity steps), complete with lens support mechanism, omni directional blue lens, lens clamping mechanism, lens supporting mechanism, central column assembly, breakable coupling, gaskets, two pin secondary leads of sufficient length, base plate tapped to receive 6 Nos of M-10 bolt along with 6 Nos M-10 stainless steel bolts, nuts, spring wahsers, plian washers and other accessories suitable for the fixing on transformer housing box etc. complete as required, confirming to ICAO aviation visual aid requirements as specified in Annex-14 amended up to date. (Make: As per AAI approved list of makes manufactures who meet ICAO requirement for ISO CANDALA as specified in Annexure- 14. | 30.00 | Each |  | 7500.00 | 225000.00 | 7000.00 | 210000.00 | 210000.00 | Balaji Engineering
7.00 | Supply of bi-directional inset type high intensity halogen runway edge light fitting for runway edge lightings as per ICAO aviation visual aids requirements complete with shallow base and matching body of the fitting, inner body and outer cover made of dia cast aluminium complete with 2 x 105 Watts, 6.6 amps pre-focused reflector halogen lamp with connected heat resistant accessories, prism and prism assesembly, optical assembly, filters, 'O' ring seal, pressure relief test plug, clear lenses and all standard hardware and accessories ready for site installation etc complete as required. (Make: As per AAI approved list of makes manufactures who meet ICAO requirement for ISO CANDALA as specified in Annexure- 14. | 4.00 | Nos |  | 75000.00 | 300000.00 | 60000.00 | 240000.00 | 240000.00 | Balaji Engineering
8.00 | Supply of omini directional inset type, medium intensity LED type taxiway edge light fittings as per ICAO aviation visual aids requirements complete with shallow base and matching body of the fitting, inner body and outer cover made of dia cast aluminium complete with LED driver unit suitable for 6.6 amps series circuit, pre-focused prism assesembly, optical assembly, 'O' ring seal, pressure relief test plug, clear glass/lenses and all standard hardware and accessories ready for site installation etc complete as required. (Make: As per AAI approved list of makes manufactures who meet ICAO requirement for ISO CANDALA as specified in Annexure- 14. | 22.00 | Each |  | 60000.00 | 1320000.00 | 50000.00 | 1100000.00 | 1100000.00 | Balaji Engineering
9.00 | Supply of elevated, LED type high intensity guard light fitting, wig-wag unidirectional yellow with cover tube, sun shield, T bar with breakable coupling base plate, LED driver and flasher unit (falsh rate minimum 45 to 50 flashes per minute per lamp) suitable for working in 6.6A series circuit (taxiway circuit) lenses & filters etc. two pin secondary lead of sufficient length, base plate tapped to receive 6 Nos of M-10 bolt along with 6 Nos M-10 stainless steel bolts, nuts, spring and plain washers and other accessories suitable for the fixing on transformer housing box etc. and with all standard hardware and accessories ready for site installation and as per ICAO aviation visual aid requirements suitable for operation along with taxi way lights etc. complete as required. (Make: As per AAI approved list of makes manufactures who meet ICAO requirement for ISO CANDALA as specified in Annexure- 14. (1 set consist of two lights) | 3.00 | Sets |  | 400000.00 | 1200000.00 | 350000.00 | 1050000.00 | 1050000.00 | Balaji Engineering
10.00 | Supply of 5 KV grade 50Hz series type isolating transformers of following capacity encapsulsted in polyester resin, finally mould in neopprene type rubber with primary & secondary connections and ready to install etc. complete as required.
10.10 | 15 watts 6.6 / 6.6 amps | 50.00 | Each |  | 3200.00 | 160000.00 | 3000.00 | 150000.00 | 150000.00 | Balaji Engineering
10.20 | 100W 6.6/6.6 Amps | 12.00 | Each |  | 5500.00 | 66000.00 | 5000.00 | 60000.00 | 60000.00 | Balaji Engineering
10.30 | 200W 20/6.6 Amps | 5.00 | Each |  | 6500.00 | 32500.00 | 6000.00 | 30000.00 | 30000.00 | Balaji Engineering
11.00 | Design and supply of fully water proof aircraft guidance sign boards of various sizes made out of reinforced anodized aluminum profile with suitable aluminum support both having thickness of min. 2mm and min. 2 mm thick aluminum sheet for side and rear panels. The front facia each signage sheet should be easily removable /openable for easy maintenance. Each signage sheet shall be 4 mm thick, long life imported polycarbonate non-secular sheet surface with letters and symbols made out from 3 M film pasted from inside with required coloring for mandatory / informatory guidance sign as per ICAO standards. Each sign boards should be uniformly and internally illuminated with suitable number of LEDs/LED lamp module/ LED tube light to get that luminance as per ICAO standards alongwith all other accessories such as converter / driver suitable for operating in taxiway AC constant current series system to 6.6A, reflectors, holder, etc., The signage shall be opeated with maximum 100W 6.6/6.6 A isolation transformer and the illumination shall not vary with steps of CCR. Suitable locking arrangement should be provided for the door to secure tightly the board after closing and no water should enter the box. Signboard should have copper secondary leads and copper earthing with 2.5 sqmm size FRLS PVC insulated copper wire up to isolating transformer provided in housing box. Suitable arrangement to be made on the secondary lead with plug and receptacles for connecting to isolation transformer for supply and lugs for connecting to housing box for earthing. Suitable rated DP MCB should be provided inside the signage for isolating the supply. The secondary lead and copper earth wire to be protected with steel wire re-inforced PVC pipe of dia not less than 25mm glanded to the board and to the housing box. The signages should be fixed to min. 50mm dia 5mm thick aluminum legs using stainless steel/aluminium clamps. The lugs shall be fitted to a base plate of thickness not less than 10mm through frangible coupling. The height of the signage should be as decided by Engineer -in -charge. The supply includes all other materials required for installation complete as required and as per the direction of Engineer-In-Charge. The boards should have to meet all the requirement as per ICAO standard amended up to date. | 21.00 | Sq.Mtr |  | 36000.00 | 756000.00 | 30000.00 | 630000.00 | 630000.00 | Balaji Engineering
12.00 | Supply of 10 mm thick 330mm dia CI dummy plate having 6 nos M-10 holes suitable for fixing in the housing box including supply and fixing of neoprene gasket and 6 nos M 10 SS bolt, nuts, spring/plain washers etc . | 24.00 | Each |  | 1400.00 | 33600.00 | 1000.00 | 24000.00 | 24000.00 | Balaji Engineering
13.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of upto 5.0 kV grade of following size in the existing RCC/ HUME/ METAL/HDPE/PVC pipe as required
13.10 | Up to 35 Sq.mm | 17611.00 | Mtrs |  | 15.00 | 264165.00 | 5.00 | 88055.00 | 88055.00 | Balaji Engineering
13.20 | Above 35 Sq.mm up to 95 Sq.mm | 404.00 | Mtrs |  | 15.00 | 6060.00 | 5.00 | 2020.00 | 2020.00 | Balaji Engineering
13.30 | Above 95 Sq.mm up to 185 Sq.mm | 1030.00 | Mtrs |  | 15.00 | 15450.00 | 5.00 | 5150.00 | 5150.00 | Balaji Engineering
14.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of up to 5.0 kV grade of following size in the existing masonry open duct as required.
14.10 | Up to 35 Sq.mm | 735.00 | Mtrs |  | 15.00 | 11025.00 | 5.00 | 3675.00 | 3675.00 | Balaji Engineering
15.00 | Making field connections by crimping 6/16.sq.mm plug and receptacle with the existing 6/16 sq.mm single core GLF cable including filling all the gap with water sealent silicon compound, providing and wrapping with HT insulation tape and over which wrapping with PVC tape etc. as required. | 117.00 | Sets |  | 100.00 | 11700.00 | 50.00 | 5850.00 | 5850.00 | Balaji Engineering
16.00 | Supplying and making straight through joint with heat shrinkable kit including ferrules and other jointing materials for following size PVC/ XLPE insulated and PVC sheathed aluminium conductor cable of 1.1 KV grade as required :
16.10 | 4 x 16 sq.mm. | 2.00 | Sets |  | 4000.00 | 8000.00 | 1000.00 | 2000.00 | 2000.00 | Balaji Engineering
16.20 | 3.5 x 95 sq.mm. | 2.00 | Sets |  | 5000.00 | 10000.00 | 1000.00 | 2000.00 | 2000.00 | Balaji Engineering
16.30 | 3.5 x 120 sq.mm. | 2.00 | Sets |  | 6000.00 | 12000.00 | 1000.00 | 2000.00 | 2000.00 | Balaji Engineering
17.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC/ XLPE insulated and PVC sheathed aluminium conductor cable of 1.1. KV grade as required :
17.10 | 4C x 4 Sq.mm | 21.00 | Set |  | 400.00 | 8400.00 | 100.00 | 2100.00 | 2100.00 | Balaji Engineering
17.20 | 4C x 16 Sq.mm | 25.00 | Set |  | 500.00 | 12500.00 | 200.00 | 5000.00 | 5000.00 | Balaji Engineering
17.30 | 3.5C x 95 Sq.mm | 4.00 | Set |  | 600.00 | 2400.00 | 200.00 | 800.00 | 800.00 | Balaji Engineering
17.40 | 3.5C x 120 Sq.mm | 4.00 | Set |  | 700.00 | 2800.00 | 300.00 | 1200.00 | 1200.00 | Balaji Engineering
18.00 | Supplying and making control cable end termination of following sizes of 1.1 KV grade LT XLPE insulated, PVC sheathed, armoured copper conductor with tinned copper lugs suitable for krone connctors and single compression glands and all necessary materials complete as required
18.10 | 19c x 2.5 Sq.mm | 4.00 | Sets |  | 700.00 | 2800.00 | 500.00 | 2000.00 | 2000.00 | Balaji Engineering
18.20 | 4C x 2.5 Sq.mm | 25.00 | Sets |  | 600.00 | 15000.00 | 400.00 | 10000.00 | 10000.00 | Balaji Engineering
19.00 | Installation of isolation transformer housing boxes of dimension 330mm dia and 450mm height in concrete with a base concrete of 1:2:4 of size 630 x 630 x 100 mm thick all round concrete of 1 : 2 : 4, at 150 mm thick (to be fixed along with concreting of base for signage) with top projecting 20 to 25mm above finished surface, top sloped with 1:2:4 cement to match the surface, providing and fixing of 1.0 mtr long 50mm dia ISI marekd B class GI pipe to the exisitng hole, fixing the pipe with double check nut (one inside and one outside the box), providing and fixing 250 mm long 15 mm dia.ISI marked B class GI pipe for drainage of water including excavation of earth etc. complete as required. | 9.00 | Each |  | 4000.00 | 36000.00 | 1000.00 | 9000.00 | 9000.00 | Balaji Engineering
20.00 | Installation of inset light fittings including fixing of inset light housing box in the concrete runway/taxiway surface by core cutting the surface with suitable core cutting machine tool for the required size for fixing the inset housing box, alignment of the box to match the surface, fixing it using quick setting sealant(dobofil/fosroc or equivalent) compounds, alignment, levelling and making all secondary lead connections to transformer & fittings, making earth connections, testing and commissioning of the whole inset fittings etc complete as required. | 26.00 | Each |  | 6000.00 | 156000.00 | 1000.00 | 26000.00 | 26000.00 | Balaji Engineering
21.00 | Installation of isolation transformer housing boxes of dimenssion 330mm dia and 450mm height (in earth) with a base concrete of 1:2:4 of size 630 x 630 x 100 mm thick all round concrete of 1 : 2 : 4, at 150 mm thick, with top projecting 20 to 25mm above finished surface, top sloped with 1:2:4 cement to match the surface including providing and fixing of 250mm long 15 mm dia.ISI marked B class GI pipe for drainage of water including excavation of earth etc. complete as required. | 17.00 | Each |  | 3000.00 | 51000.00 | 1000.00 | 17000.00 | 17000.00 | Balaji Engineering
22.00 | Installation of elevated type high/medium intensity runway/taxiway light/RGL fittings on the existing transformer housing boxes including, installation of isolating transformers, lens, filters, lamps and other accessories, alignment, levelling and making secondary lead connections to transformer & fittings, making earth connections, testing and commissioning etc. complete as required. | 33.00 | Each |  | 200.00 | 6600.00 | 50.00 | 1650.00 | 1650.00 | Balaji Engineering
23.00 | Providing and laying in position cement concrete of 1:2:4 grade (1 Cement : 2 coarse sand (zone-III) : 4 graded stone aggregate 20 mm nominal size) of 150mm thick which extends all around the aircraft guidance signages with a distance of 2000mm from front phase, and 1000mm each from back, right and left phase of signage including excavation of earth for the PCC, supply and fixing of suitable size stainless steel bolts with templates matching to the signage leg base plate holes in the concrete where ever signage legs are to be mounted. The concrete base shall be 20-25mm above the ground level and all sides and shall be chamferred on all sides from the concrete base top not less than 30cm below the strip surface area etc complete as required. | 15.00 | Cum |  | 6000.00 | 90000.00 | 3000.00 | 45000.00 | 45000.00 | Balaji Engineering
24.00 | Installation of aircraft guidance signages of various sizes on the existing bolts of concrete platform using stainless steel nuts , making all electrical/earth connections inside signage and to isolation transformer testing and commissioning etc complete as required. | 9.00 | Nos |  | 5000.00 | 45000.00 | 500.00 | 4500.00 | 4500.00 | Balaji Engineering
25.00 | Laying of 2 x 2.5 Sq.mm AFL secondary lead cable in the existing RCC/ HUME/ METAL/HDPE/PVC pipe etc complete as required. | 357.00 | Mtrs |  | 15.00 | 5355.00 | 5.00 | 1785.00 | 1785.00 | Balaji Engineering
26.00 | Earthing with G.l. earth pipe 4.50 meter long,40 mm dia including ISI marked B class GI pipe and accessories, drilling the bore of required dia and depth, providing concrete enclosure with concrete cover of size 450 x 450 x 300mm masonry enclosure with cover plate having locking arrangement and watering pipe etc. with charcoal/coke and salt as required. | 28.00 | Sets |  | 4800.00 | 134400.00 | 4000.00 | 112000.00 | 112000.00 | Balaji Engineering
27.00 | Providing and laying earth connection from earth electrode with 4.00 mm dia bare copper conductor in 15 mm dia ISI mareked B class G.I. pipe from earth electrode including connection with copper thimble excavation and re-filling as required. (excavation and refilling excluded) | 55.00 | Mtrs |  | 400.00 | 22000.00 | 300.00 | 16500.00 | 16500.00 | Balaji Engineering
28.00 | Providing and laying of 4mm (8 SWG) dia bare copper conductor along with cable in the exisitng trench/pipe, making all conncectoins etc complete as required. | 20021.00 | Mtrs |  | 120.00 | 2402520.00 | 100.00 | 2002100.00 | 2002100.00 | Balaji Engineering
29.00 | Providing & fixing 25mm x 5 mm G.I strip in 40mm dia ISI marked B class GI pipe from earth electrode including connection with G.l. nut, bolt, spring, washer as required (Excavation and refilling not included) | 26.00 | Mtrs |  | 750.00 | 19500.00 | 650.00 | 16900.00 | 16900.00 | Balaji Engineering
30.00 | Providing & fixing 25mm x 5mm G.I strip from earth electrode including connection with G.l. nut, bolt, spring, washer as required (Excavation and refilling not included) | 55.00 | Mtrs |  | 250.00 | 13750.00 | 200.00 | 11000.00 | 11000.00 | Balaji Engineering
31.00 | Excavation of trenches for cable/pipe laying in all kind of soil with suitable width and depth (nominal 35cm width and 80cm in depth) including dressing of sides, lift upto 1.5 m, getting out the excavated soil, refilling available earth after laying of cable/ pipe etc in layers of 20 cm, ramming, watering and disposal of surplus excavated soil as directed, within a lead of 50 metres. | 531.00 | Cum |  | 150.00 | 79650.00 | 100.00 | 53100.00 | 53100.00 | Balaji Engineering
32.00 | Excavation of trenches for cable/pipe laying in laterite/soft rock by mechanical/manual means with suitable width and depth (nominal 35cm width and 80cm in depth), including dressing of sides, lift upto 1.5 m, getting out the excavated soil, refilling available earth after laying of cable/ pipe etc in layers of 20 cm, ramming, watering and disposal of surplus excavated soil as directed, within a lead of 50 metres. | 797.00 | Cum |  | 300.00 | 239100.00 | 200.00 | 159400.00 | 159400.00 | Balaji Engineering
33.00 | Supplying and laying of following size DWC HDPE pipe ISI marked along with all accessories like socket, bend, couplers, T bends/joints etc. conforming to IS 14930, Part II complete with fitting and cutting, jointing etc. in the existing trench, complete as required. - 63mm Dia (63mm OD, 50mm ID Nominal) | 4673.00 | Mtrs |  | 165.00 | 771045.00 | 150.00 | 700950.00 | 700950.00 | Balaji Engineering
34.00 | Design, Supply, Installation, Testing and Commissioning of feeder piller with minimum dimenssion of 1200x1200x300mm or more as per design, outdoor, cubicle type, double door made out of 14 swg CRCA sheet steel, totally enclosed, dust and vermin proof, compartmentalised, powder coated suitable for operation on 3 Phase and neutral, 415v, 50 Hz AC supply system with aluminium busbars, suitable connectors, cable alley for terminations of cable from brakers, interconnections with suitable size solid aluminium/copper strips/or copper wires from busbar and also to connectors, meters etc. 2 way, 20 pair din rail terminal blocks (for connecting control cables), all internally wired, having following incomer and outgoing MCCB's complete with releases for protection, electrical & mechanical interlock etc complete as required as per items and as per specifications: Incomer MCCB, Ics=Icu 25 kA, 4 Pole, thermo-magnetic release, over load setting 80% - 100% and with suitable roatary operating mechanism, spreader links etc: 1) 125 Amps - 2 Nos Incomer shall have one set of the following items all internally wired: 1) 1 set of LED type indication Lamps, comprising of Phase indication R,Y,B and breaker 'ON' , 'OFF', indiactions wired with control MCB. 2)Digital MFM Class 0.05 which reads V, A, F, PF, KW, KVA with suitable CT calss 0.5 and in built selector switch 3)Ammeter (0-100 A) digital type with suitbale CT and ini built selector switch Bus coupler MCCB, Ics= Icu 25 kA, 4 Pole, thermo-magnetic release, over load setting 80% - 100% and with suitable roatary operating mechanism, spreader links etc: 1) 125 Amps - 1 Nos Bus bar 250 A 4P aluminium bus bars with colour coded heat shrinkable sleeves supported on non hygroscopic bus supports Out Goings MCCB, Ics = Icu= 25KA 4 Pole, with thermo-magnetic release, over load setting 80% - 100% and with suitable rotary operating mecahnism, spreader links: 1) 63 Amps - 8 Nos 2) Spare cubicle - Provision for fixing 100A MCCB - 2 No Each outgoing shall have one set of the following items all internally wired: 1) Ammeter (0-100 A) digital type with suitbale CT and ini built selector switch 2) 1 set of LED type indication Lamps, comprising of suppy indication RED, breaker 'ON' (RED) indiactions wired with control MCB. | 2.00 | Each |  | 100000.00 | 200000.00 | 75000.00 | 150000.00 | 150000.00 | Balaji Engineering
35.00 | Removal of inset light fittings including shallow housing box from different locations in runway/taxiway/edge area including dismantling of all round concrete/bitumin of housing box, removal of all the debris from site, transportation of fittings to AAI store, stacking etc. as per the direction of Engineer in Charge complete as required. | 10.00 | Nos |  | 1000.00 | 10000.00 | 500.00 | 5000.00 | 5000.00 | Balaji Engineering
36.00 | Removal of old isolation transformer housing boxes from different locations in runway/taxiway/edge area after dismantling of all round concrete foundation, refilling of excavated portion with cement concrete upto existing level of runway and matching with surface, making good to the original shape and strength, removal of all the debris from site, transportation of fittings to AAI store, stacking etc. as per the direction of Engineer in Charge complete as required. | 10.00 | Nos |  | 2000.00 | 20000.00 | 500.00 | 5000.00 | 5000.00 | Balaji Engineering
37.00 | Numbering / nomenclature of AGL light fixtures, high masts, panels after providing a suitable size with runway yellow enamel paint and stenciling with black enamel paint on it etc. completed as required as per direction of Engineer-in-Charge | 50.00 | Nos |  | 200.00 | 10000.00 | 50.00 | 2500.00 | 2500.00 | Balaji Engineering
38.00 | Identifying and removing/retrival of existing cables from duct banks/trenches including earthing wire, , other accessories etc. without damaging and shifting to AAI store etc complete as required. | 1.00 | Job |  | 5000.00 | 5000.00 | 500.00 | 500.00 | 500.00 | Balaji Engineering
39.00 | Supply , Installation Testing and Commissioning of 30 m High Mast System totally hot dip galvanised in three sections suitable for wind speed of 39 m/sec, along with raising lowering system comprising of head frame, luminaries carriage suitable to install 8 nos luminaries in asymmetrical arrangement, double drum winch, 6 mm diameter SS wire rope, trailing cable, connectors, integral power tool motor, manual handle, junction box, 01set of lightning arrestor finial, LED type aviation obstruction lamps (1 set comprising 2 LED lamps) foundation bolts etc. on suitable foundation, including civil works for foundation, casting of concrete foundation as per manufacturer's design and site conditions and as per technical specifications attached along with following luminaires and control panel complete as required. 1. 400W LED floodlight type -8 Nos. 2. Feeder pillar- Incomer 63A 4P MCCB, single dial time switch, 25A TP contactor for the automatic switching of luminaries, power tool control with 2 nos of 9A contactors and raise lower push button. 3. All round barricading at a height of 500mm from the ground using 80mm dia ISI marked heavy duty GI pipe with intermediate supports, painting the baricade with red and white colour with dimensions as required by EIC 4. All electrical wiring & inter connection etc. from control panel to luminaires. | 4.00 | Nos |  | 450000.00 | 1800000.00 | 425000.00 | 1700000.00 | 1700000.00 | Balaji Engineering
40.00 | Supply , Installation Testing and Commissioning of 20 m High Mast System totally hot dip galvanised in three sections suitable for wind speed of 39 m/sec, along with raising lowering system comprising of head frame, luminaries carriage suitable to install 8 nos luminaries in asymmetrical arrangement, double drum winch, 6 mm diameter SS wire rope, trailing cable, connectors, integral power tool motor, manual handle, junction box, 01set of lightning arrestor finial, LED type aviation obstruction lamps (1 set comprising 2 LED lamps) foundation bolts etc. on suitable foundation, including civil works for foundation as per manufacturer's design and site conditions and as per technical specifications attached along with following luminaires and control panel complete as required. 1. 400 W LED floodlight type -8 Nos. 2. Feeder pillar- Incomer 63A 4p MCCB, single dial time switch, 25A TP contactor for the automatic switching of luminaries, power tool control with 2 nos of 9A contactors and raise lower push button. 3. All round barricading at a height of 500mm from the ground using 80mm dia ISI marked heavy duty GI pipe with intermediate supports, painting the baricade with red and white colour with dimensions as required by EIC 4. All electrical wiring & inter connection etc. from control panel to luminaires. | 2.00 | Nos |  | 400000.00 | 800000.00 | 375000.00 | 750000.00 | 750000.00 | Balaji Engineering
41.00 | Carrying out chase cutting on the concrete runway/taxiway/GSE/road surface with suitable chase cutting tools to a required depth to match the cable entry hole of inset housing box and width to accommodate the pipe, chipping the slot, removal of the debris from the site, etc complete as required. | 357.00 | Mtrs |  | 400.00 | 142800.00 | 200.00 | 71400.00 | 71400.00 | Balaji Engineering
42.00 | Constructing brick masonry chamber 230mm thick wall with common burnt clay F.P.S. (non modular) bricks of class designation 7.5 in cement mortar 1:4 (1 cement : 4 coarse sand) with R.C.C top slab with 1:1.5:3 mix (1 cement : 1.5 coarse sand (zone-III) : 3 graded stone aggregate 20mm nominal size), foundation concrete 1:4:8 mix (1 cement : 4 coarse sand (zone-III) : 8 graded stone aggregate 40mm nominal size), inside plastering 12 mm thick with cement mortar 1:3 (1 cement : 3 coarse sand) finished with floating coat of neat cement, inside size 120x90 cm and 90 cm deep, providng and fixing of 40x40x3mm angel iron frame at the inner edge of RCC, providing and fixing of 10mm thick MS cover plate with lifting handles, providing and fixing of 90mm OD DWC HDPE sleeves 5 Nos on three sides of the chamber at suitable height including end caps etc complete as required. Suitable holes as directed by EIC shall be provided in the PCC for water drain. The drawings shall be get approved by EIC . | 9.00 | Nos |  | 12000.00 | 108000.00 | 10000.00 | 90000.00 | 90000.00 | Balaji Engineering
43.00 | Making Horizontal drilling(HDD) by trencheless directional drilling (HDD) method by deploying HDD machines under runway/taxiway in depth of not less than 1.5 mtrs suitable to lay 110 mm dia pipe supply and laying of 110 mm dia HDPE pipe of PN6 P80 of approved make through the drilled holes leaving 2 mtr extra on both the ends matching with existing cable chamber etc. complete as required. | 155.00 | Mtrs |  | 600.00 | 93000.00 | 200.00 | 31000.00 | 31000.00 | Balaji Engineering
44.00 | Supply of fully water proof triangular SNI (Standard Number Indicator) & rectangular WGS (World Geodetic Systems) signage of following face area to indicate SNI & WGS coordinates at stand, fabricated with suitable opening for easy maintenance made of reinforced 2mm thick anodized aluminium profile with suitable support. The rear and side panel shall be made of 2mm thick aluminium sheet & proper re-inforcement with ready to install fitting for mounting on pole or facade. The long life facia shall be UV stabilized polycarbonate face of 4mm thickness with special adhesive and vinyl pasting from inside of polycarbonate face. The board shall have hinged front face to allow easy access for maintenance. The boards shall be internally and uniformly illuminated with LEDs as per approved make which is mounted on strips or as per design of OEM to get the illuminatin as mentiond in ICAO document. All other accessories including having individual LED drivers shall work on 230V AC supply complete with all internal wiring, connectors. The board shall be in aviation yellow colour or any other colour as decided by EIC
44.10 | SNI , Triangular shape, face size 1280mm x 600mm x 1852 (for two letters) | 10.00 | Nos |  | 40000.00 | 400000.00 | 35000.00 | 350000.00 | 350000.00 | Balaji Engineering
44.20 | WGS , Rectangular shape, face size 1900mm x 700mm x 175mm | 10.00 | Nos |  | 45000.00 | 450000.00 | 36000.00 | 360000.00 | 360000.00 | Balaji Engineering
45.00 | Providing support structure for installation of SNI and WGS signage (single support for both as per note below) with GI pipe including providing 6 Mtr long 100 mm dia ISI marked B class GI pipe, providing 1.5 mtr long 50mm dia ISI marked GI pipe (for cable entry), providing and fixing of base plate of size 300mm x 300mm x 10 mm thickness to the GI pipes (cable entry pipe shall be on the back side of the main pipe), providng holes to accomodate 16 mm dia foundation bolts, providing and fixing of 5mm thick triangular support plate of minimum dimension of 300 x 300 on the top of 100 mm pipe for fixing triangular SNI signage and 2 nos of 1000mm length C channel of dimenssion of minimum 75 x 40 x 2 mm for fixing WGS signage on the pole, providng suitable hole for bolting both the signages, providng cement concrete of ratio 1:1.5:3 for foundation of 1 mtr (L) x 1 mtr (W) x 1 mtr (D) including excavation, curing etc. providng and fixing foundation bolts of 16mm dia, 900 mm length in the concrete foundation matching to the base plate hole, providing and fixing of 50mm dia (ID) DWC HDPE pipe inside the foundation for cable entry, fixing of bay idientification siganges on the support structure, providng and drawing 3C x 1.5 Sq.mm PVC insualted PVC round sheathed copper conductor flexible cable from signage connectors interconnecting both signages upto the bottom of the pipe for conenting to MCB, erection of the whole unit, making all necessary electrical interconnections etc, testing, commissioning etc complete as required. Note: - This item is for ITC of signages mentioned in Sl No 44(a) and 44(b) and both shall be installed on the same pole. On the top portion SNI shall be installed and below it WGS shall be installed as per the direction of EIC) | 10.00 | Nos |  | 16000.00 | 160000.00 | 11000.00 | 110000.00 | 110000.00 | Balaji Engineering
46.00 | Supply of thermo plastic cable junction boxes with minimum size of 250x200x105 (LxBxH) mm having IP 65 protection and having metric knock outs for minimum two cable entry, earthing terminals and with cable connecting studs of minimum 8 terminals suitable for connecting of 3C X 6 sq mm size PVC/ XLPE insulated PVC sheathed armoured power cable, providing and fixing din rail suitbale for fixing MCBs, providing and fixing of C series 6A DP MCB, fixing the whole unit on the pole/wall using clamps, making all interconnections, testing and commissioning etc complete as required. | 10.00 | Nos |  | 2100.00 | 21000.00 | 1500.00 | 15000.00 | 15000.00 | Balaji Engineering
| Total in Figures |  |  |  |  | 19699954.00 |  | 16433275.00
Lowest Amount Quoted BY: Balaji Engineering(16433275.00)

## BOQ Summary
BOQ Summary Details Tender Title: Extension and re-configuration of Apron Bays for Code-C type of aircraft and allied infrastructure at Hubballi Airport - Electrical works Tender ID: 2025_AAI_247901_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Balaji Engineering (BID ID -910208) | 16433275.00 | L1
| 2 | Manish Electricals (BID ID -910095) | 19699954.00 | L2