## BoQ1
Government eProcurement System Created By: ANIL KUMAR Created Date/Time: 18-Nov-2025 01:37 PM Tender Title: Augmentation of Airconditioning System in Terminal Building at CE Hindon Tender ID: 2025_AAI_248744_1
Tender Inviting Authority: AGM (Engg.-Electrical), AAI, Civil Enclave, Hindon Airport, Ghaziabad, Uttar Pradesh
Name of Work: Augmentation of Air-conditioning System in Terminal Building at CE Hindon
Contract No: Tender Id: 2025_AAI_248744_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Superior Aircon Pvt. Ltd. (GSTN-07AALCS0647P2ZQ) BID ID -912050 |  | BRITE INDUSTRIES (GSTN-09AAKFM6551E1Z4) BID ID -913875 |  | aircon engineers (GSTN-NA) BID ID -912039 |  | AIR DESIGN SOLUTIONS (GSTN-NA) BID ID -913395
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply Installation Testing and Commissiong of 160 HP Hot & Cool VRF/VRV System comprises of outdoor VRF units (Minimum capacity of each unit 20 HP) and floor mounted high static tower type indoor units each of capacity not less than 8 TR, complete with interconnecting copper piping, electrical cabling, drain piping, (excluding cost of copper piping, drain piping and electrical cabling and same shall be measeured and paid as per separate BOQ item) mounting stand, centralized remote control unit etc. complete as required as per site requirement. (The VRF/VRV units shall have the ISEER values as defined in ECSBC 2024) | 1.00 | Job |  | 5580000.00 | 5580000.00 | 6984000.00 | 6984000.00 | 5280000.00 | 5280000.00 | 5960795.00 | 5960795.00 | 5280000.00 | aircon engineers
2.00 | Supply & Installation of copper refrigerent piping of sizes as per OEM design requirement alongwith accessories like bend, coupler, Y connection etc insulated with 19mm thick closed cell elastomeric nitrile tubular insulation between each set of indoor & outdoor units as per specifications properly supported and fixed on floor/ wall/ cable tray with hangers/clamps etc. complete as required (Cost of cable tray not included in this item). | 538.00 | Mtr |  | 1500.00 | 807000.00 | 1200.00 | 645600.00 | 1750.00 | 941500.00 | 1500.00 | 807000.00 | 645600.00 | BRITE INDUSTRIES
3.00 | Supply & Installation of PVC Drain Piping of minimum dia 50mm complete with fittings like, bend, tee, etc. supports as per specifications and duly insulated with 9 mm thick closed cell nitrile rubber insulation etc. complete as required. | 210.00 | Mtr |  | 200.00 | 42000.00 | 370.00 | 77700.00 | 250.00 | 52500.00 | 150.00 | 31500.00 | 31500.00 | AIR DESIGN SOLUTIONS
4.00 | Supply & Installation of control cum Interconnecting copper cable between indoor & outdoor units and from AC unit to the centralised remote control unit laid through suitable size of PVC conduit etc. complete as required. (3Cx2.5 Sq mm) | 538.00 | Mtr |  | 200.00 | 107600.00 | 120.00 | 64560.00 | 180.00 | 96840.00 | 187.00 | 100606.00 | 64560.00 | BRITE INDUSTRIES
5.00 | Dismantling, Shifting and Reinstalltion of Existing 26 HP VRF unit alongwith 3 nos. Floor mounted Indoor Unit of LG Make VRF system including Pumpdown, vaccumising and leak testing, toping of refrigerent, testing & commissiong as per direction of EIC . [Complete VRF unit consists of 1 No 26 HP Outdoor unit and 3 Nos Indoor units ( 8 TR Floor mounted unit -2 Nos and 4 TR Floor mounted unit -1 Nos)] | 1.00 | Job |  | 150000.00 | 150000.00 | 195000.00 | 195000.00 | 180000.00 | 180000.00 | 77800.00 | 77800.00 | 77800.00 | AIR DESIGN SOLUTIONS
6.00 | SITC of 4.0 TR Hot & Cool, 5 Star Rating Inverter type Floor mounted Tower Type Air-Conditioner with stabliser free operation suitable for 415 V+/(-)10% AC, 3 phase supply complete with refrigerant, interconnection between indoor & outdoor unit with suitable size copper flexible wire, refrigerant and drain piping up to 4 Mtrs etc. with copper condenser & evaporator coils, mounting stand for indoor and outdoor units etc. complete as required. | 3.00 | Job |  | 200000.00 | 600000.00 | 260000.00 | 780000.00 | 175000.00 | 525000.00 | 120816.00 | 362448.00 | 362448.00 | AIR DESIGN SOLUTIONS
7.00 | Supplying and installing following size of perforated Hot Dipped Galvanised Iron cable tray (Galvanisation thickness not less than 50 microns) with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with G.I. suspenders/mounted on wall/structure with MS angle (35x35x5 mm) including G.I. bolts & nuts, etc. as required.
7.10 | 300 mm width X 50 mm depth X 1.6 mm thickness | 411.00 | Mtr. |  | 800.00 | 328800.00 | 650.00 | 267150.00 | 1250.00 | 513750.00 | 618.00 | 253998.00 | 253998.00 | AIR DESIGN SOLUTIONS
7.20 | 600 mm width X 50 mm depth X 2.0 mm thickness | 150.00 | Mtr. |  | 1500.00 | 225000.00 | 1375.00 | 206250.00 | 1470.00 | 220500.00 | 1118.00 | 167700.00 | 167700.00 | AIR DESIGN SOLUTIONS
8.00 | Supplying and installing following size of Ladder Type Hot Dipped Galvanised Iron cable tray (Galvanisation thickness not less than 50 microns), in convenient sections, joined with connectors, suspended from the ceiling with G.I. suspenders/mounted on wall/structure with MS angle (35x35x5 mm) including G.I. bolts & nuts, etc. as required.
8.10 | 450 mm width X 50 mm depth X 2 mm thickness | 250.00 | Mtr. |  | 800.00 | 200000.00 | 560.00 | 140000.00 | 1750.00 | 437500.00 | 850.00 | 212500.00 | 140000.00 | BRITE INDUSTRIES
9.00 | Supply of XLPE/PVC insulated, PVC sheathed aluminium conductor armoured power cable of 1.1KV grade confirming to IS 7098 (Part I) 1978 with upto date amendments etc as required of the following sizes:
9.10 | 4CX25 Sqmm | 300.00 | Mtr. |  | 300.00 | 90000.00 | 180.00 | 54000.00 | 550.00 | 165000.00 | 250.00 | 75000.00 | 54000.00 | BRITE INDUSTRIES
9.20 | 3.5CX150 Sqmm | 300.00 | Mtr |  | 1250.00 | 375000.00 | 700.00 | 210000.00 | 970.00 | 291000.00 | 815.00 | 244500.00 | 210000.00 | BRITE INDUSTRIES
9.30 | 3.5CX300 Sqmm | 1200.00 | Mtr |  | 2500.00 | 3000000.00 | 1350.00 | 1620000.00 | 2850.00 | 3420000.00 | 1640.00 | 1968000.00 | 1620000.00 | BRITE INDUSTRIES
9.40 | Supply of 1X16 Sqmm PVC/XLPE insulated copper conductor single core flexible power cable ISI marked. | 100.00 | Mtr |  | 400.00 | 40000.00 | 590.00 | 59000.00 | 350.00 | 35000.00 | 315.00 | 31500.00 | 31500.00 | AIR DESIGN SOLUTIONS
10.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on cable tray as required. Upto 35 sq. mm (clamped with 1mm thick saddle) | 230.00 | Mtr |  | 100.00 | 23000.00 | 70.00 | 16100.00 | 270.00 | 62100.00 | 80.00 | 18400.00 | 16100.00 | BRITE INDUSTRIES
11.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on wall surface as required. Upto 35 sq. mm (clamped with 1mm thick saddle) | 70.00 | Mtr |  | 100.00 | 7000.00 | 70.00 | 4900.00 | 270.00 | 18900.00 | 80.00 | 5600.00 | 4900.00 | BRITE INDUSTRIES
12.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. 4 X 25 sq. mm (28mm) | 16.00 | Set |  | 1000.00 | 16000.00 | 3000.00 | 48000.00 | 500.00 | 8000.00 | 300.00 | 4800.00 | 4800.00 | AIR DESIGN SOLUTIONS
13.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing masonry open duct as required. Above 95 sq. mm and upto 185 sq. mm | 60.00 | Mtr |  | 150.00 | 9000.00 | 200.00 | 12000.00 | 270.00 | 16200.00 | 100.00 | 6000.00 | 6000.00 | AIR DESIGN SOLUTIONS
14.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/ HUME/HDPE/METAL pipe etc. as required. Above 95 sq. mm and upto 185 sq. mm | 240.00 | Mtr |  | 150.00 | 36000.00 | 200.00 | 48000.00 | 270.00 | 64800.00 | 110.00 | 26400.00 | 26400.00 | AIR DESIGN SOLUTIONS
15.00 | Supplying and laying of following size DWC HDPE pipe ISI marked along with all accessories like socket, bend, couplers etc. conforming to IS 14930, Part II complete with fitting and cutting, jointing etc.direct in ground (75 cm below ground level) including excavation and refilling the trench but excluding sand cushioning and protective covering etc., complete as required. 120 mm dia (OD-120 mm & ID-103 mm nominal) | 200.00 | Mtr. |  | 600.00 | 120000.00 | 175.00 | 35000.00 | 1250.00 | 250000.00 | 195.00 | 39000.00 | 35000.00 | BRITE INDUSTRIES
16.00 | Supplying and making end termination with brass compression gland and aluminium lugs for 3.5 X 150 sq. mm (50mm) size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. | 4.00 | Each |  | 1500.00 | 6000.00 | 6500.00 | 26000.00 | 400.00 | 1600.00 | 650.00 | 2600.00 | 1600.00 | aircon engineers
17.00 | Supply and Laying of 160 mm dia HDPE pipe (ISI mark, PN6 & PE80 grade and as per relevant IS amended upto date) along with its necessary accessories like couplers, end plugs etc below the ground (including road crossing, cement concrete area) at a depth of 1.5-4.5 Mtr by horizontal directional drilling etc. complete as required after doing ground penetrating radar survey and submitting its report of the underground utilities as required. | 800.00 | Mtr |  | 2000.00 | 1600000.00 | 230.00 | 184000.00 | 1250.00 | 1000000.00 | 650.00 | 520000.00 | 184000.00 | BRITE INDUSTRIES
18.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/ HUME/HDPE/ METAL pipe etc. as required. Above 185 sq. mm and upto 400 sq. mm | 850.00 | Mtr |  | 180.00 | 153000.00 | 300.00 | 255000.00 | 270.00 | 229500.00 | 125.00 | 106250.00 | 106250.00 | AIR DESIGN SOLUTIONS
19.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing masonry open duct as required. Above 185 sq. mm and upto 400 sq. mm | 165.00 | Mtr |  | 180.00 | 29700.00 | 350.00 | 57750.00 | 270.00 | 44550.00 | 125.00 | 20625.00 | 20625.00 | AIR DESIGN SOLUTIONS
20.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on cable tray as required. Above 185 sq. mm and upto 400 sq. mm (clamped with 40x3mm MS flat clamp) | 695.00 | Mtr |  | 180.00 | 125100.00 | 350.00 | 243250.00 | 270.00 | 187650.00 | 150.00 | 104250.00 | 104250.00 | AIR DESIGN SOLUTIONS
21.00 | Supplying and making end termination with brass compression gland and aluminium lugs for 3.5 X 300 sq. mm (70mm) size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. | 10.00 | Each |  | 2000.00 | 20000.00 | 8500.00 | 85000.00 | 1800.00 | 18000.00 | 850.00 | 8500.00 | 8500.00 | AIR DESIGN SOLUTIONS
22.00 | SITC of outdoor type panel with double door weather proof protection fabricated from 14 SWG MS sheet duly inhibited dust and vermin proof and powder coated complete with rubber gasket, hinged, having IP 65 ingress protection, doors, removable 3mm thick gland plate for cable entry, Contineous earth strips with provision of connection of 2 nos earths at both ends. Oudoor panel to be installed on the angle iron stand made of MS angle of size 50mmx5mm having four legs and to be mounted/grouted on plateform/floor etc. complete as required comprisis of following switchgear: 1) 400 A 4 Pole aluminium busbar chamber with DMC/SMC supporting insulators and MS shrouding - 1 set. 2) 400 A 50KA FP MCCB - 2 Nos (For Incomings) 3) 400 A 50KA FP MCCB -01 No (Buscoupler) 4) 63 A 36 KA FP MCCB -7 Nos , (Outgoing) 5) 4P 10KA MCB 63 A- 3 Nos, (Outgoing) 6) 2P 10KA MCB 16 A- 3 Nos (For outgoings) 7) 96 Sqmm 3 phase digital multi function meter with inbuilt selector switch to read V, A, Hz, PF, KW, KVA, KWH & Harmonis, having RS485 communication port with suitable rating CTs. of Class 1.0 - 2 Sets for incomers 8) Phase reversal/failture relay- 2 Sets for incomers 9)R,Y,B LED indicating lamps with 3 nos. control 6 Amp SP MCB -2 Sets for incommers. 10) Rotary handles for all MCCBs. | 2.00 | Each |  | 350000.00 | 700000.00 | 650000.00 | 1300000.00 | 270000.00 | 540000.00 | 446000.00 | 892000.00 | 540000.00 | aircon engineers
23.00 | SITC of outdoor type panel with double door weather proof protection fabricated from 14 SWG MS sheet duly inhibited dust and vermin proof and powder coated complete with rubber gasket, hinged, having IP 65 ingress protection, doors removable 3mm thick gland plate for cable entry, Contineous earth strips with provision of connection of 2 nos earths at both ends. Oudoor panel to be installed on the angle iron stand made of MS angle of size 50mmx5mm having four legs and to be mounted/grouted on plateform/floor etc. complete as required comprisis of following switchgear: 1) 200 A 4 Pole aluminium busbar chamber with DMC/SMC supporting insulators and MS shrouding - 1 set. 2) 200 A 36 KA FP MCCB - 2 Nos (For Incomings) 3) 200 A 36 KA FP MCCB - 1 No (Buscoupler) 4) 63 A 36KAFP MCCB -4 Nos , 5) 4P 10KA MCB 63 A- 2 Nos, (Outgoing) 6) 2P 10KA MCB 16 A- 2 Nos (For outgoings) 7) 96 Sqmm 3 phase digital multi function meter with inbuilt selector switch to read V, A, Hz, PF, KW, KVA, KWH & Harmonis having RS485 communication port with suitable rating CTs. of Class 1.0 - 2 Sets for incomers 8) Phase reversal/failture relay- 2 Sets for incomers 9)R,Y,B LED indicating lamps with 3 nos. control 6 Amp SP MCB -2 Sets for incommers. 10) Rotary handles for all MCCB. | 1.00 | Each |  | 225000.00 | 225000.00 | 350000.00 | 350000.00 | 270000.00 | 270000.00 | 316000.00 | 316000.00 | 225000.00 | Superior Aircon Pvt. Ltd.
24.00 | SITC of maintenance free earthing with copper earth electrode made of UL Listed copper electrode with company name marked on electrod of diameter- 17.2 mm, Length- 3 meters, Tested according to IEC / EN 62561- 2, UL 467, alongwith 20 kg Carbon based backfill/earthing compound having Resistivity- < 0.12 ΩM, Complying to IEC 62561-7, duly testedand Certified from NABL accredited Laboratories, SS 316 grade/brass clamp to terminate the earthing conductor, Poly plastic pit cover etc. complete as required. | 21.00 | Set |  | 10000.00 | 210000.00 | 25000.00 | 525000.00 | 4500.00 | 94500.00 | 12500.00 | 262500.00 | 94500.00 | aircon engineers
25.00 | Providing and fixing 25mm X 5mm Copper strip on surface or in recess for connections etc. as required. | 250.00 | Mtr. |  | 1200.00 | 300000.00 | 1450.00 | 362500.00 | 650.00 | 162500.00 | 200.00 | 50000.00 | 50000.00 | AIR DESIGN SOLUTIONS
26.00 | Supply & laying of 63 mm PN-16 HDPE pipe in floor by cutting the tile precisely and excavation in hard concrete floor inside the Terminal Building upto a depth of 200-250 mm and width 150-200 mm using tile cutting machine and concrete breaker during non operational hours and repairing the same after laying of HDPE pipe with cement concrete and providing and fixing similar colour 10 mm thick new vitrified tiles by cutting the same precisely in suitable size and fixing with cement concrete etc. complete as required. | 180.00 | RM |  | 1000.00 | 180000.00 | 65.00 | 11700.00 | 1500.00 | 270000.00 | 300.00 | 54000.00 | 11700.00 | BRITE INDUSTRIES
27.00 | Constructing brick masonry manhole in cement mortar 1:4 ( 1 cement : 4 coarse sand ) with R.C.C. top slab with 1:1.5:3 mix (1 cement : 1.5 coarse sand (zone-III) : 3 graded stone aggregate 20 mm nominal size), foundation concrete 1:4:8 mix (1 cement : 4 coarse sand (zone-III) : 8 graded stone aggregate 40 mm nominal size), inside plastering 12 mm thick with cement mortar 1:3 (1 cement: 3 coarse sand) finished with floating coat of neat cement and making channels in cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size) finished with a floating coat of neat cement complete as per standard design : Inside size 120x90 cm and 90 cm deep including C.I. cover with frame (medium duty) 500 mm internal diameter, total weight of cover and frame to be not less than 116 kg (weight of cover 58 kg and weight of frame 58 kg) : With common burnt clay F.P.S. (non modular) bricks of class designation 7.5 | 5.00 | Each |  | 35000.00 | 175000.00 | 45000.00 | 225000.00 | 8500.00 | 42500.00 | 30000.00 | 150000.00 | 42500.00 | aircon engineers
28.00 | Excavation in hard rock/paved area/ cement concrete manually using floor cutter, concrete breaker etc including disposal of material within 50 metres lead as per direction of EIC. | 5.00 | CUM |  | 2500.00 | 12500.00 | 5000.00 | 25000.00 | 8500.00 | 42500.00 | 2500.00 | 12500.00 | 12500.00 | Superior Aircon Pvt. Ltd., AIR DESIGN SOLUTIONS
29.00 | Repsiring and Making the excavated/demolished area by cement concreate 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 40mm nominal size) in pavements/ Road, laid to required slope etc. as required as per site conditions. | 5.00 | CUM |  | 15000.00 | 75000.00 | 8000.00 | 40000.00 | 8500.00 | 42500.00 | 6000.00 | 30000.00 | 30000.00 | AIR DESIGN SOLUTIONS
30.00 | Annual comprehensive maintenance of 160 HP Hot & Cool VRF/VRV System comprises of outdoor VRF units and indoor units complete with interconnecting copper piping, electrical cabling, drain piping, mounting stand, remote unit etc. complete as required.
30.10 | 1st Year after DLP | 1.00 | Per Year |  | 350000.00 | 350000.00 | 250000.00 | 250000.00 | 600000.00 | 600000.00 | 304000.00 | 304000.00 | 250000.00 | BRITE INDUSTRIES
30.20 | 2nd Year after DLP | 1.00 | Per Year |  | 400000.00 | 400000.00 | 300000.00 | 300000.00 | 650000.00 | 650000.00 | 319200.00 | 319200.00 | 300000.00 | BRITE INDUSTRIES
30.30 | 3rd Year after DLP | 1.00 | Per Year |  | 450000.00 | 450000.00 | 552000.00 | 552000.00 | 725000.00 | 725000.00 | 335160.00 | 335160.00 | 335160.00 | AIR DESIGN SOLUTIONS
30.40 | 4th Year after DLP | 1.00 | Per Year |  | 500000.00 | 500000.00 | 579600.00 | 579600.00 | 750000.00 | 750000.00 | 351918.00 | 351918.00 | 351918.00 | AIR DESIGN SOLUTIONS
30.50 | 5th Year after DLP | 1.00 | Per Year |  | 550000.00 | 550000.00 | 608580.00 | 608580.00 | 775000.00 | 775000.00 | 369513.00 | 369513.00 | 369513.00 | AIR DESIGN SOLUTIONS
| Total in Figures |  |  |  |  | 17817700.00 |  | 17447640.00 |  | 19024390.00 |  | 14602563.00
Lowest Amount Quoted BY: AIR DESIGN SOLUTIONS(14602563.00)

## BOQ Summary
BOQ Summary Details Tender Title: Augmentation of Airconditioning System in Terminal Building at CE Hindon Tender ID: 2025_AAI_248744_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | AIR DESIGN SOLUTIONS (BID ID -913395) | 14602563.00 | L1
| 2 | BRITE INDUSTRIES (BID ID -913875) | 17447640.00 | L2
| 3 | Superior Aircon Pvt. Ltd. (BID ID -912050) | 17817700.00 | L3
| 4 | aircon engineers (BID ID -912039) | 19024390.00 | L4