## BoQ1
Government eProcurement System Created By: Jagannath singh Deshmukh Created Date/Time: 13-Nov-2025 05:42 PM Tender Title: Construction of MSSR at Rajkot International Airport. SH Provision of Precision Airconditioning and Other Associated Works. Tender ID: 2025_AAI_248919_1
Tender Inviting Authority:Asst.General Manager (E-E)
Name of Work: “Construction of MSSR at Rajkot International Airport (SH: Provision of Precision Airconditioning & Other Associated Works)"
Contract No: 2025_AAI_248919_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | VOLKS ENERGIE PVT LTD (GSTN-07AADCV9396C1ZZ) BID ID -916989
[5 empty] | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply of DX type 10 TR inverter type floor mounted, Precision Air Conditioning unit with minimum airflow of 10000 CMH, Return Air at 24 Deg C & 50% RH, suitable to operate on 3 Phase, 415V, 50 Hz AC supply equipped with most advanced industry technology guaranteeing precise control of temperature/humidity. The units shall be selected on the basis of following parameters: a) The Indoor unit shall comprise of Digital Scroll Compressor, EC fans, Coated Evaporator DX Cooling Coil, Infrared Humidifiers, Heaters, Microprocessor controllers, Thermostatic Expansion valves, Driers, G4 Filter, Suction and Discharge piping, Internal power and Control wiring, Crankcase heaters, HP/LP Cutouts, Power and Control contactors, water leak detectors and Other Electrical accessories. b) The Outdoor Condenser unit shall comprise of Condenser fans & motor, Condenser cooling coil (Copper coil with aluminium fins), Fan speed controller, Isolater switch. The condensing temperature of matching air cooled condenser not to exceed 55 Deg C at design conditions. c) Each unit should be having individual LCD display panel, which shall display date, time, Air temperature - actual & set values, Humidity- actual & set values, operating conditions, signal faults, collective faults, limiting values,humidifier/fan/sensor failures, accumulative operating hours etc. The display shall provide record of temperature and humidity with graphical display on the screen. d) Units should have provision of Unit to Unit Ethernet connection to operate with multiple units, run/stand-by rotation, automatic changeover and parameter sharing functions, external communications through BMS, sequential control,auto restart timer etc. Unit memory shall hold minimum 400 recent alarms/events with date and time for each alarm/event. | 3.00 | Each |  | 850000.00 | 2550000.00 | 2550000.00 | VOLKS ENERGIE PVT LTD
2.00 | Supply of indoor and outdoor unit stand made up of heavy duty MS angle iron of suitable size including applying primer and 02 coat paint etc. including all accessories as required. | 200.00 | Kg |  | 120.00 | 24000.00 | 24000.00 | VOLKS ENERGIE PVT LTD
3.00 | Installation Testing and commissioning of 10 TR precision AC unit as per Item no.1 , including fixing indoor and outdoor stand, supplying and charging refrigerent Gas etc. complete including all accessories as required as per site requirement. | 2.00 | Each |  | 180000.00 | 360000.00 | 360000.00 | VOLKS ENERGIE PVT LTD
4.00 | Supply and installation of OEM recommended 18G copper piping between indoor unit and outdoor unit [ Hot gas + liquid line ] of standard size including providing and fixing rubber nitrile insulation including supply and laying of 3 core x 2.5 sqmm copper Cable . | 20.00 | Mtr |  | 7000.00 | 140000.00 | 140000.00 | VOLKS ENERGIE PVT LTD
5.00 | Supply and fixing of drain CPVC / UPVC pipe [ 40 mm ] for condensate water from indoor unit to nearest drain point including coupling, elbow etc. including all accessories as required. | 20.00 | Mtr |  | 300.00 | 6000.00 | 6000.00 | VOLKS ENERGIE PVT LTD
6.00 | Supply and fixing of drain CPVC / UPVC pipe [ 25 mm ] for humidifier / condensate water including coupling , elbow etc. including all accessories as required. | 20.00 | Mtr |  | 150.00 | 3000.00 | 3000.00 | VOLKS ENERGIE PVT LTD
7.00 | Supplying and installing of following size of perforated Hot dip Galvanised iron cable trays with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with G.I. suspenders including G.I. bolts & nuts etc as required. 300mm width x 50 mm depth x 1.6mm thickness | 60.00 | Mtr |  | 450.00 | 27000.00 | 27000.00 | VOLKS ENERGIE PVT LTD
8.00 | Providing & fixing GI sheet cover over the cable trays on the cable trays of size 300 mm width X 50 mm depth by using 2 mm thick GI sheet including bending as per required size, fixing securely over the cable trays to give a finished look complete as required as per site requirement. | 60.00 | Mtr |  | 300.00 | 18000.00 | 18000.00 | VOLKS ENERGIE PVT LTD
9.00 | Supply , fabrication, installation, testing and commissioning of site fabricated/pre fab 22 Gauge GI sheet metal ducting complete with gaskets, elbows, hangers, anchor fastener, supports etc. including supply and fixing of nitrile rubber insulation complete as required. | 40.00 | Sq.Mtr |  | 600.00 | 24000.00 | 24000.00 | VOLKS ENERGIE PVT LTD
10.00 | Supply and fixing of 19 mm thick closed cell nitrile rubber (Class 'O') insulation by applying suitable cold setting adhesive as required for Server Room & walls below false floor etc. complete as required. | 200.00 | Sq.Mtr |  | 400.00 | 80000.00 | 80000.00 | VOLKS ENERGIE PVT LTD
11.00 | Supply and installation of heavy duty MS/ Aluminium powder coated floor grill for Supply air along with Aluminium powder coated volume control dampers, with load bearing capacity of min. 1000 kgs etc. complete as required. | 20.00 | Sq.Ft |  | 1300.00 | 26000.00 | 26000.00 | VOLKS ENERGIE PVT LTD
12.00 | Supply and installation of heavy duty MS/ Aluminium powder coated grill for return air etc. complete as required. | 30.00 | Sq.Ft |  | 950.00 | 28500.00 | 28500.00 | VOLKS ENERGIE PVT LTD
13.00 | Supply and installation of Digital Thermohygrometer Data logger for recording and displaying temperature and humidity in a room etc. including all accessories complete as per site requirement. | 3.00 | Each |  | 7500.00 | 22500.00 | 22500.00 | VOLKS ENERGIE PVT LTD
14.00 | Installation of 1.5 to 2.0 TR airconditioner, including recharge of refrigerant gas, supply and installation of pre-fabricated MS Stand for outdoor unit including all accessories etc. as required as per site requirement.[ Pre fabricated stand length should be such that there shall be gap of 10-12 inch between wall and outdoor unit. ] | 8.00 | Each |  | 1500.00 | 12000.00 | 12000.00 | VOLKS ENERGIE PVT LTD
15.00 | Supply and fixing of refrigerant piping, cabling, insulating with foam between indoor and outdoor units of 1.5 to 2.0 TR etc. as required. | 48.00 | Mtr |  | 400.00 | 19200.00 | 19200.00 | VOLKS ENERGIE PVT LTD
16.00 | SITC of Self contained,storage type of 40/80 Ltr Capacity water cooler suitable for operation on 230V ± 10%, single phase, AC supply and generally conforming to IS: 1475/2001 with upto amendment having nominal cooling capacity 40 Ltr/ Hr. complete with compressor,thermostat, stainless steel tank and stainless steel full body etc. as per technical specification and as per site requirement. | 1.00 | Each |  | 70000.00 | 70000.00 | 70000.00 | VOLKS ENERGIE PVT LTD
17.00 | SITC of RO+UV based Water Purification system having capacity 25 Ltr/hr including filters, UV lamp, RO Membrane and auto cut off water level sensor as per technical specifications etc. complete as per site requirement. | 1.00 | Each |  | 50000.00 | 50000.00 | 50000.00 | VOLKS ENERGIE PVT LTD
| Total in Figures |  |  |  |  | 3460200.00
Lowest Amount Quoted BY: VOLKS ENERGIE PVT LTD(3460200.00)

## BOQ Summary
BOQ Summary Details Tender Title: Construction of MSSR at Rajkot International Airport. SH Provision of Precision Airconditioning and Other Associated Works. Tender ID: 2025_AAI_248919_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | VOLKS ENERGIE PVT LTD (BID ID -916989) | 3460200.00 | L1