## BoQ1
Government eProcurement System Created By: Gajraj Singh Bhati Created Date/Time: 28-Oct-2025 11:20 AM Tender Title: Design, Supply, Installation, Testing and Commissioning of 50KW Rooftop Solar Power Plant at Dimapur Airport Tender ID: 2025_AAI_249404_1
Tender Inviting Authority: AGM(E-E) AAI, Dimapur Airport.
Name of Work: Design, Supply, Installation, Testing and Commissioning of 50KW Rooftop Solar Power Plant at Dimapur Airport.
Contract No:
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | MATESHWARI ENTERPRISES (GSTN-08AQUPJ7022P1Z2) BID ID -913679 |  | NEWSOL PV POWER PRIVATE LIMITED (GSTN-NA) BID ID -914424 |  | MADHAV SOLAR ENERGY LIMITED (GSTN-NA) BID ID -909100 |  | DOON INFRAPOWER PROJECTS PVT. LTD. (GSTN-NA) BID ID -913385 |  | Aboriginal Energy Private Limited (GSTN-NA) BID ID -913561 |  | RUNWAY INDIA (GSTN-NA) BID ID -915663
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | SUB HEAD:A- DSITC of 50kW PV solar plant 40kW rooftop solar plant at Fire station building Design, Supply, Installation, Testing and Commissioning of ongrid Solar Photovoltaic Power Plant conforming to MNRE specifications as amended, consisting of Mono Crystalline silicon solar cells, net metering facility, necessary protections, earthing, mounted on GI structure of suitable strength having anti reflective frame treatment with following components complete as required:- a) Solar Photovoltaic Module of capacity 400Wp to 500Wp or above, manufactured in India, conforming to IS 14286/IEC 61215, IS/IEC 61730-Part-1, IS/IEC 61730-Part-2. Solar Photovoltaic Module conversion efficiency shall not be less than 16.5%. PV modules used in solar power plants/ systems must be warranted for their output peak watt capacity, which should not be less than 90% at the end of 10 years and 80% at the end of 25 years. b) Power Conditioning Unit (PCU) of 350-800 V DC Input voltage range and 400 V AC, three phase, 4 wire, 50Hz +/- 2.5 Hz, output voltage suitable to generate AC Power with efficiency not less than 97%, total harmonic distortion less than 3% and suitable for ambient temperature from 0 to 50 degree C. The PCU shall adjust the voltage and frequency level to suit the Grid Voltage Frequency. | 1.00 | Job |  | 1560000.00 | 1560000.00 | 1920000.00 | 1920000.00 | 1600000.00 | 1600000.00 | 189000.00 | 189000.00 | 2220000.00 | 2220000.00 | 1938272.00 | 1938272.00 | 189000.00 | DOON INFRAPOWER PROJECTS PVT. LTD.
1.10 | c) Data Monitoring System for both locations complete with accessories. d) Fixing of Array junction box & Main junction box with IP 65 protection and termination arrangement for incoming and outgoing cable along with glands, lugs and other accessories etc. as required. e) Lightning and surge voltage protection. f) Connections & Interconnections by supplying & fixing required size XLPE insulated copper conductor 1.1 kV grade armoured power and control cables between solar modules, main power cable to grid supply PCU unit along with supplying & fixing of necessary channel/conduit lugs and other accessories etc. as required
2.00 | 10kW rooftop solar plant at power house building Design, Supply, Installation, Testing and Commissioning of ongrid Solar Photovoltaic Power Plant conforming to MNRE specifications as amended, consisting of Mono Crystalline silicon solar cells, net metering facility, necessary protections, earthing, mounted on GI structure of suitable strength having anti reflective frame treatment with following components complete as required:- a) Solar Photovoltaic Module of capacity 400Wp to 500Wp or above, manufactured in India, conforming to IS 14286/IEC 61215, IS/IEC 61730-Part-1, IS/IEC 61730-Part-2. Solar Photovoltaic Module conversion efficiency shall not be less than 16.5%. PV modules used in solar power plants/ systems must be warranted for their output peak watt capacity, which should not be less than 90% at the end of 10 years and 80% at the end of 25 years. b) Power Conditioning Unit (PCU) of 350-800 V DC Input voltage range and 400 V AC, three phase, 4 wire, 50Hz +/- 2.5 Hz, output voltage suitable to generate AC Power with efficiency not less than 97%, total harmonic distortion less than 3% and suitable for ambient temperature from 0 to 50 degree C. The PCU shall adjust the voltage and frequency level to suit the Grid Voltage Frequency. | 1.00 | Job |  | 390000.00 | 390000.00 | 480000.00 | 480000.00 | 400000.00 | 400000.00 | 590000.00 | 590000.00 | 620000.00 | 620000.00 | 1063442.00 | 1063442.00 | 390000.00 | MATESHWARI ENTERPRISES
2.20 | c) Fixing of Array junction box & Main junction box with IP 65 protection and termination arrangement for incoming and outgoing cable along with glands, lugs and other accessories etc. as required. d) Lightning and surge voltage protection. e) Connections & Interconnections by supplying & fixing required size XLPE insulated copper conductor 1.1 kV grade armoured power and control cables between solar modules, main power cable to grid supply PCU unit along with supplying & fixing of necessary channel/conduit lugs and other accessories etc. as required
3.00 | ACDB Panel Supply, installation, testing and commissioning of dust, damp and vermin proof cubicle free floor, indoor type factory built sheet steel enclosed modular bolted construction extendable Main LT panel, suitable for operation on 415 ±10% volts, 50 Hz AC 3 phase 4 wire supply system fabricated out of compartmentalised design and covered with CRCA sheet steel of 2mm thick for frame work and 1.6mm thick for doors/ covers, 3mm thick for gland plates i/c cleaning & finishing complete with 7 tank process for powder coating in approved shade, having extensible type TPN Aluminium bus bars of high conductivity, DMC/SMC bus bar supports, with suitable short circuit with stand capacity, bottom base channel of section not less than ISMC 75mm, fabrication shall be done in transportable sections, entire panel shall have a common copper earth bar of suitable size with 2 nos earth studs, solid connections from main bus bar to switch gears with required size of Aluminium bus bars, including control wiring with 2.5 sqmm. PVC insulated FRLS copper conductor Single Core cable for voltage & current circuits, cable alleys, cable gland plates in two half, danger notice plates, with interconnections, necessary metering protections & indications and mounted with the following switch gears as per drawing and technical specifications etc. complete as required. The Panel shall have following incommer, outgoings :- Suitable provision for parallel operation of two inverters of capacity 10kW and 40kW through suitable capacity of MCCBs, busbars, outgoing MCCB to connect the Main LT panel of power house, Energy meter for solar generation from rooftop plant. Complete as required | 1.00 | Job |  | 60000.00 | 60000.00 | 200000.00 | 200000.00 | 500000.00 | 500000.00 | 175000.00 | 175000.00 | 90000.00 | 90000.00 | 373600.00 | 373600.00 | 60000.00 | MATESHWARI ENTERPRISES
4.00 | Net metering arrangement and liaising charges with Department of Power, Nagaland alongwith provision of net metering arrangement including application fee, site visit coordination DISCOM approval, final inspection, bi-directional meter installation / testing etc complete as required. | 1.00 | Job |  | 75000.00 | 75000.00 | 150000.00 | 150000.00 | 300000.00 | 300000.00 | 175000.00 | 175000.00 | 250000.00 | 250000.00 | 59000.00 | 59000.00 | 59000.00 | RUNWAY INDIA
5.00 | SUB HEAD:B- LAYING OF CABLES AND ASSOCIATED WORKS Supply of XLPE insulated, armoured 1.1 KV grade aluminium conductor cable as per IS 7098 (Part 1) 1988 with upto date ammendments of following sizes:
5.10 | 3.5 x 185 sq.mm | 300.00 | Meter |  | 1100.00 | 330000.00 | 1200.00 | 360000.00 | 1700.00 | 510000.00 | 1050.00 | 315000.00 | 500.00 | 150000.00 | 1239.00 | 371700.00 | 150000.00 | Aboriginal Energy Private Limited
6.00 | Laying of one number XLPE armoured power cable of 1.1 KV grade of following size in the existing masonry open duct as required:
6.10 | Above 95 sq. mm and upto 185 sq. mm | 25.00 | Meter |  | 100.00 | 2500.00 | 350.00 | 8750.00 | 1400.00 | 35000.00 | 750.00 | 18750.00 | 400.00 | 10000.00 | 1003.00 | 25075.00 | 2500.00 | MATESHWARI ENTERPRISES
6.20 | upto 35 sq. mm | 25.00 | Meter |  | 80.00 | 2000.00 | 100.00 | 2500.00 | 600.00 | 15000.00 | 625.00 | 15625.00 | 400.00 | 10000.00 | 944.00 | 23600.00 | 2000.00 | MATESHWARI ENTERPRISES
7.00 | Laying and fixing of one number XLPE armoured power cable of 1.1 KV grade of following size on cable tray as required.
7.10 | Above 95 sq. mm and upto 185 sq. mm (clamped with 25/40x3mm MS flat clamp) | 25.00 | meter |  | 200.00 | 5000.00 | 200.00 | 5000.00 | 1000.00 | 25000.00 | 750.00 | 18750.00 | 400.00 | 10000.00 | 1239.00 | 30975.00 | 5000.00 | MATESHWARI ENTERPRISES, NEWSOL PV POWER PRIVATE LIMITED
7.20 | upto 35 sq. mm (clamped with 1mm thick shaddle) | 25.00 | meter |  | 150.00 | 3750.00 | 100.00 | 2500.00 | 800.00 | 20000.00 | 650.00 | 16250.00 | 400.00 | 10000.00 | 1156.00 | 28900.00 | 2500.00 | NEWSOL PV POWER PRIVATE LIMITED
8.00 | Laying of one number XLPE armoured power cable of 1.1 KV grade of following size in the existing RCC/HUME/METAL/DWC pipe as required:
8.10 | Above 95 sq. mm and upto 185 sq. mm | 250.00 | Meter |  | 100.00 | 25000.00 | 200.00 | 50000.00 | 100.00 | 25000.00 | 750.00 | 187500.00 | 400.00 | 100000.00 | 1890.00 | 472500.00 | 25000.00 | MADHAV SOLAR ENERGY LIMITED, MATESHWARI ENTERPRISES
9.00 | Supplying and laying of following size DWC HDPE pipe along with all accessories like socket, bend, couplers, seal rings etc. conforming to IS 14930, Part II complete with fitting and cutting, jointing etc. direct in ground (75 cm below ground level) including excavation and refilling the trench but excluding sand cushioning and protective covering etc., complete as required.
9.10 | 120 mm dia (OD-120 mm & ID-103.5 mm nominal) | 250.00 | Meter |  | 500.00 | 125000.00 | 600.00 | 150000.00 | 5000.00 | 1250000.00 | 650.00 | 162500.00 | 400.00 | 100000.00 | 650.00 | 162500.00 | 100000.00 | Aboriginal Energy Private Limited
10.00 | Supplying and making end termination with brass compression gland and aluminium lugs size for following size of XLPE armoured aluminium conductor cable of 1.1 KV grade as required.
10.10 | 3.5 x 185 sq.mm | 2.00 | set |  | 300.00 | 600.00 | 4000.00 | 8000.00 | 5000.00 | 10000.00 | 3500.00 | 7000.00 | 900.00 | 1800.00 | 4720.00 | 9440.00 | 600.00 | MATESHWARI ENTERPRISES
10.20 | 3.5 x 35 sq.mm | 2.00 | set |  | 200.00 | 400.00 | 1000.00 | 2000.00 | 5000.00 | 10000.00 | 2500.00 | 5000.00 | 900.00 | 1800.00 | 3540.00 | 7080.00 | 400.00 | MATESHWARI ENTERPRISES
11.00 | Providing, laying and fixing of following dia GI pipe (medium class) in ground complete with GI fittings including trenching (75 cm deep) and refilling etc. as required.
11.10 | 100 mm dia | 18.00 | meter |  | 1500.00 | 27000.00 | 300.00 | 5400.00 | 5000.00 | 90000.00 | 900.00 | 16200.00 | 1100.00 | 19800.00 | 2293.00 | 41274.00 | 5400.00 | NEWSOL PV POWER PRIVATE LIMITED
12.00 | Supply, Installation, Testing and Commissioning of smart RFID based electronic cable marker 220 mm dia, 1.5 m depth range 10 digit hexadecimal ID code, 134 kHz frequency complete as required | 12.00 | Each |  | 1600.00 | 19200.00 | 3000.00 | 36000.00 | 28000.00 | 336000.00 | 2000.00 | 24000.00 | 6000.00 | 72000.00 | 5664.00 | 67968.00 | 19200.00 | MATESHWARI ENTERPRISES
13.00 | PART - II SUB HEAD:C- Operation and AICMC Operation and all Inclusive Comprehensive Maintenance of 50 KWp Solar rooftop plant as provided under SH-I for the period of 05 years after sucessful completion of DLP of 01 years including deployment of one semi-skilled manpower on all days (excluding weekly off) in general shift, material, spares, transportation as per technical specification etc. complete as required.
13.10 | First year AICMC after completion of DLP of 01 years | 12.00 | month |  | 2500.00 | 30000.00 | 7000.00 | 84000.00 | 30000.00 | 360000.00 | 45000.00 | 540000.00 | 5000.00 | 60000.00 | 18350.00 | 220200.00 | 30000.00 | MATESHWARI ENTERPRISES
13.20 | Second year AICMC after completion of DLP of 01 years | 12.00 | month |  | 2500.00 | 30000.00 | 8000.00 | 96000.00 | 31500.00 | 378000.00 | 45000.00 | 540000.00 | 5000.00 | 60000.00 | 19350.00 | 232200.00 | 30000.00 | MATESHWARI ENTERPRISES
13.30 | Third year AICMC after completion of DLP of 01 years | 12.00 | month |  | 2500.00 | 30000.00 | 9000.00 | 108000.00 | 33000.00 | 396000.00 | 45000.00 | 540000.00 | 5000.00 | 60000.00 | 20350.00 | 244200.00 | 30000.00 | MATESHWARI ENTERPRISES
13.40 | Fourth year AICMC after completion of DLP of 01 years | 12.00 | month |  | 2500.00 | 30000.00 | 10000.00 | 120000.00 | 34800.00 | 417600.00 | 45000.00 | 540000.00 | 5000.00 | 60000.00 | 21350.00 | 256200.00 | 30000.00 | MATESHWARI ENTERPRISES
13.50 | Fifth year AICMC after completion of DLP of 01 years | 12.00 | month |  | 2500.00 | 30000.00 | 11000.00 | 132000.00 | 36500.00 | 438000.00 | 45000.00 | 540000.00 | 5000.00 | 60000.00 | 22350.00 | 268200.00 | 30000.00 | MATESHWARI ENTERPRISES
| Total in Figures |  |  |  |  | 2775450.00 |  | 3920150.00 |  | 7115600.00 |  | 4615575.00 |  | 3965400.00 |  | 5896326.00
Lowest Amount Quoted BY: MATESHWARI ENTERPRISES(2775450.00)

## BOQ Summary
BOQ Summary Details Tender Title: Design, Supply, Installation, Testing and Commissioning of 50KW Rooftop Solar Power Plant at Dimapur Airport Tender ID: 2025_AAI_249404_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | MATESHWARI ENTERPRISES (BID ID -913679) | 2775450.00 | L1
| 2 | NEWSOL PV POWER PRIVATE LIMITED (BID ID -914424) | 3920150.00 | L2
| 3 | Aboriginal Energy Private Limited (BID ID -913561) | 3965400.00 | L3
| 4 | DOON INFRAPOWER PROJECTS PVT. LTD. (BID ID -913385) | 4615575.00 | L4
| 5 | RUNWAY INDIA (BID ID -915663) | 5896326.00 | L5
| 6 | MADHAV SOLAR ENERGY LIMITED (BID ID -909100) | 7115600.00 | L6