## BoQ1
Government eProcurement System Created By: Vikas Kumar Tripathi Created Date/Time: 12-Nov-2025 05:04 PM Tender Title: Procurement and Replacement of LT Panels of A and B Block at RGB,New Delhi. Tender ID: 2025_AAI_250049_1
Tender Inviting Authority: Senior Manager . (Engg. – Elect)- IMU, AAI, CHQ, R.G. Bhawan, New Delhi-110003
Name of Work: Procurement and Replacement of LT Panels of A&B Block at Rajiv Gandhi Bhawan, New Delhi.
Tender ID:- ( 2025_AAI_250049_1 )
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | ENGINEERS AND ENGINEERS ELECTRICALS PRIVATE LIMITED (GSTN-08AABCE5310P1ZJ) BID ID -910998 |  | HIMALAYA GENERATORS (GSTN-09AEDPA0988G1ZL) BID ID -911705 |  | ECS ENGINEERING PVT LTD (GSTN-09AABCE5944P1Z1) BID ID -914637 |  | Avon Electricals (GSTN-07AAPFA2943K1Z6) BID ID -913720 |  | RISHA CONTROL ENGINEERS PRIVATE LIMITED (GSTN-NA) BID ID -914518 |  | ultima switchgears ltd (GSTN-NA) BID ID -914483 |  | Shiva Enterprises (GSTN-NA) BID ID -914925
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Fabrication, Supply installation testing Commissioning of following (item No. 1.01 to 1.04) of floor mounted, indoor type LT Panel suitable for 3Phase ,4 Wire 415Volt 50Hz AC Supply , enclosed LT PANEL (PTTA) compartmentalized design (Separate for the each MCCB/Form 3B) and covered with CRCA sheet steel of 2mm thick for doors/covers, 3mm thick for gland plates, & finishing complete with seven tank process for powder coating in approved shade, totally enclosed free standing ,interconnection wiring with 2.5sqmm FRLSH copper conductor wire, Cable alleys, cable gland plates in two half, danger notice plates, Earthing stud and detachable gland plate at top and rubber gasket for doors with locking arrangement etc. complete with MS iron base frame (C Channel) fabricated from 75mm x 50mm x5mm MS channel as required. 1. All MCCB Shall be provided with Front rotary handle and spreader links. 2. ALL Incomer MCCB shall be provided with ON/OFF/TRIP Indication Lamps. with control MCB and Phase Indication Lamps, Multifunction meter i/c. CTs 3. All MCCBs shall be having Ics = 100% Icu. 4. ALL incomer MCCB shall be provided with . microprocessor based releases of (36 kA Ics Value), Breaker Release shall provide protection against O/L, S/C & E/F. 5. ALL Outgoing MCCB shall be provided with Thermal magnetic releases of (25kA Ics Value). Breaker Release shall provide protection against O/L, S/C. 6. ALL Outgoing MCCB shall be provided with ON/OFF/TRIP Indication Lamps 7. ALL the compartment shall have name plate of MCCB. 8. Main bus bar Shall be 400sqmm (40x10mm) 9. All other accessories such as control MCB, auxillary contactors, auxillary switches, etc to be provided as required. Note: Panels will be installed at various floors of A&B block as mentioned below shifting to be done manually.
1.01 | Location and Panel Name: A Block, Ground Floor Panel-1 , A Block, VIP Third Floor, B Block VIP Third Floor, B Block, Third Floor Incomer MCCBs: 4P 250A MCCB-1No. Outgoing MCCBs: i) 4P 63A - 4Nos. ii) 4P 80A - 2Nos. iii) 4P 100A - 3 Nos. | 4.00 | Each |  | 242707.10 | 970828.40 | 255000.00 | 1020000.00 | 211000.00 | 844000.00 | 267560.00 | 1070240.00 | 263000.00 | 1052000.00 | 175000.00 | 700000.00 | 252000.00 | 1008000.00 | 700000.00 | ultima switchgears ltd
1.02 | Location and Panel Name: A Block, Ground Floor Panel-2, A Block, First Floor,B Block, First Floor, A Block, Third Floor, B Block, Second Floor Incomer MCCBs: 4P 250A MCCB-1No. Outgoing MCCBs: i) 4P 63A - 5 Nos. ii) 4P 80A - 4 Nos. iii) 4P 100A - 2 Nos. | 5.00 | Each |  | 263032.64 | 1315163.20 | 255000.00 | 1275000.00 | 240000.00 | 1200000.00 | 269589.00 | 1347945.00 | 292000.00 | 1460000.00 | 175000.00 | 875000.00 | 302000.00 | 1510000.00 | 875000.00 | ultima switchgears ltd
1.03 | Location and Panel Name: A Block, Second Floor, A Block, VIP Second Floor, A Block, VIP Ground Floor, B Block, VIP Ground Floor, Incomer: MCCB : 4P, 250A MCCB-1No. Outgoing MCCBs: i) 4P, 63A - 4 Nos. ii) 4P,80A - 3 Nos. iii) 4P, 100A - 3 Nos. | 4.00 | Each |  | 252560.64 | 1010242.56 | 255000.00 | 1020000.00 | 224000.00 | 896000.00 | 258692.00 | 1034768.00 | 278000.00 | 1112000.00 | 175000.00 | 700000.00 | 289000.00 | 1156000.00 | 700000.00 | ultima switchgears ltd
1.04 | Location and Panel Name: B Block, Ground Floor Incomer: 4P, 250A MCCB-1No. Outgoing MCCBs: i) 4P, 63A - 4 Nos. ii) 4P,80A - 3 Nos. iii) 4P, 100A - 4 Nos. | 2.00 | Each |  | 263032.64 | 526065.28 | 255000.00 | 510000.00 | 239000.00 | 478000.00 | 266800.00 | 533600.00 | 293000.00 | 586000.00 | 175000.00 | 350000.00 | 252000.00 | 504000.00 | 350000.00 | ultima switchgears ltd
2.00 | Supply and fixing of following size MCCB and Thermal magnetic releases , terminal spreader in existing cubical panel including drilling holes in cubical panel , making termination, extended rotary handle with SS Bolts, Nuts, Washers etc as required as per satisfaction of EIC.
2.01 | 4P 250Amp MCCB With 36 KA braking Capacitiy suitable for the exising Cubical Panel | 10.00 | Each |  | 31443.00 | 314430.00 | 22500.00 | 225000.00 | 30400.00 | 304000.00 | 22033.00 | 220330.00 | 31500.00 | 315000.00 | 35000.00 | 350000.00 | 52000.00 | 520000.00 | 220330.00 | Avon Electricals
2.02 | 4P 63Amp MCCB With 25 KA braking Capacitiy Suitable for the exising Cubical Panel | 8.00 | Each |  | 12711.00 | 101688.00 | 15000.00 | 120000.00 | 9500.00 | 76000.00 | 6610.00 | 52880.00 | 9500.00 | 76000.00 | 15000.00 | 120000.00 | 16000.00 | 128000.00 | 52880.00 | Avon Electricals
3.00 | Fabrication, Supply, installationg, testing, commissioning of Feeder Pillar of following (item No. 3.01 to 3.03 ) of , outdoor type, IP-54 rated Feeder pillar panel with double door arrangement suitable for 3Phase ,4 Wire 415Volt 50Hz AC Supply , enclosed Feeder Panel compartmentalized design and covered with CRCA sheet steel of 2mm thick for doors/covers, 3mm thick for gland plates, & finishing complete with seven tank process for powder coating in approved shade, totally enclosed free standing dust tight, vermin proof, totally enclosed, cubicle type with top canopy for rain protection(all around) ,interconnection wiring with 2.5sqmm FRLSH copper conductor wire, Cable alleys, cable gland plates in two half, danger notice plates, Earthing stud and detachable gland plate at bottom and rubber gasket for doors with locking arrangement etc. and duly fixed on MS angle fram of size 50x50x5mm, 90cm long leg out of which 45cm duly grouted in cement as required. 1. ALL Incomer MCCB shall be provided with Thermal magnetic releases of (25kA Ics Value). 2. All incomer MCCB Shall be provided with Front rotary handle and spreader links. 3. ALL Incomer MCCB shall be provided with ON/OFF/TRIP Indication Lamps and Phase Indication Lamps, Multifunction meter i/c. CTs 4. All MCCBs shall be having Ics = 100% Icu
3.01 | Incomer : 4P, 100Amp MCCB-1No. Outgoing : MCB with braking capacity 10KA , C-Curve 1. 4P 63Amp MCB-2No. 2. 4P 32Amp MCB-2No. 3. 4P 16Amp MCB-4Nos. 4. 2P 25 Amp MCB -4Nos. 5. 01No. Spare Compartment with Din rail as required. | 1.00 | Each |  | 115007.18 | 115007.18 | 90000.00 | 90000.00 | 83000.00 | 83000.00 | 135590.00 | 135590.00 | 88500.00 | 88500.00 | 62000.00 | 62000.00 | 110000.00 | 110000.00 | 62000.00 | ultima switchgears ltd
3.02 | Incomer : 4P, 100Amp MCCB-1No. Outgoing : MCB with braking capacity 10KA , C-Curve 1. 4P 100Amp MCB-1No. 2. 4P 63Amp MCB-1No. 3. 4P 32Amp MCB-2Nos. 4. 4P 16AMP MCB -2Nos. 5. 2P 25 Amp MCB -4Nos. 6. 01No. Spare Compartment with Din rail as required. | 1.00 | Each |  | 121839.14 | 121839.14 | 90000.00 | 90000.00 | 101000.00 | 101000.00 | 41525.00 | 41525.00 | 91000.00 | 91000.00 | 72500.00 | 72500.00 | 110000.00 | 110000.00 | 41525.00 | Avon Electricals
3.03 | Incomer : 4P, 100Amp MCCB-1No. Outgoing : MCB with braking capacity 10KA , C-Curve 1. 4P 100Amp MCB-1No. 2. 4P 63Amp MCB-4No. 3. 4P 32Amp MCB-4Nos. 4. 4P 16AMP MCB -2Nos. 5. 2P 25 Amp MCB -4Nos. 7. 10 Hp 3Phase Motor starter as required in separate Compartment. 8. 01No. Spare Compartment with Din rail as required. | 1.00 | Each |  | 134338.22 | 134338.22 | 90000.00 | 90000.00 | 114000.00 | 114000.00 | 57628.00 | 57628.00 | 136000.00 | 136000.00 | 82500.00 | 82500.00 | 137500.00 | 137500.00 | 57628.00 | Avon Electricals
4.00 | S.I.T.C of 250A Rating, 4 Pole in Sheet Steel Enclosure Automatic Changeover Swith complete with Phase barrier, Handle Assembly having Door Interlock and Padlocking arrangement, indication lamps, made out of 2mm thick outer, CRCA sheet steel, dust tight, vermin proof, totally enclosed, cubicle type,wall mounted, suitable for operation at 415V, 3 phase, 4 wire, 50 Hz, A.C. Power Supply System complete with all accessories, interconnection, Cable Entry provision etc. as required. | 7.00 | Each |  | 111589.00 | 781123.00 | 30000.00 | 210000.00 | 66000.00 | 462000.00 | 38000.00 | 266000.00 | 70500.00 | 493500.00 | 62000.00 | 434000.00 | 85000.00 | 595000.00 | 210000.00 | HIMALAYA GENERATORS
5.00 | Supply, installation, testing, Commissioning of maintenance free earthing system set(Chemical earthing) consisting of one Galvanizd Pipe in pipe earthing electrode of Outer dia 48-50mm and inner dia. 25mm, 3Mtr. In Length along with two bags(25kg) of ground Enhancement Material(GEM) with one set of H clamp and Earth pit chamber as required. | 30.00 | Each |  | 16770.00 | 503100.00 | 6000.00 | 180000.00 | 8000.00 | 240000.00 | 14000.00 | 420000.00 | 10070.00 | 302100.00 | 10000.00 | 300000.00 | 4500.00 | 135000.00 | 135000.00 | Shiva Enterprises
6.00 | Providing and fixing 25 mm X 5 mm G.I. strip on surface or in recess for connections etc. as required. | 300.00 | Mtr. |  | 145.08 | 43524.00 | 130.00 | 39000.00 | 158.00 | 47400.00 | 240.00 | 72000.00 | 245.00 | 73500.00 | 1000.00 | 300000.00 | 140.00 | 42000.00 | 39000.00 | HIMALAYA GENERATORS
7.00 | Supplying and laying 25 mm X 5 mm G.I strip at 0.50 metre below ground as strip earth electrode, including connection/ terminating with G.I. nut, bolt, spring, washer etc. as required. (Jointing shall be done by overlapping and with 2 sets of G.I. nut bolt & spring washer spaced at 50mm) | 300.00 | Mtr. |  | 249.08 | 74724.00 | 400.00 | 120000.00 | 280.00 | 84000.00 | 270.00 | 81000.00 | 265.00 | 79500.00 | 1000.00 | 300000.00 | 180.00 | 54000.00 | 54000.00 | Shiva Enterprises
8.00 | Supplying and making end termination with brass double compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
8.01 | 4 X 10 sq. mm | 20.00 | Each |  | 559.00 | 11180.00 | 150.00 | 3000.00 | 200.00 | 4000.00 | 338.00 | 6760.00 | 420.00 | 8400.00 | 1000.00 | 20000.00 | 350.00 | 7000.00 | 3000.00 | HIMALAYA GENERATORS
8.02 | 4 X 25 sq. mm | 20.00 | Each |  | 751.40 | 15028.00 | 250.00 | 5000.00 | 250.00 | 5000.00 | 338.00 | 6760.00 | 420.00 | 8400.00 | 1000.00 | 20000.00 | 380.00 | 7600.00 | 5000.00 | HIMALAYA GENERATORS, ECS ENGINEERING PVT LTD
8.03 | 3.5X 35 sq. mm | 20.00 | Each |  | 1004.90 | 20098.00 | 350.00 | 7000.00 | 300.00 | 6000.00 | 358.00 | 7160.00 | 495.00 | 9900.00 | 1000.00 | 20000.00 | 420.00 | 8400.00 | 6000.00 | ECS ENGINEERING PVT LTD
8.04 | 3.5 X 50 sq. mm | 20.00 | Each |  | 1177.80 | 23556.00 | 450.00 | 9000.00 | 460.00 | 9200.00 | 430.00 | 8600.00 | 520.00 | 10400.00 | 1500.00 | 30000.00 | 450.00 | 9000.00 | 8600.00 | Avon Electricals
8.05 | 3.5 X 95 sq. mm | 10.00 | Each |  | 1712.10 | 17121.00 | 550.00 | 5500.00 | 700.00 | 7000.00 | 516.00 | 5160.00 | 630.00 | 6300.00 | 2500.00 | 25000.00 | 550.00 | 5500.00 | 5160.00 | Avon Electricals
8.06 | 3.5 X 185 sq. mm | 10.00 | Each |  | 2966.60 | 29666.00 | 650.00 | 6500.00 | 1000.00 | 10000.00 | 625.00 | 6250.00 | 1260.00 | 12600.00 | 3500.00 | 35000.00 | 750.00 | 7500.00 | 6250.00 | Avon Electricals
8.07 | 3.5 X 240 sq. mm | 10.00 | Each |  | 3543.80 | 35438.00 | 750.00 | 7500.00 | 1400.00 | 14000.00 | 670.00 | 6700.00 | 2100.00 | 21000.00 | 4000.00 | 40000.00 | 1050.00 | 10500.00 | 6700.00 | Avon Electricals
9.00 | Dismantling of following existing LT Panels(including termination,earthing, etc) from the Various floors and handing over to AAI store as per direction of Engineer-In-Charge. Note: Dismantling of panel will be done same day of installation of new panel
9.01 | Ground Floor | 9.00 | Each |  | 8100.00 | 72900.00 | 3900.00 | 35100.00 | 12000.00 | 108000.00 | 2966.00 | 26694.00 | 13000.00 | 117000.00 | 50000.00 | 450000.00 | 6500.00 | 58500.00 | 26694.00 | Avon Electricals
9.02 | 1st Floor | 2.00 | Each |  | 8100.00 | 16200.00 | 4900.00 | 9800.00 | 15000.00 | 30000.00 | 4237.00 | 8474.00 | 22000.00 | 44000.00 | 60000.00 | 120000.00 | 10000.00 | 20000.00 | 8474.00 | Avon Electricals
9.03 | 2nd Floor | 4.00 | Each |  | 8100.00 | 32400.00 | 5800.00 | 23200.00 | 16000.00 | 64000.00 | 5508.00 | 22032.00 | 25000.00 | 100000.00 | 70000.00 | 280000.00 | 13500.00 | 54000.00 | 22032.00 | Avon Electricals
9.04 | 3rd Floor | 3.00 | Each |  | 10800.00 | 32400.00 | 6800.00 | 20400.00 | 18000.00 | 54000.00 | 6255.00 | 18765.00 | 29000.00 | 87000.00 | 80000.00 | 240000.00 | 16500.00 | 49500.00 | 18765.00 | Avon Electricals
| Total in Figures |  |  |  |  | 6318059.98 |  | 5121000.00 |  | 5240600.00 |  | 5456861.00 |  | 6290100.00 |  | 5926000.00 |  | 6247000.00
Lowest Amount Quoted BY: HIMALAYA GENERATORS(5121000.00)

## BOQ Summary
BOQ Summary Details Tender Title: Procurement and Replacement of LT Panels of A and B Block at RGB,New Delhi. Tender ID: 2025_AAI_250049_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | HIMALAYA GENERATORS (BID ID -911705) | 5121000.00 | L1
| 2 | ECS ENGINEERING PVT LTD (BID ID -914637) | 5240600.00 | L2
| 3 | Avon Electricals (BID ID -913720) | 5456861.00 | L3
| 4 | ultima switchgears ltd (BID ID -914483) | 5926000.00 | L4
| 5 | Shiva Enterprises (BID ID -914925) | 6247000.00 | L5
| 6 | RISHA CONTROL ENGINEERS PRIVATE LIMITED (BID ID -914518) | 6290100.00 | L6
| 7 | ENGINEERS AND ENGINEERS ELECTRICALS PRIVATE LIMITED (BID ID -910998) | 6318059.98 | L7