## BoQ1
Government eProcurement System Created By: SINDHU L S Created Date/Time: 28-Oct-2025 05:00 PM Tender Title: Replacement of Fire Fighting system for Terminal Building at Puducherry Airport Tender ID: 2025_AAI_250054_1
Tender Inviting Authority: ASST. GENERAL MANAGER (ENGG-ELECTRICAL), AAI, RHQ-SR, CHENNAI - 600016
Name of Work: Replacement of Fire Fighting system for Terminal Building at Puducherry Airport.
Contract No: 2025_AAI_250054_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | J.K.DEFENCE FIRE ENGG. SERVICES (GSTN-NA) BID ID -916477 |  | Delta Leonis Building Solutions (GSTN-NA) BID ID -915378 |  | DElite System Engineering (India) Pvt. Ltd. (GSTN-NA) BID ID -913752 |  | VOID FIRE CONSULTANTS (GSTN-NA) BID ID -916722 |  | ILLUMECH ENGINEERING (GSTN-NA) BID ID -917039
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | SH I : FIRE FIGHTING SYSTEM AND HYDRANT SYSTEM
2.00 | Supplying, Installation, Testing and Commissioning of Diesel engine driven main Fire Pump at underground pump house suitable for Automatic & Manual operation and consisting of following: Horizontal type Split casing centrifugal pump of cast iron body and bronze impeller with stainless steel shaft, Mechanical Seal to ensure a minimum pressure of 3.5 Kg/sq.cm at highest and farthest outlet at specified flow of 2280 lpm at 70 metre Head conforming to IS 1520, Suitable HP, 1500 RPM water cooled with radiator, diesel engine conforming to relevant BS& IS standard complete with auto starting mechanism, Engine Control Panel, emergency stop button, 12 volts/24 Volts electric starting equipment, 200 Ltrs Diesel day tank with water level indicator & necessary fuel line valves, Exhaust pipe extended upto 1 m outside pump house from underground pump house, duly insulated with 50 mm thick glass wool with 1.0 mm thick aluminium sheet cladding, Residential silencer, Instruments and protection as per specification, Emergency Stop button, painted with post office red colour, M.S. fabricated Common base plate, coupling guard, including cement concrete foundation upto 600mm height, foundation bolts, AVM pads, Bellows, all sides duly plastered & painted, all interconnections between Diesel Engine to main electrical panel & fuel Pipe line connections with Day tank, body earthing with 25 x 5 mm GI earth strip etc. complete as required. Note : As Pump is installed in UnderGround sump, the pump and motor shall be brought separately and assembled at site by OEM/Dealer as per site condition. (Make : As per List of Preferred makes) | 1.00 | NO. |  | 950000.00 | 950000.00 | 619999.00 | 619999.00 | 700000.00 | 700000.00 | 590000.00 | 590000.00 | 876780.00 | 876780.00 | 590000.00 | VOID FIRE CONSULTANTS
3.00 | Supplying, Installation, Testing and Commissioning of Electric driven main Fire pump at underground pump house suitable for Automatic & Manual operation and consisting of following: Horizontal type, multistage, centrifugal, split casing pump of cast iron body & bronze impeller with stainless steel shaft, mechanical seal to ensure a minimum pressure of 3.5 Kg/sq.cm at highest and farthest outlet at specified flow of 2280 lpm at 70 Metre head conforming to IS 1520, suitable HP Squirrel cage induction motor, IE-3, TEFC, synchronous speed 1500 RPM, suitable for operation on 415 volts, 3 phase 50 Hz AC supply with IP 55 protection for enclosure, horizontal foot mounted type with Class F Insulation, conforming to IS:325, M.S. fabricated Common base plate, coupling guard, including cement concrete foundation upto 600mm height, foundation bolts, AVM pads, Bellows, all sides duly plastered & painted, body earthing with 25 x 5 mm GI earth strip etc. complete as required. Note : As Pump is installed in UnderGround sump, the pump and motor shall be brought separately and assembled at site by OEM/Dealer as per site condition. (Make : As per List of Preferred makes) | 1.00 | NO. |  | 700000.00 | 700000.00 | 414997.00 | 414997.00 | 500000.00 | 500000.00 | 389000.00 | 389000.00 | 721965.00 | 721965.00 | 389000.00 | VOID FIRE CONSULTANTS
4.00 | Supplying Installation, Testing and Commissioing of Electric driven pressurisation pump/Jockey Pump at underground pump house suitable for Automatic & Manual operation and consisting of following: Multistage centrifugal pump of cast iron body and bronze impeller with stainless steel shaft, mechanical seal and flow of 180 lpm at 70 metres head conforming to IS : 1520, Suitable HP Squrrel cage induction motor, IE-3, TEFC type suitable for operation on 415 volts, 3 phase 50 Hz AC supply with IP 55 protection for enclosure, horizontal foot mounted type with Class F Insulation, conforming to IS:325, M.S. fabricated Common base plate, coupling guard, including cement concrete foundation upto 600mm height, foundation bolts, AVM pads, Bellows, all sides duly plastered & painted, body earthing with 25 x 5 mm GI earth strip etc. complete as required. (Make : As per List of Preferred makes) | 1.00 | NO. |  | 250000.00 | 250000.00 | 135193.00 | 135193.00 | 250000.00 | 250000.00 | 140000.00 | 140000.00 | 212100.00 | 212100.00 | 135193.00 | Delta Leonis Building Solutions
5.00 | Providing, laying, testing & commissioning of MS Heavy class Pipe conforming to IS 1239 including cutting, welding etc. etc. complete with all fittings viz. tees, elbows, reducers, union, flanges, rubber gaskets, GI nuts, bolts, washer, foot valve including Installation/fixing the pipe with MS supports i/c clamps, hangers as per specification etc. complete as required. (Rates includes one coat of red oxide primer and two coats of fire red synthetic enamel paint). a)200 mm dia (Thickness 6.35 mm) (Make : As per List of Preferred makes) | 20.00 | MTR |  | 3000.00 | 60000.00 | 3949.00 | 78980.00 | 4500.00 | 90000.00 | 3546.00 | 70920.00 | 3481.00 | 69620.00 | 60000.00 | J.K.DEFENCE FIRE ENGG. SERVICES
6.00 | Supplying, laying, jointing and testing of following sizes of MS Heavy class pipes conforming to IS-1239 including cutting, welding etc. complete with all fittings viz. tees, elbows, reducers, union, flanges, rubber gaskets, GI nuts, bolts, washer including Installation/fixing the pipe on floor/wall with concrete blocks/MS supports i/c clamps, hangers as per specification etc. complete as required. (Rates includes one coat of red oxide primer and two coats of fire red synthetic enamel paint). (Make : As per List of Preferred makes)
6.01 | 150mm dia | 440.00 | MTR |  | 2300.00 | 1012000.00 | 2190.00 | 963600.00 | 3500.00 | 1540000.00 | 2790.00 | 1227600.00 | 2258.00 | 993520.00 | 963600.00 | Delta Leonis Building Solutions
6.02 | 100mm dia | 20.00 | MTR |  | 1900.00 | 38000.00 | 1949.00 | 38980.00 | 2900.00 | 58000.00 | 2110.00 | 42200.00 | 1956.00 | 39120.00 | 38000.00 | J.K.DEFENCE FIRE ENGG. SERVICES
6.03 | 80mm dia | 24.00 | MTR |  | 1800.00 | 43200.00 | 1349.00 | 32376.00 | 2499.00 | 59976.00 | 1680.00 | 40320.00 | 1592.00 | 38208.00 | 32376.00 | Delta Leonis Building Solutions
6.04 | 25mm dia | 24.00 | MTR |  | 800.00 | 19200.00 | 449.00 | 10776.00 | 1200.00 | 28800.00 | 490.00 | 11760.00 | 485.00 | 11640.00 | 10776.00 | Delta Leonis Building Solutions
7.00 | Supplying, fixing, testing and commissioning of pipes of following size of MS Heavy class pipes along with necessary fittings such as bends, tees, flanges, washers, GI nuts & bolts etc. adequately supported on rigid supports as applicable, duly painted with anti corrosive wrapping, coating conforming to IS 10221 and buried in ground including excavation and refilling, concrete blocks (if required) etc. complete as required. a) 150mm dia (Make : As per list of preferred makes) | 18.00 | MTR |  | 2850.00 | 51300.00 | 2999.00 | 53982.00 | 4999.00 | 89982.00 | 3110.00 | 55980.00 | 3879.00 | 69822.00 | 51300.00 | J.K.DEFENCE FIRE ENGG. SERVICES
8.00 | Supplying, fixing, testing and commissioning of pipes of following size of MS Heavy class pipes along with necessary fittings such as bends, tees, flanges, washers, GI nuts & bolts, adequately supported on rigid support with clamps as applicable, duly painted with anti corrosive wrapping, coating conforming to IS 10221 in existing Trench / Pipe / Man hole etc. complete as required. a) 150mm dia (Make : As per list of preferred makes) | 188.00 | MTR |  | 3150.00 | 592200.00 | 2899.00 | 545012.00 | 3900.00 | 733200.00 | 3668.00 | 689584.00 | 3190.00 | 599720.00 | 545012.00 | Delta Leonis Building Solutions
9.00 | Supplying and fixing single headed Internal/External Landing hydrant valve with instantaneous Gun metal couplings of 63 mm dia with cast iron wheel ISI marked conforming to IS 5290 (Type A) with blank PVC cap and GI chain etc. complete as required. (Make : As per List of Preferred makes) | 16.00 | EACH |  | 7500.00 | 120000.00 | 10499.00 | 167984.00 | 12000.00 | 192000.00 | 9590.00 | 153440.00 | 11954.00 | 191264.00 | 120000.00 | J.K.DEFENCE FIRE ENGG. SERVICES
10.00 | Supplying and fixing 63 mm dia 15 mtr. Long RRL hose pipe (Type A) conforming to IS 636 with instantaneous 63 mm dia Male and Female Gun Metal couplings duly binded with Copper wire, copper rivets etc., conforming to IS 903 etc. complete as required. (Make : As per List of Preferred makes) | 32.00 | EACH |  | 6000.00 | 192000.00 | 6849.00 | 219168.00 | 12000.00 | 384000.00 | 5274.00 | 168768.00 | 5376.00 | 172032.00 | 168768.00 | VOID FIRE CONSULTANTS
11.00 | Supplying and fixing First-aid Hose Reel with MS construction spray painted in Post office Red, conforming to IS 884 with upto date amendments, etc. complete as required with the following: (i) 30 m long 19 mm (nominal internal) dia Thermoplastic type II water hose as per IS: 12585. (ii) 19 mm nominal internal dia gun metal ball valve & nozzle. (iii) Drum and Swing type brackets for fixings the equipments on wall. (iv) Connections from riser with 25 mm dia gun metal Ball valve with union & reducer & M.S. Pipe etc. complete as required. (Make : As per List of Preferred makes) | 3.00 | SETS |  | 9000.00 | 27000.00 | 9749.00 | 29247.00 | 9000.00 | 27000.00 | 8357.00 | 25071.00 | 6824.00 | 20472.00 | 20472.00 | ILLUMECH ENGINEERING
12.00 | Supplying and fixing 63 mm dia Gun metal Branch pipe with 20mm (nominal Internal diameter) size Gun Metal nozzle conforming to IS 903 and suitable for instantaneous connection to interconnect Fire hose pipe coupling etc. complete as required. (Make : As per List of Preferred makes) | 16.00 | EACH |  | 4000.00 | 64000.00 | 3699.00 | 59184.00 | 5000.00 | 80000.00 | 2945.00 | 47120.00 | 3200.00 | 51200.00 | 47120.00 | VOID FIRE CONSULTANTS
13.00 | Supplying and fixing of Internal MS hose cabinet of size 1200 mm x 2100 mm x 600 mm made of 2 mm thick MS sheet with 6 mm thick glazed glass doors, Provision for hanging the hose & Branch Pipe in the cabinet including necessary locking arrangement suitable to accommodate Internal hydrant Fire Fighting system consisting of Main Pipe line, Hydrant Valve, 2 Nos. 15 Metres Long RRL Hose pipe, 1 No. branch pipe & First Aid Hose Reel Drum, mounted on Floor, necessary wall support/floor support with grouting and in raised brick platform & duly painted/powder coated with Post Office Red colour externally and white internally with synthetic enamel paint etc. complete as required. | 3.00 | NO. |  | 10000.00 | 30000.00 | 12499.00 | 37497.00 | 6000.00 | 18000.00 | 9590.00 | 28770.00 | 26845.00 | 80535.00 | 18000.00 | DElite System Engineering (India) Pvt. Ltd.
14.00 | Supplying and fixing of External MS hose cabinet of size 750 mm x 600 mm x 250 mm made of 2 mm thick MS sheet with 6 mm thick glazed glass doors, Provision for hanging the hose & Branch pipe in the cabinet including necessary locking arrangement suitable to accommodate 2Nos. 15 Metres. Long RRL Hose & 1 No. Branch pipe, mounted on wall/floor with grouting, raised brick platform & duly painted with Post Office Red Colour externally and white internally with synthetic enamel paint etc. complete as required. | 13.00 | NO. |  | 6000.00 | 78000.00 | 7349.00 | 95537.00 | 5000.00 | 65000.00 | 4247.00 | 55211.00 | 9984.00 | 129792.00 | 55211.00 | VOID FIRE CONSULTANTS
15.00 | Supply, Installation, Testing and Commissioning of Non-return valve, Cast Iron, Double flange, Wedge Stainless spindle, PN 1.6 rating of following sizes confirming to IS:5312 complete with rubber gasket, GI bolts nuts, washers etc. complete as required. (Make : As per List of Preferred makes)
15.01 | 150 mm dia | 3.00 | NO. |  | 10000.00 | 30000.00 | 16249.00 | 48747.00 | 19000.00 | 57000.00 | 16318.00 | 48954.00 | 28637.00 | 85911.00 | 30000.00 | J.K.DEFENCE FIRE ENGG. SERVICES
15.02 | 80 mm dia | 1.00 | NO. |  | 7500.00 | 7500.00 | 7099.00 | 7099.00 | 12000.00 | 12000.00 | 6035.00 | 6035.00 | 12845.00 | 12845.00 | 6035.00 | VOID FIRE CONSULTANTS
16.00 | Supply, Installation, Testing and Commissioning of Y strainer, Cast Iron, Double flange, Stainless steel mesh of following sizes, PN 1.6 rating confirming to complete with rubber gasket, GI bolts nuts, washers etc. complete as required. (Make : As per List of Preferred makes)
16.01 | 150 mm dia | 2.00 | NO. |  | 35000.00 | 70000.00 | 24759.00 | 49518.00 | 29000.00 | 58000.00 | 18840.00 | 37680.00 | 32845.00 | 65690.00 | 37680.00 | VOID FIRE CONSULTANTS
16.02 | 80 mm dia | 1.00 | NO. |  | 15000.00 | 15000.00 | 9799.00 | 9799.00 | 22000.00 | 22000.00 | 6513.00 | 6513.00 | 14765.00 | 14765.00 | 6513.00 | VOID FIRE CONSULTANTS
17.00 | Supply, Installation, Testing and Commissioning of following sizes Butterfly valve PN 1.6, with cast iron body, Double flange, Stainless steel Disc, EPDM seal conforming to IS 13095 complete with rubber gasket, GI bolts nuts, washers etc. complete as required. (Make : As per List of Preferred makes)
17.01 | 150 mm dia | 17.00 | NO. |  | 10000.00 | 170000.00 | 8251.00 | 140267.00 | 7999.00 | 135983.00 | 5680.00 | 96560.00 | 12784.00 | 217328.00 | 96560.00 | VOID FIRE CONSULTANTS
17.02 | 80 mm dia | 1.00 | NO. |  | 6500.00 | 6500.00 | 6149.00 | 6149.00 | 5000.00 | 5000.00 | 3150.00 | 3150.00 | 5872.00 | 5872.00 | 3150.00 | VOID FIRE CONSULTANTS
18.00 | Supplying and fixing 4 way Fire Bridgade connection of cast iron body with 4 Nos. Gun metal male instantaneous inlet couplings complete with rubber cap and GI chain for 150 mm dia MS pipe connection, conforming to IS etc. complete as required. (Make : As per List of Preferred makes) | 1.00 | NO. |  | 15000.00 | 15000.00 | 14998.00 | 14998.00 | 12000.00 | 12000.00 | 9590.00 | 9590.00 | 15294.00 | 15294.00 | 9590.00 | VOID FIRE CONSULTANTS
19.00 | Supplying and fixing Air vessel, floor mounting type, made of 250 mm dia, 8 mm thick MS sheet, 1200 mm height with air release valve on top and flanged connection to riser, drain arrangement with 25 mm dia Gun metal Ball valve, with required accessories, pressure gauge, seated on concrete/brick pedestal and painting with synthetic enamel paint of approved shade etc. complete as required. | 1.00 | NO. |  | 26500.00 | 26500.00 | 21999.00 | 21999.00 | 5000.00 | 5000.00 | 16440.00 | 16440.00 | 38790.00 | 38790.00 | 5000.00 | DElite System Engineering (India) Pvt. Ltd.
20.00 | Supply, Installation, Testing and Commissioning of Pressure guage 0-200 PSI (0-14 Kg) range, 3/8" BSP bottom entry, 4" dial weather proof with stainless steel internals, siphon tube and ball valve including fittings etc. complete as required. (Make : As per List of Preferred makes) | 5.00 | NO. |  | 2000.00 | 10000.00 | 2749.00 | 13745.00 | 1500.00 | 7500.00 | 1932.00 | 9660.00 | 3265.00 | 16325.00 | 7500.00 | DElite System Engineering (India) Pvt. Ltd.
21.00 | Supplying, Installation, Testing and Commissioning of Pressure switch including necessary wiring upto control panel, connection with existing pipeline etc. complete as required. (Make : As per List of Preferred makes) | 3.00 | NO. |  | 3250.00 | 9750.00 | 2599.00 | 7797.00 | 2200.00 | 6600.00 | 1450.00 | 4350.00 | 3265.00 | 9795.00 | 4350.00 | VOID FIRE CONSULTANTS
22.00 | Supplying, Installation, Testing and Commissioning of 50 mm Pressure release valve with Gun metal Ball valve etc. complete as required. (Make : As per List of Preferred makes) | 2.00 | NO. |  | 7000.00 | 14000.00 | 7249.00 | 14498.00 | 3000.00 | 6000.00 | 11339.00 | 22678.00 | 19890.00 | 39780.00 | 6000.00 | DElite System Engineering (India) Pvt. Ltd.
23.00 | Supplying, testing, installation & commissioning of 25 mm Air Release release valve with Gun metal Ball valve including etc. complete as required. (Make : As per List of Preferred makes) | 1.00 | NO. |  | 4500.00 | 4500.00 | 2549.00 | 2549.00 | 3400.00 | 3400.00 | 1220.00 | 1220.00 | 6964.00 | 6964.00 | 1220.00 | VOID FIRE CONSULTANTS
24.00 | Main Fire Pump Panel: Fabrication, Supply, Installation, Testing and Commissioining of Electrical LT Panel conforming to IEC 61439 (TTA type) of cubicle construction, floor mounted type, fabricated out of 2 mm thick CRCA sheet, compartmentalized with hinged lokable doors, dust and vermin proof, powder coated of approved shade after 7 tank treatment process, cable alley, inter connection, having switchgears and accessories mounting and internal wirng, earth terminals, etc., complete in all respects, suitable for operation on 415V, 3 phase, 50 Hz AC supply with enclosure protection class IP 42 etc. complete as required. INCOMERS: 2 Nos. Incomers of 250 Amps TPN, MCCB, 35 KA with Microprocessor based release, each Incomer having Digital Voltmeter (0-500 volts), Digital Ammeter (0 - 250 Amps), Set of 3 phase indicating Lamps LED type with protective fuse and Mechanical Interlocking for both the Incomers. BUSBAR Set of Aluminium Bus bar of 300 Amps.
24.01 | OUTGOINGS All outgoings shall have Digital Ammeter and ON, OFF, TRIP Indication lamps 1) Man Fire Pump - 1 No. 200 Amps, TPN MCCB, 25 KA with Microprocessor release, suitable HP fully automatic star/delta starter with overloaded protection, current sensing type single phase preventor, Selector swicth, Push buttons complete with all accessories and internal wiring required for auto / manual operation. 2) Jockey Pump - 1 No. 100 Amps, TPN, 25 KA MCCB with thermal magnetic release suitable HP fully atomatic DOL starter with overload protection, current sensing type single phase preventor, Selector switch, push buttons, complete with all accessories and internal wiring required for auto / manual operation. 3) Spare outgoing cubicle with 125 Amps TPN MCCB. 4) Diesel Engine Control - 1 No. consisting of Auto/ manual Selector Switch & 3 attempt starting device, timers and relays as required, push buttons, start/stop in manual mode, Indication lamp for High/ Low Lube Oil pressure, High water Termperature and Engine ON indication, battery Charger suitable for 12 V/ 24 V DC with boost and trickle selector switch, 0-15 V/0-30 V DC volt meter, 0-20 A DC Ammeter, All standard relays and accessories for auto / manual operation of diesel engine. (All items as above : 24.00 to 24.01) | 1.00 | JOB |  | 700000.00 | 700000.00 | 299999.00 | 299999.00 | 400000.00 | 400000.00 | 250000.00 | 250000.00 | 485895.00 | 485895.00 | 250000.00 | VOID FIRE CONSULTANTS
25.00 | Supply of following size of PVC/XLPE insulated PVC sheathed Copper conductor armoured power cable of 1.1 KV grade conforming to IS-7098 Part-I Part 1 amended upto date etc. complete as required.
25.01 | 3C x 16 Sqmm | 40.00 | MTR |  | 300.00 | 12000.00 | 349.00 | 13960.00 | 300.00 | 12000.00 | 1053.00 | 42120.00 | 750.00 | 30000.00 | 12000.00 | DElite System Engineering (India) Pvt. Ltd., J.K.DEFENCE FIRE ENGG. SERVICES
25.02 | 3C x 50 sqmm | 40.00 | MTR |  | 450.00 | 18000.00 | 574.00 | 22960.00 | 499.00 | 19960.00 | 2765.00 | 110600.00 | 2980.00 | 119200.00 | 18000.00 | J.K.DEFENCE FIRE ENGG. SERVICES
26.00 | Supply and making end termination with double brass compression gland and copper lugs for following size of PVC insulated and PVC Sheathed/ XLPE aluminuim conductor cable of 1.1 KV grade as required.
26.01 | 3C x 16 Sqmm | 2.00 | SETS |  | 1500.00 | 3000.00 | 449.00 | 898.00 | 1200.00 | 2400.00 | 1164.00 | 2328.00 | 25736.00 | 51472.00 | 898.00 | Delta Leonis Building Solutions
26.02 | 3C x 50 sqmm | 2.00 | SETS |  | 2000.00 | 4000.00 | 649.00 | 1298.00 | 1200.00 | 2400.00 | 1370.00 | 2740.00 | 98650.00 | 197300.00 | 1298.00 | Delta Leonis Building Solutions
26.03 | 3.5C x 70 Sqmm | 2.00 | SETS |  | 3000.00 | 6000.00 | 624.00 | 1248.00 | 1500.00 | 3000.00 | 1712.00 | 3424.00 | 210552.00 | 421104.00 | 1248.00 | Delta Leonis Building Solutions
27.00 | Supply & Fixing of 4.5 Kg Capacity Co2 Fire Extinguser including filling of Co2 Gas, discharge pipe, handle, wheel type Brass valve, wall hook, conforming to IS 15683 etc., complete as required. (Make : As per List of Preferred makes) | 4.00 | NO. |  | 7500.00 | 30000.00 | 5199.00 | 20796.00 | 6000.00 | 24000.00 | 5343.00 | 21372.00 | 6823.00 | 27292.00 | 20796.00 | Delta Leonis Building Solutions
28.00 | Supply & Fixing of 6 Kg capacity ABC type Fire Extinguser including dry powder, propellant, discharge hose, handle, valve assembly, Nozzle, Pressure indicating Gauge, wall hook, conforming to IS 15683 etc. complete as required. (Make : As per List of Preferred makes) | 4.00 | NO. |  | 3000.00 | 12000.00 | 2599.00 | 10396.00 | 6000.00 | 24000.00 | 2350.00 | 9400.00 | 2583.00 | 10332.00 | 9400.00 | VOID FIRE CONSULTANTS
29.00 | Supply & Fixing of 50 Kg capacity mobile wheeled type ABC type Fire extinguser including dry powder, propellant, discharge hose, handle, Valve assembly, Nozzle, Pressure indicating Gauge, conforming to IS 16018 etc., complete as required. (Make : As per List of Preferred makes) | 1.00 | NO. |  | 25000.00 | 25000.00 | 23998.00 | 23998.00 | 40000.00 | 40000.00 | 20139.00 | 20139.00 | 24857.00 | 24857.00 | 20139.00 | VOID FIRE CONSULTANTS
30.00 | Supply, Installation, Testing and Commissioning of Frangible, Lattice type structure & illuminated wind direction indicator (WDI) confirming to ICAO Annex 14 ,Volume I and suitable for operation on 230V, 50Hz, Single phase AC Supply and consist of following as required. (a) Height not less than 6670 mm FRP frangible mast. The frangibility shall confirm to ICAO Annex14 & Aerodrome design manual part-6/FAA. The color of pole/mast shall be preferably Aviation red/white. (b) Wind sock assembly complete with sliprings, drum, bracket for drum, bearing, carbon brush with holder etc. (c) 1 No. LED light (20 W nominal capacity) inside the windsock drum, 4 Nos. LED light (20 W nominal capacity) fittings with shades for external illumination along with Lamps mounting arrangement for outdoor conditions. (d) One No. LED Aviation obstruction light (AOL) at top having aluminium castbody and red polycarbonate dome suitable for operation on 230V, 50Hz, AC supply. (e) Internal wiring, provision for remote control operation, electric supply, control panel, junction box etc., meeting ICAO/FAA standards and specification including wind sock of 3600mm long made of special natural colour, fungus proof, nylon fabric with alternate black/red and white strip etc., complete as required. (f) Providing and laying and modification in existing cement concrete foundation suitable for installation of Windsock as per OEM recommendations. | 1.00 | JOB |  | 125000.00 | 125000.00 | 350999.00 | 350999.00 | 250000.00 | 250000.00 | 274000.00 | 274000.00 | 635382.00 | 635382.00 | 125000.00 | J.K.DEFENCE FIRE ENGG. SERVICES
31.00 | SH II : Associated Civil works
32.00 | Dismantling and Shifting of Existing Diesel Engine Driven Main Fire Pump, Electrical Driven Main Fire Pump, and Jockey Pump from the Underground(UG) pump room including Disconnection and removal of associated Pipelines, fittings, valves, nuts, bolts, Base plates, cables, Electrical panel, Diesel tank etc., as required. The works involves breaking of existing RCC/Brick foundation for all three pumps, breaking of UG sump wall for removal of pumps if required, removal of debris/rubbish including safe lifting and shifting of materials from under ground sump to outside Airport premises as per the directions of Engineer-in-charge and rebuilding the damaged walls, floor patching etc. complete as required. | 1.00 | JOB |  | 250000.00 | 250000.00 | 715000.00 | 715000.00 | 100000.00 | 100000.00 | 102750.00 | 102750.00 | 256774.00 | 256774.00 | 100000.00 | DElite System Engineering (India) Pvt. Ltd.
33.00 | Construction and RCC Manhole Chamber of Internal Dimension 1M X 1M X 1M (External 1.2M X 1.2M X 1.2M) with RCC half split top cover of thickness 100mm with L angle reinforced at all sides of top and bottom of covers, necessary openings for pipe line entry/exit, lifting hook including finishing etc., complete as required. | 10.00 | NO. |  | 20000.00 | 200000.00 | 24000.00 | 240000.00 | 30000.00 | 300000.00 | 26400.00 | 264000.00 | 28160.00 | 281600.00 | 200000.00 | J.K.DEFENCE FIRE ENGG. SERVICES
34.00 | Earth work in excavation by mechanical means (Hydraulic excavator) / manual means in foundation trenches or drains (not exceeding 1.5 m in width or 10 sqm on plan), including dressing of sides and ramming of bottoms, lift upto 1.5 m, including getting out the excavated soil and disposal of surplus excavated soil as directed, within a lead of 50 m. (a) All kinds of soil. | 27.00 | CUM |  | 250.00 | 6750.00 | 250.00 | 6750.00 | 7000.00 | 189000.00 | 243.00 | 6561.00 | 650.00 | 17550.00 | 6561.00 | VOID FIRE CONSULTANTS
35.00 | Demolishing cement concrete manually/ by mechanical means including disposal of material within 50 metres lead as per direction of Engineer - in - charge. (a) Nominal concrete 1:3:6 or richer mix (i/c equivalent design mix) | 5.76 | CUM |  | 6500.00 | 37440.00 | 1850.00 | 10656.00 | 4000.00 | 23040.00 | 3335.00 | 19209.60 | 7980.00 | 45964.80 | 10656.00 | Delta Leonis Building Solutions
36.00 | Dismantling of flexible pavement (bituminous courses) by mechanical means and disposal of dismantled material up to a lead of 1 kilometre, as per direction of Engineer-in-charge. | 4.86 | CUM |  | 7000.00 | 34020.00 | 300.00 | 1458.00 | 9000.00 | 43740.00 | 575.00 | 2794.50 | 1536.00 | 7464.96 | 1458.00 | Delta Leonis Building Solutions
37.00 | Supplying, spreading and filling of M sand in ground level including watering, ramming and dressing complete as per the direction of Engineer in Charge. | 1.20 | CUM |  | 3000.00 | 3600.00 | 2400.00 | 2880.00 | 9000.00 | 10800.00 | 3425.00 | 4110.00 | 2688.00 | 3225.60 | 2880.00 | Delta Leonis Building Solutions
38.00 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering - All work up to plinth level : (a) 1:4:8 (1 Cement : 4 coarse sand (zone-III) : 8 graded stone aggregate 40 mm nominal size) | 3.00 | CUM |  | 9000.00 | 27000.00 | 6000.00 | 18000.00 | 12000.00 | 36000.00 | 2196.00 | 6588.00 | 9600.00 | 28800.00 | 6588.00 | VOID FIRE CONSULTANTS
39.00 | Centering and shuttering including strutting, propping etc. and removal of form work for : (a) Foundations, footings, bases for columns, etc. for mass concrete | 8.00 | SQM |  | 750.00 | 6000.00 | 300.00 | 2400.00 | 9000.00 | 72000.00 | 674.00 | 5392.00 | 1200.00 | 9600.00 | 2400.00 | Delta Leonis Building Solutions
40.00 | Centering and shuttering including strutting, propping etc. and removal of form work for : (a) Columns, Pillars, Piers, Abutments, Posts and Struts. | 40.00 | SQM |  | 1000.00 | 40000.00 | 900.00 | 36000.00 | 3000.00 | 120000.00 | 1454.00 | 58160.00 | 1200.00 | 48000.00 | 36000.00 | Delta Leonis Building Solutions
41.00 | Providing 1:1½:3 cement concrete (1 Cement: 1½ coarse sand(zone-III) derived from natural sources : 3 graded stone aggregate 20 mm nominal size derived from natural sources). | 4.64 | CUM |  | 9500.00 | 44080.00 | 6000.00 | 27840.00 | 9000.00 | 41760.00 | 10980.00 | 50947.20 | 8320.00 | 38604.80 | 27840.00 | Delta Leonis Building Solutions
42.00 | Steel reinforcement for R.C.C. work including straightening, cutting, bending, placing in position and binding all complete upto plinth level. (a) Thermo-Mechanically Treated bars of grade Fe-500D or more. | 603.00 | KGS |  | 150.00 | 90450.00 | 525.00 | 316575.00 | 150.00 | 90450.00 | 145.00 | 87435.00 | 112.00 | 67536.00 | 67536.00 | ILLUMECH ENGINEERING
43.00 | Providing and laying non-pressure NP2 class (light duty) R.C.C. pipes with collars jointed with stiff mixture of cement mortar in the proportion of 1:2 (1 cement : 2 fine sand) including testing of joints etc. complete : (a) 300 mm dia. R.C.C. pipe | 48.00 | MTR |  | 1250.00 | 60000.00 | 999.00 | 47952.00 | 3000.00 | 144000.00 | 510.00 | 24480.00 | 1536.00 | 73728.00 | 24480.00 | VOID FIRE CONSULTANTS
44.00 | Providing, hoisting and fixing above plinth level up to floor five level precast reinforced cement concrete work in string courses, bands, copings, bed plates, anchor blocks, plain window sills and the like, including the cost of required centering, shuttering but , excluding cost of reinforcement with 1:1.5:3 (1 cement : 1.5 coarse sand(zone-III) derived from natural sources : 3 graded stone aggregate 20 mm nominal size derived from natural sources). | 2.70 | CUM |  | 10500.00 | 28350.00 | 1500.00 | 4050.00 | 20000.00 | 54000.00 | 11420.00 | 30834.00 | 12544.00 | 33868.80 | 4050.00 | Delta Leonis Building Solutions
| Total in Figures |  |  |  |  | 6368340.00 |  | 6015790.00 |  | 7148991.00 |  | 5397958.30 |  | 7722699.96
Lowest Amount Quoted BY: VOID FIRE CONSULTANTS(5397958.30)

## BOQ Summary
BOQ Summary Details Tender Title: Replacement of Fire Fighting system for Terminal Building at Puducherry Airport Tender ID: 2025_AAI_250054_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | VOID FIRE CONSULTANTS (BID ID -916722) | 5397958.30 | L1
| 2 | Delta Leonis Building Solutions (BID ID -915378) | 6015790.00 | L2
| 3 | J.K.DEFENCE FIRE ENGG. SERVICES (BID ID -916477) | 6368340.00 | L3
| 4 | DElite System Engineering (India) Pvt. Ltd. (BID ID -913752) | 7148991.00 | L4
| 5 | ILLUMECH ENGINEERING (BID ID -917039) | 7722699.96 | L5