## BoQ1
Government eProcurement System Created By: Harpal Singh Daral Created Date/Time: 10-Nov-2025 01:09 PM Tender Title: Provision of VRF System in Passenger Boarding Bridge at Srinagar International Airport Tender ID: 2025_AAI_250674_1
Tender Inviting Authority: SM (ENGG-ELECT), AAI, SRINAGAR INTERNATIONAL AIRPORT, SRINAGAR, J&K-190007.
Name of Work: Name of Work : Provision of VRF System in Passenger Boarding Bridge at Srinagar International Airport.
Contract No: <Enter Contract No Details>
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | U V ENGINEERS (GSTN-NA) BID ID -917277 |  | Blue Star Ltd (GSTN-NA) BID ID -917103 |  | V Save Electronics Pvt Ltd (GSTN-NA) BID ID -917226 |  | M/s Alpha Tech Engineers (GSTN-NA) BID ID -917346
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | VRF System Supply, Installation, Testing and Commissioning of Variable Refrigerant Flow modular type airconditioning system suitable for 220 +/- 10 % volt, 50 Hz, 1 phase AC supply for outdoor units and 220 ± 10 % volt, 50 Hz, 1 phase AC supply for indoor units with stepless modulation complete with indoor and outdoor units,individual remote controller and compatible for centralised controller, interconnected refrigerant piping, full charge of refrigerant gas and oil, control cabling, loading & unloading etc.as per site requirements and details given in the specifications and having following items: (Refrigerant to be used shall be R410 A). Hi Side - Outdoor Units Outdoor unit cooling / Heat Pumps, having cooling COP not less than 3.1 at AHRI conditions and conditions equipped with efficient fully inverter scroll/rotary compressor, special heat exchanger, top discharge type, low noise condenser fan, auto check function for connection error, auto address setting and minimum capacity as mentioned below incuding MS angle frame of size 50mm x50mm x 5mm as per OEM standard complete with all accessories. ODU - 4 HP (Heating & Cooling) | 10.00 | EACH |  | 182000.00 | 1820000.00 | 100000.00 | 1000000.00 | 130550.00 | 1305500.00 | 132000.00 | 1320000.00 | 1000000.00 | Blue Star Ltd
2.00 | Low Side - Indoor Units - (Ceiling Mounted Cassette Units) Supply, Installation, Testing and Commissioning of Indoor Units for variable refrigerant flow airconditioning system suitable for 220 ± 10% volt, 50 Hz, 1 phase AC supply equipped with pre-filter,fan section with low noise fan, multispeed motor, coil section with DX (Direct Expansion) coil, outer cabinet, drain pan, drain water lift-up mechanism, insulation, pipe connections, fresh air intake etc. complete with PVC insulated FRLS copper conductor electric wire upto 1.5 metre length for electrically connecting the IDU with minimum capacity as given below as per specifications.
2.10 | Ceiling Mounted Cassette Four Way Flow with Cassette Panel 3.00 TR Cooling Capacity with Corded Remote Controller. (Please note that the dimension of main unit shall be as per Toshiba Indoor Model No. RAV-SM 1104UT-E i.e HxWxD = 319mm x 840mm x 840mm) | 6.00 | EACH |  | 70000.00 | 420000.00 | 48500.00 | 291000.00 | 59946.00 | 359676.00 | 42000.00 | 252000.00 | 252000.00 | M/s Alpha Tech Engineers
2.20 | Under Ceiling Mounted Cassette one Way Flow with Cassette Panel 2.50 TR Cooling Capacity complete with Corded Remote Controller (Please note that the dimension of main unit shall be as per Toshiba Indoor Model No. RAV-SM 804CT-E i.e HxWxD = 210mm x1180mm x 680mm) | 4.00 | EACH |  | 50000.00 | 200000.00 | 63500.00 | 254000.00 | 49955.00 | 199820.00 | 37000.00 | 148000.00 | 148000.00 | M/s Alpha Tech Engineers
3.00 | Transmission Control Wiring Providing and fixing transmission/control wiring PVC insulated of 2 core x 1.5 sq.mm copper conductor shielded flexible wire in 25 mm PVC conduits between outdoor to indoor and remote control unit. (Make of cable : KEI/ POLYCAB/ HAVELLS) (Make for conduit: BEC /AKG /POLYPACK/PRECISION /MIHIR/PRINCE.) | 70.00 | Meter |  | 180.00 | 12600.00 | 270.00 | 18900.00 | 120.00 | 8400.00 | 100.00 | 7000.00 | 7000.00 | M/s Alpha Tech Engineers
4.00 | Refrigerant Piping for VRV/VRF System Supply, installation, testing and commissioning of following interconnecting copper refrigerant pipe suitable for VRF system of airconditioning conforming to JISH 3300: 1997, recessed/concealed or laid and supported on the existing slotted cable trays, duly insulated with closed cell elastomeric nitrile rubber type tubular insulation of nominal thickness as specified between indoor and outdoor units as per specification. Make: RAJCO / MANDEV / MEXFLOW
4.10 | 15.9 mm (5/8 inch) OD with 0.80 mm wall thickness (Insulation : 13 mm) | 70.00 | Meter |  | 800.00 | 56000.00 | 925.00 | 64750.00 | 1000.00 | 70000.00 | 600.00 | 42000.00 | 42000.00 | M/s Alpha Tech Engineers
4.20 | 9.5 mm (3/8 inch) OD with 0.80 mm wall thickness (Insulation : 13 mm) | 70.00 | Meter |  | 500.00 | 35000.00 | 775.00 | 54250.00 | 1000.00 | 70000.00 | 300.00 | 21000.00 | 21000.00 | M/s Alpha Tech Engineers
5.00 | Drain Pipe Supply, installation, testing and commissioning of following Drain piping made of rigid uPVC pipe Class - 3 (6 kg/cm2) confirming to IS 4985-2000 complete with fittings, supports etc. as per specifications and duly insulated with 9 mm thick closed cell nitrile rubber insulation.
5.10 | 25 mm dia (with insulation) | 70.00 | Meter |  | 180.00 | 12600.00 | 230.00 | 16100.00 | 90.00 | 6300.00 | 140.00 | 9800.00 | 6300.00 | V Save Electronics Pvt Ltd
6.00 | Supply, Laying, testing & commissioning of size 3Core, 6 Sq.mm 1.1 KV grade multicore copper conductor XLPE insulated and PVC sheathed armoured cable as per IS : 7098:1988 (Part-I) with upto date amendments complete with end terminations, connections etc as required. | 120.00 | Meter |  | 1200.00 | 144000.00 | 510.00 | 61200.00 | 180.00 | 21600.00 | 400.00 | 48000.00 | 21600.00 | V Save Electronics Pvt Ltd
7.00 | Dismantling of existing 04 Nos. Toshiba make Cassette type units (Outdoor Model No. RAV-SM 1103AT-E and Indoor Model No. RAV-SM 1104UT-E) complete with control panel, refrigerant pipe with insulation, cable and connections etc. complete in all as required. | 1.00 | JOB |  | 8000.00 | 8000.00 | 4000.00 | 4000.00 | 5000.00 | 5000.00 | 1000.00 | 1000.00 | 1000.00 | M/s Alpha Tech Engineers
8.00 | Dismantling of existing 04 Nos. Toshiba make Cassette type units (Outdoor Model No. RAV-SM 803AT-E and Indoor Model No. RAV-SM 804CT-E) complete with control panel, refrigerant pipe with insulation, cable and connections etc. complete in all as required. | 1.00 | JOB |  | 8000.00 | 8000.00 | 4000.00 | 4000.00 | 5000.00 | 5000.00 | 1500.00 | 1500.00 | 1500.00 | M/s Alpha Tech Engineers
9.00 | SITC of following capacity , Hi-wall mount, Cold type, BEE rated 5 STAR Split type Air conditioner with inverter type compressor filled with R410a/ R32 gas, copper condensor tube/coil, cordless remote control for temperature adjustment, indoor unit blower speed, swing adjustment, auto restart, sleep mode, turbo mode, with LED display for temperature and other standard features suitable for operation on 230 V, 50 Hz , AC supply including wiring with suitable size FR, PVC flexible copper cable for control/power wiring, Suction and liquid line copper piping between indoor & outdoor unit (approx distance of 10 ft) with insulation as per technical specifications etc complete as required.
9.10 | 1.5 TR , Minimum cooling capacity 18000 BTU/Hr | 2.00 | Job |  | 50000.00 | 100000.00 | 27000.00 | 54000.00 | 17500.00 | 35000.00 | 40000.00 | 80000.00 | 35000.00 | V Save Electronics Pvt Ltd
10.00 | SITC of following capacity, Hi-wall mount, Hot & Cold type, Split type Air conditioner with inverter type compressor having working operating temperature range (-10 degree C to 45 degree C) filled with R410a/ R32 gas, copper condensor tube/coil, cordless remote control for temperature adjustment, indoor unit blower speed, swing adjustment, auto restart, sleep mode, turbo mode, with LED display for temperature and other standard features suitable for operation on 230 V, 50 Hz , AC supply including wiring with suitable size FR, PVC flexible copper cable for control/power wiring , Suction and liquid line copper piping between indoor & outdoor unit (approx distance of 10 ft) with insulation as per technical specifications etc complete as required
10.10 | 1.5 TR , BEE rated 5 STAR, Minimum cooling capapcity- 16800 BTU/Hr & Minimum Heating capacity- 18000 BTU/Hr. | 2.00 | Job |  | 55000.00 | 110000.00 | 31000.00 | 62000.00 | 17500.00 | 35000.00 | 62000.00 | 124000.00 | 35000.00 | V Save Electronics Pvt Ltd
| Total in Figures |  |  |  |  | 2926200.00 |  | 1884200.00 |  | 2121296.00 |  | 2054300.00
Lowest Amount Quoted BY: Blue Star Ltd(1884200.00)

## BOQ Summary
BOQ Summary Details Tender Title: Provision of VRF System in Passenger Boarding Bridge at Srinagar International Airport Tender ID: 2025_AAI_250674_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Blue Star Ltd (BID ID -917103) | 1884200.00 | L1
| 2 | M/s Alpha Tech Engineers (BID ID -917346) | 2054300.00 | L2
| 3 | V Save Electronics Pvt Ltd (BID ID -917226) | 2121296.00 | L3
| 4 | U V ENGINEERS (BID ID -917277) | 2926200.00 | L4