## BoQ1
Government eProcurement System Created By: Madan Mohan Agrawal Created Date/Time: 11-Nov-2025 03:22 PM Tender Title: Replacement of AHU, Valves and modification of piping in Terminal Building at Surat International Airport, Surat. Tender ID: 2025_AAI_250993_1
Tender Inviting Authority: AGM (E-E)-II, AAI, Surat Airport, Surat
Name of Work :"Replacement of AHU, Valves and modification of piping in Terminal Building at Surat International Airport, Surat."
Tender ID : 2025_AAI_250993_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | M/s. PRANAM HVAC ENGINEERING PVT. LTD. (GSTN-24AAHCP2093C1ZP) BID ID -916113 |  | SNOWMEX ENGINEERS LIMITED (GSTN-07AAMCS8717P1ZF) BID ID -920172 |  | Ingenious Industries (GSTN-27AADFI4734Q1ZV) BID ID -921232 |  | AirBizz AirConditioning Pvt. Ltd. (GSTN-NA) BID ID -913231 |  | Mvac Engineers (GSTN-NA) BID ID -921125
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply, Installation, Testing and commissioning of factory built (suitable for assembling at site in operational terminal Building AHU room) floor mounted chilled water double skin type horizontal Air Handling Units made with Thermal Break Profile 46 -50 mm panel thicknes consisting of pre plasticized G.I. casing of thickness 1 mm outside layer and 1 mm inside layer with CFC free polyurethane foam (PUF) insulation factory injected between them by injection moulding machine, complete with blower section with blower suitable for static pressure of 70 mm WC, minimum 2 bend GSS/PVC eliminators, cooling coil section with aluminium finned copper tubes (tubes thickness not less than 0.5 mm) cooling coil of 6 row deep, filter section with 50 mm thick washable synthetic type air pre-filters, MERV-8 Pre-filter section (90% down to 10 microns) with UV light, backward curve belt drive DIDW blower fan package with TEFC drive motor of efficiency class IE3 suitable for 415 ± 10% V, 50Hz, 3 Phase AC supply suitably designed for variable frequency drive applications, drain connections, stainless steel (1.25mm thick) drain pan with PUF insulation,3mm thick galvanised steel base channel frame, 150 mm dia. dial type Stainless steel pressure gauges (2 Nos.) and industrial type thermometers (2 Nos.) at the inlet and outlet of AHU including test points and necessary vibration isolation arrangement, Duct flexible connector (fire proof) shall be provided at outlets and return connection of AHU etc. with SITC of starter panel with VFD (fabricated out of powder coated 16 gauge CRCA sheet) and control accessories i/c LED indicating lamp, Sensor for operation of fire damper, inter connection to AHU and other accessories as per specification for following capacities. VFD should have suitable comunication port to work with BMS system, starter panel should have minimum 04 potential free contacts. Safety Features : 1) The Fan Access Door shall be equipped with micro-switch inter locked with fan motor to enable switching off the fan motor automatically in the event of door opening. 2) The Access Door shall further have wire mesh screen as an added safety feature bolted on to the unit frame. 3) Fan and motor base shall be properly grounded.
1.01 | 35000 CFM | 1.00 | Job |  | 1810000.00 | 1810000.00 | 1328562.00 | 1328562.00 | 1904500.00 | 1904500.00 | 1670921.00 | 1670921.00 | 1349450.00 | 1349450.00 | 1328562.00 | SNOWMEX ENGINEERS LIMITED
1.02 | 23500 CFM | 2.00 | Job |  | 1205000.00 | 2410000.00 | 901520.00 | 1803040.00 | 1254240.00 | 2508480.00 | 1245657.00 | 2491314.00 | 943930.00 | 1887860.00 | 1803040.00 | SNOWMEX ENGINEERS LIMITED
1.03 | 15000 CFM | 2.00 | Job |  | 821000.00 | 1642000.00 | 604160.00 | 1208320.00 | 741000.00 | 1482000.00 | 774493.00 | 1548986.00 | 624040.00 | 1248080.00 | 1208320.00 | SNOWMEX ENGINEERS LIMITED
1.04 | 10000 CFM | 1.00 | Job |  | 650000.00 | 650000.00 | 477000.00 | 477000.00 | 578110.00 | 578110.00 | 564992.00 | 564992.00 | 452100.00 | 452100.00 | 452100.00 | Mvac Engineers
2.00 | Supplying, laying/ fixing, testing and commissioning of following nominal sizes of chilled water piping inside the AHU Room in the building (with necessary clamps, vibration isolators and fittings but excluding valves, strainers, gauges etc.) duly insulated with following closed cell elastrometric nitrile rubber of minimum 45 Kg / m3 density, thermal conductivity 0.034 W/MK or better at 20 deg mean temperature class ‘O’ insulation 32 mm thick with Glass Cloth pre-applied by suitable adhesive complete including repairing of damage to building etc. as per specifications and as required complete in all respect. Note:-The Pipes of sizes 150 mm & below shall be M.S. ‘C’ class as per IS : 1239 and pipes size above 150 mm shall be welded black steel pipe heavy class as per IS: 3589, from minimum 6.35 mm thick M.S. Sheet for pipes upto 350 mm dia. and from minimum 7mm thick MS sheet for pipes of 400 mm dia and above.
2.01 | 125 mm dia (32 mm GC insulation) | 18.00 | Rtm |  | 3100.00 | 55800.00 | 100.00 | 1800.00 | 3491.25 | 62842.50 | 4478.00 | 80604.00 | 2710.00 | 48780.00 | 1800.00 | SNOWMEX ENGINEERS LIMITED
2.02 | 100 mm dia (32 mm GC insulation) | 24.00 | Rtm |  | 2500.00 | 60000.00 | 2291.00 | 54984.00 | 2930.00 | 70320.00 | 3793.00 | 91032.00 | 2240.00 | 53760.00 | 53760.00 | Mvac Engineers
2.03 | 80 mm dia (32 mm GC insulation) | 24.00 | Rtm |  | 2000.00 | 48000.00 | 1563.00 | 37512.00 | 2206.25 | 52950.00 | 3280.00 | 78720.00 | 1720.00 | 41280.00 | 37512.00 | SNOWMEX ENGINEERS LIMITED
2.04 | 65 mm dia (32 mm GC insulation) | 18.00 | Rtm |  | 1700.00 | 30600.00 | 100.00 | 1800.00 | 1896.25 | 34132.50 | 2816.00 | 50688.00 | 1440.00 | 25920.00 | 1800.00 | SNOWMEX ENGINEERS LIMITED
3.00 | Providing and fixing in position the following valves in the chilled water piping complete with counter flanges, nuts, bolts, gaskets, etc plumbing duly insulated to the same specifications as the connected piping and adequately supported as per specifications. BUTTERFLY VALVE (MANUAL) with C I / carbon steel body, SS Disc, Nitrile Rubber Seal & 0- Ring PN 16 pressure rating for chilled water circulation as specified including the insulation complete as required.
3.01 | 125 mm dia Butterfly valve | 4.00 | Each |  | 7050.00 | 28200.00 | 100.00 | 400.00 | 6187.50 | 24750.00 | 12376.00 | 49504.00 | 6910.00 | 27640.00 | 400.00 | SNOWMEX ENGINEERS LIMITED
3.02 | 100 mm dia Butterfly valve | 8.00 | Each |  | 5650.00 | 45200.00 | 5650.00 | 45200.00 | 3730.00 | 29840.00 | 9549.00 | 76392.00 | 5640.00 | 45120.00 | 29840.00 | Ingenious Industries
3.03 | 80 mm dia Butterfly valve | 8.00 | Each |  | 4300.00 | 34400.00 | 3650.00 | 29200.00 | 2800.00 | 22400.00 | 7571.00 | 60568.00 | 4530.00 | 36240.00 | 22400.00 | Ingenious Industries
3.04 | 65 mm dia Butterfly valve | 4.00 | Each |  | 3775.00 | 15100.00 | 100.00 | 400.00 | 2437.50 | 9750.00 | 6771.00 | 27084.00 | 3930.00 | 15720.00 | 400.00 | SNOWMEX ENGINEERS LIMITED
4.00 | Suuply and Fixing in position Y-Strainer of PN 16 rating fabricated out of MS 'C' class pipe with flanged ends at inlet and oulet connections with stainless steel strainer for chilled water circulation including insulation and with counter flanges, nuts, bolts, gaskets, etc. complete as required.
4.01 | 125 mm dia Y-Strainer | 1.00 | Each |  | 27100.00 | 27100.00 | 120.00 | 120.00 | 12687.50 | 12687.50 | 22057.00 | 22057.00 | 10900.00 | 10900.00 | 120.00 | SNOWMEX ENGINEERS LIMITED
4.02 | 100 mm dia Y-Strainer | 2.00 | Each |  | 15700.00 | 31400.00 | 9150.00 | 18300.00 | 6583.75 | 13167.50 | 13804.00 | 27608.00 | 8410.00 | 16820.00 | 13167.50 | Ingenious Industries
4.03 | 80 mm dia Y-Strainer | 2.00 | Each |  | 12200.00 | 24400.00 | 8150.00 | 16300.00 | 4802.50 | 9605.00 | 11368.00 | 22736.00 | 7080.00 | 14160.00 | 9605.00 | Ingenious Industries
4.04 | 65 mm dia Y-Strainer | 1.00 | Each |  | 9000.00 | 9000.00 | 120.00 | 120.00 | 4375.00 | 4375.00 | 8020.00 | 8020.00 | 6040.00 | 6040.00 | 120.00 | SNOWMEX ENGINEERS LIMITED
5.00 | Providing & Fixing in position of following sizes of Globe type 2 Way Pressure Independent Dynamic Balancing Valves, self balancing, pressure independent, 2-way control valve with 100% authority on the control valve. For 40 to 150 mm Grey iron body , Diff Pressure (P1-P3)- 30 To 400 kPa .The valve should be equipped with an electronic modulating actuator which can accept either 4(0)-20 mA / 2(0)-10 V DC signals. Operating voltage for actuator shall be 24V AC/ 50Hz. The actuator shall be able to close against maximum differential pressure of 6 Bar. Actuator body shall be of non-corrosive and shall be rated with IP42 or Higher. System shall be complete in accordance with AAI technical specifications.
5.01 | 125 mm dia | 1.00 | Each |  | 322000.00 | 322000.00 | 570.00 | 570.00 | 115397.50 | 115397.50 | 169427.00 | 169427.00 | 100920.00 | 100920.00 | 570.00 | SNOWMEX ENGINEERS LIMITED
5.02 | 100 mm dia | 2.00 | Each |  | 131000.00 | 262000.00 | 29000.00 | 58000.00 | 79086.25 | 158172.50 | 122594.00 | 245188.00 | 64010.00 | 128020.00 | 58000.00 | SNOWMEX ENGINEERS LIMITED
5.03 | 80 mm dia | 2.00 | Each |  | 90000.00 | 180000.00 | 27000.00 | 54000.00 | 65543.75 | 131087.50 | 107548.00 | 215096.00 | 56690.00 | 113380.00 | 54000.00 | SNOWMEX ENGINEERS LIMITED
5.04 | 65 mm dia | 1.00 | Each |  | 80500.00 | 80500.00 | 310.00 | 310.00 | 55022.50 | 55022.50 | 104085.00 | 104085.00 | 46580.00 | 46580.00 | 310.00 | SNOWMEX ENGINEERS LIMITED
6.00 | Dismantling & shifting (to Dismentle store of AAI) of existing double skin AHU of following capacity alongwith all valves, other accessories i/c cutting of connecting header of AHU unit in existing AHU Room in terminal building etc. complete as per site requirement for installtion of new AHU complete as required.
6.01 | 35000 CFM | 1.00 | Job |  | 25000.00 | 25000.00 | 15000.00 | 15000.00 | 65000.00 | 65000.00 | 83640.00 | 83640.00 | 95900.00 | 95900.00 | 15000.00 | SNOWMEX ENGINEERS LIMITED
6.02 | 23500 CFM | 2.00 | Job |  | 25000.00 | 50000.00 | 15000.00 | 30000.00 | 65000.00 | 130000.00 | 65518.00 | 131036.00 | 64390.00 | 128780.00 | 30000.00 | SNOWMEX ENGINEERS LIMITED
6.03 | 15000 CFM | 2.00 | Job |  | 25000.00 | 50000.00 | 15000.00 | 30000.00 | 45000.00 | 90000.00 | 47794.00 | 95588.00 | 41100.00 | 82200.00 | 30000.00 | SNOWMEX ENGINEERS LIMITED
6.04 | 10000 CFM | 1.00 | Job |  | 25420.00 | 25420.00 | 15000.00 | 15000.00 | 45265.00 | 45265.00 | 35846.00 | 35846.00 | 27400.00 | 27400.00 | 15000.00 | SNOWMEX ENGINEERS LIMITED
7.00 | Supply, installation, balancing and commissioning of fabricated at site GSS sheet metal rectangular/round ducting complete with neoprene rubber gaskets, elbows, splitter dampers, vanes, hangers, supports etc. as per approved drawings and specifications of following sheet thickness complete as required.
7.01 | 24 G | 15.00 | Sqmtr. |  | 1000.00 | 15000.00 | 975.00 | 14625.00 | 880.00 | 13200.00 | 1301.00 | 19515.00 | 910.00 | 13650.00 | 13200.00 | Ingenious Industries
7.02 | 22 G | 20.00 | Sqmtr. |  | 1200.00 | 24000.00 | 1020.00 | 20400.00 | 975.00 | 19500.00 | 1484.00 | 29680.00 | 1050.00 | 21000.00 | 19500.00 | Ingenious Industries
7.03 | 20 G | 50.00 | Sqmtr. |  | 1600.00 | 80000.00 | 150.00 | 7500.00 | 1080.00 | 54000.00 | 1709.00 | 85450.00 | 1250.00 | 62500.00 | 7500.00 | SNOWMEX ENGINEERS LIMITED
7.04 | 18 G | 30.00 | Sqmtr. |  | 1800.00 | 54000.00 | 150.00 | 4500.00 | 1160.00 | 34800.00 | 2025.00 | 60750.00 | 1790.00 | 53700.00 | 4500.00 | SNOWMEX ENGINEERS LIMITED
8.00 | CANVASS CONNECTION:- Supply, fabrication, installation and testing of fire retarding flexible heavy canvas sleeve at least 10cm long securely bonded and bolted on both sides for AHUs, CAHUs,Fans etc. Quoted rates shall include the necessary mounting arrangement, flanges, nuts and bolts and treated-for-fire requisite length of canvass cloth. System shall be complete in accordance with AAI technical specifications. | 10.00 | Sqmtr. |  | 3500.00 | 35000.00 | 4500.00 | 45000.00 | 6500.00 | 65000.00 | 3050.00 | 30500.00 | 2040.00 | 20400.00 | 20400.00 | Mvac Engineers
9.00 | Duct Thermal Insulation:- Supply and installation of Closed Cell Nitrile rubber for duct thermal insulation of Supply & Return air duct. Nitrile rubber shall be Factory laminated black/Grey fiber Glass Cloth closed cell Elastomeric UV resistant. Thermal conductivity for the insulation material shall not exceed 0.038 W/mK at an average temperature of 25-30 Deg. C. Nitrile rubber shall be 40-60 Kg/m3. The material should comply to Class’O’ fire rating. The insulation material shall be non-combustible as per National Building Code 2016, Clause: 3.4.8.3.5 Part 4 Fire and Life Safety and should comply latest ECBC norms, fire rated for BS 476 Part 4 (Non –Combustible), BS 476 Part 5 (Ignitibility Test), Class 0 as per BS 476 Part 6: 1989 for fire propagation test and for Class 1 as per BS476 Part 7, 1987 for surface spread of flame test. The Material shall comply to BS 6853 / ISO 5659 / BS 6853 / ABD 0031 for smoke density and toxicity values. Line item shall be in compliance with AAI technical specifications.
9.01 | 19 mm | 50.00 | Sqmtr. |  | 750.00 | 37500.00 | 750.00 | 37500.00 | 672.00 | 33600.00 | 965.00 | 48250.00 | 840.00 | 42000.00 | 33600.00 | Ingenious Industries
9.02 | 13 mm | 50.00 | Sqmtr. |  | 850.00 | 42500.00 | 500.00 | 25000.00 | 600.00 | 30000.00 | 846.00 | 42300.00 | 720.00 | 36000.00 | 25000.00 | SNOWMEX ENGINEERS LIMITED
10.00 | Duct Accoustic Insulation :-Supply and installation of 15mm thick Open cell Nitrile rubber foam insulation duct acoustic lining of supply/ventilation air duct up to a distance of 5 m from AHU and Ventilation fan outlet with density 140-180 kg/m3 and material thermal conductivity not exceeding 0.047 W/mK. The material should confirm to class 1 rating for surface spread of flame. Insulation should have antimicrobial product protection, and should pass Fungi Resistance and Bacterial Resistance. The insulation should pass Air Erosion Resistance Test in accordance to ASTM Standard as specified and comliance to AAI technical specification. | 50.00 | Sqmtr. |  | 950.00 | 47500.00 | 1050.00 | 52500.00 | 950.00 | 47500.00 | 1355.00 | 67750.00 | 1040.00 | 52000.00 | 47500.00 | M/s. PRANAM HVAC ENGINEERING PVT. LTD., Ingenious Industries
11.00 | Supply, installation, testing and commissioning of Motorized fire & Smoke Damper having fire rating of 1.5 Hrs in accordance with latest edition of UL555 and shall be classified as Leakage Class 1 smoke damper in accordance with latest edition of UL555S. Each fire/smoke damper shall be AMCA licensed and bear the AMCA seal for air Performance. Actuators used shall be UL listed. Damper shall be of multi-leaf type and provided with Spring Return electrical actuator having its own thermal trip for ambient air temperature outside the duct and air temperature inside the duct. Actuator shall have Form fit type of mounting, metal enclosure and guaranteed long life span. The dampers shall meet the requirements of NFPA90A, 92A and 92B. Bigger size Dampers shall be supplied in Multiple modules of sizes not exceeding in dimensions of certified module, jack shafted together. Multiple actuators shall be provided for large dampers with higher torque requirements as prescribed in UL. Electric Actuator of suitable Torque and as approved by UL shall be factory mounted and tested. The actuator shall be suitable for 230V AC supply. In addition, actuator shall have elevated temperature rating of 350 deg.F. Fire retardant cables wherever required for satisfactory operation and control of the Damper. Fire/smoke damper shall be provided with factory fitted sleeves; however, access doors shall be provided in the ducts within AHU room. Dampers shall be spring return, motorized & failsafe type with indication for open/ close position. Damper operation shall be interlocked with the signal from fire alarm panel. Fire dampers shall be compatible with the existing fire detection system of building & shall be capable of operating automatically through an electric motor on receiving signal from fire alarm panel. Access door will be provided in the duct before each set of fire dampers. Potential free contact shall be provided by the vendor for closing of fire & smoke damper. On expiry of fire signal, fire & smoke dampers shall be opened manually through reset button. The System shall be complete in accordance with AAI technical specifications. | 10.00 | Sqmtr. |  | 30000.00 | 300000.00 | 17500.00 | 175000.00 | 18800.00 | 188000.00 | 34448.00 | 344480.00 | 51720.00 | 517200.00 | 175000.00 | SNOWMEX ENGINEERS LIMITED
12.00 | Supply, installation, testing and balancing of opposed blade volume control dampers shall be of Galvanised iron construction with louver dampers of robust construction and tightly fitted. The sheet thickness of blade shall be 0.8 mm and of the frame shall be 1.0 mm. Dampers shall be provided with suitable links, levers and quadrants as required for their proper operation; control or setting devices shall be made robust, easily operable and accessible through suitable access doors in the ducts. Volume control Damper (opposed bladed type with min. 18 gauge blades and 18 gauge casing of GSS) in the main branches. System shall be complete in accordance with AAI technical specifications. | 10.00 | Sqmtr. |  | 5250.00 | 52500.00 | 7650.00 | 76500.00 | 6600.00 | 66000.00 | 20204.00 | 202040.00 | 9470.00 | 94700.00 | 52500.00 | M/s. PRANAM HVAC ENGINEERING PVT. LTD.
13.00 | Supply and Installation of AHU room acoustic lining of walls and ceiling with 15mm thick open cell nitrile rubber foam insulation with density of 140-180 kg/m3 and material thermal conductivity not exceeding 0.05 W/mK. The material should confirm to class 1 rating for surface spread of flame. Insulating material have anti microbial and anti fungal properties as specified in technical specifications. | 1000.00 | Sqmtr. |  | 900.00 | 900000.00 | 1350.00 | 1350000.00 | 1075.00 | 1075000.00 | 1390.00 | 1390000.00 | 1050.00 | 1050000.00 | 900000.00 | M/s. PRANAM HVAC ENGINEERING PVT. LTD.
14.00 | Supplying, installation, testing & commissioning of intelligent addressable duct detector including suitable Photo detector complete with base and connection to existing Main fire alram Panel complete as required. | 6.00 | Each |  | 40000.00 | 240000.00 | 3250.00 | 19500.00 | 70000.00 | 420000.00 | 29632.00 | 177792.00 | 2160.00 | 12960.00 | 12960.00 | Mvac Engineers
15.00 | Supplying & laying of 2x1.5 sqmm fire survival armoured cable, 600/1000V rated with annealed copper conductor having glass mica fire barrier tape covered by an extruded layer of cross linkable ethylene propylene rubber (EPR) insulation and LSZH inner bedding, steel wire armouring & LSZH outer sheath complete as required. | 1000.00 | Meter |  | 265.00 | 265000.00 | 185.00 | 185000.00 | 235.00 | 235000.00 | 852.56 | 852561.00 | 180.00 | 180000.00 | 180000.00 | Mvac Engineers
| Total in Figures |  |  |  |  | 10009120.00 |  | 7238963.00 |  | 9891455.00 |  | 11302200.00 |  | 8159160.00
Lowest Amount Quoted BY: SNOWMEX ENGINEERS LIMITED(7238963.00)

## BOQ Summary
BOQ Summary Details Tender Title: Replacement of AHU, Valves and modification of piping in Terminal Building at Surat International Airport, Surat. Tender ID: 2025_AAI_250993_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | SNOWMEX ENGINEERS LIMITED (BID ID -920172) | 7238963.00 | L1
| 2 | Mvac Engineers (BID ID -921125) | 8159160.00 | L2
| 3 | Ingenious Industries (BID ID -921232) | 9891455.00 | L3
| 4 | M/s. PRANAM HVAC ENGINEERING PVT. LTD. (BID ID -916113) | 10009120.00 | L4
| 5 | AirBizz AirConditioning Pvt. Ltd. (BID ID -913231) | 11302200.00 | L5