## BoQ1
Government eProcurement System Created By: Jyoti Prakash chauhan Created Date/Time: 13-Nov-2025 06:11 PM Tender Title: Augmentation of power supply system, substation and allied work at CATC, Prayagraj. SH- Replacement of existing LT Panels of Institute block and allied works Tender ID: 2025_AAI_251184_1
Tender Inviting Authority: Asstt. General Manager (Engg.-Electrical), AAI, CATC, Prayagraj
Name of Work: Augmentation of power supply system, substation and allied work at CATC, Prayagraj. SH: Replacement of existing LT Panels of Institute block and allied works.
Contract No:
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | ECS ENGINEERING PVT LTD (GSTN-09AABCE5944P1Z1) BID ID -919860 |  | Genesis (GSTN-09AGAPJ4118N1ZA) BID ID -919898 |  | Industrial Traders (GSTN-09ACJPC1773F1ZQ) BID ID -922435 |  | Awasthi Electric Works (GSTN-09ABAPA1866D1Z5) BID ID -922477 |  | M/S RAHUL ENGINEERS (GSTN-NA) BID ID -922669 |  | Shiva Enterprises (GSTN-NA) BID ID -921914 |  | Krishsons International Engineers And Consultants (I) Pvt. Ltd (GSTN-NA) BID ID -922552 |  | Virtus Techno (GSTN-NA) BID ID -922368 |  | girnar electricals (GSTN-NA) BID ID -922615
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Design, manufacture, supply, installation, testing and commissioning of Indoor type LT Panel, as per IEC 61439, cubicle & modular type, made of 2 mm thick electro galvanized steel/CRCA sheets for frame work and covers, 3mm thick for gland plates, totally enclosed, IP 54, free standing, floor mounting, dust and vermin proof, compartmentalized, including cleaning & finishing complete with all process, powder coated, painting, complete with handle and gasket, suitable for operation on 3 Phase and neutral, 415V, 50 Hz AC system with Al. bus bars, fabrication shall be done in transportation sections, entire panel shall have a common earth bar of suitable size at the rear with 2 nos. earth stud, control wiring with FRLS PVC insulated copper conductor, cable allays, cable gland plates in two half, interconnections including supply & installation of following items and as per detailed technical specification. |  |  | 1.00
2.00 | INCOMINGS |  |  | 1.00
3.00 | 250 A, FP, 36 KA, MCCB with thermal magnetic based release having adjustable over load and adjustable short circuit with rotary operating mechanism and spreader terminals-01 No. |  |  | 1.00
4.00 | METERING |  |  | 1.00
5.00 | 96 mm square flush pattern digital Voltmeter (0-500 V), accuracy class 1, suitable range for 3 phase, 4 wire operation with LED display and built-in selector switch along with 3 nos. of 2 Amp SP MCBs.- 1 set |  |  | 1.00
6.00 | 96 mm sq. Flush pattern Digital Type Ammeter of suitable range to measure 0-500A, for 3 phase 4 wire operation with LED display and built-in selector switch with 3 numbers of class 1.0 accuracy, 15 VA burden & suitable range CTs.- 1 set. |  |  | 1.00
7.00 | 1 Set of Indication Lamps, LED type, R, Y, B each with 2 Amp. SP MCB for protection. |  |  | 1.00
8.00 | BUS BAR |  |  | 1.00
9.00 | 1 set of high conductivity Aluminium electrolytic grade, bus bars of minimum 300 Amps capacity, TPN with heat shrinkable colored sleeves and non-combustible, non-hygroscopic, high strength SMC/ DMC/Polymer material bus bars supports at required intervals. |  |  | 1.00
10.00 | OUTGOINGS |  |  | 1.00
11.00 | 100A, FP, 18 KA, MCCB with thermal magnetic based release having adjustable over load and adjustable short circuit with rotary operating mechanism and spreader terminals and ON/OFF LED Indication lamp-2 Nos. |  |  | 1.00
12.00 | 63A, FP, 18 KA, MCCB with thermal magnetic based release having adjustable over load and adjustable short circuit with rotary operating mechanism and spreader terminals and ON/OFF LED Indication lamp-8 Nos. |  |  | 1.00
13.00 | Note- All MCCBs should have (i) Ics = Icu at 415 V (ii) Rotary operating mechanism and terminal extension / spreaders (iii) ON/OFF Indication (iv) All MCCBs shall be current limiting type. | 1.00 | Job | 10.00 | 200000.00 | 200000.00 | 245106.00 | 245106.00 | 410315.17 | 410315.17 | 300000.00 | 300000.00 | 190000.00 | 190000.00 | 267000.00 | 267000.00 | 204000.00 | 204000.00 | 271986.00 | 271986.00 | 287000.00 | 287000.00 | 190000.00 | M/S RAHUL ENGINEERS
14.00 | Design, manufacture, supply, installation, testing and commissioning of Indoor type LT Panel, as per IEC 61439, cubicle & modular type, made of 2 mm thick electro galvanized steel/CRCA sheets for frame work and covers, 3mm thick for gland plates, totally enclosed, IP 54, free standing, floor mounting, dust and vermin proof, compartmentalized, including cleaning & finishing complete with all process, powder coated, painting, complete with handle and gasket, suitable for operation on 3 Phase and neutral, 415V, 50 Hz AC system with Al. bus bars, fabrication shall be done in transportation sections, entire panel shall have a common earth bar of suitable size at the rear with 2 nos. earth stud, control wiring with FRLS PVC insulated copper conductor, cable allays, cable gland plates in two half, interconnections including supply & installation of following items and as per detailed technical specification.
15.00 | INCOMINGS
16.00 | 250 A, FP, 36 KA, MCCB with thermal magnetic based release having adjustable over load and adjustable short circuit with rotary operating mechanism and spreader terminals-01 No.
17.00 | METERING
18.00 | 96 mm square flush pattern digital Voltmeter (0-500 V), accuracy class 1, suitable range for 3 phase, 4 wire operation with LED display and built-in selector switch along with 3 nos. of 2 Amp SP MCBs.- 1 set
19.00 | 96 mm sq. Flush pattern Digital Type Ammeter of suitable range to measure 0-500A, for 3 phase 4 wire operation with LED display and built-in selector switch with 3 numbers of class 1.0 accuracy, 15 VA burden & suitable range CTs.- 1 set.
20.00 | 1 Set of Indication Lamps, LED type, R, Y, B each with 2 Amp. SP MCB for protection.
21.00 | BUS BAR
22.00 | 1 set of high conductivity Aluminium electrolytic grade, bus bars of minimum 300 Amps capacity, TPN with heat shrinkable colored sleeves and non-combustible, non-hygroscopic, high strength SMC/ DMC/Polymer material bus bars supports at required intervals.
23.00 | OUTGOINGS
24.00 | 63A, FP, 18 KA, MCCB with thermal magnetic based release having adjustable over load and adjustable short circuit with rotary operating mechanism and spreader terminals and ON/OFF LED Indication lamp-6 Nos.
25.00 | Note- All MCCBs should have (i) Ics = Icu at 415 V (ii) Rotary operating mechanism and terminal extension / spreaders (iii) ON/OFF Indication (iv) All MCCBs shall be current limiting type. | 3.00 | Job | 10.00 | 150000.00 | 450000.00 | 199657.50 | 598972.50 | 246336.59 | 739009.77 | 190500.00 | 571500.00 | 190000.00 | 570000.00 | 200000.00 | 600000.00 | 143000.00 | 429000.00 | 139535.00 | 418605.00 | 217000.00 | 651000.00 | 418605.00 | Virtus Techno
26.00 | Design, manufacture, supply, installation, testing and commissioning of Indoor type LT Panel, as per IEC 61439, cubicle & modular type, made of 2 mm thick electro galvanized steel/CRCA sheets for frame work and covers, 3mm thick for gland plates, totally enclosed, IP 54, free standing, floor mounting, dust and vermin proof, compartmentalized, including cleaning & finishing complete with all process, powder coated, painting, complete with handle and gasket, suitable for operation on 3 Phase and neutral, 415V, 50 Hz AC system with Al. bus bars, fabrication shall be done in transportation sections, entire panel shall have a common earth bar of suitable size at the rear with 2 nos. earth stud, control wiring with FRLS PVC insulated copper conductor, cable allays, cable gland plates in two half, interconnections including supply & installation of following items and as per detailed technical specification.
27.00 | INCOMING
28.00 | 250 A, FP, 36 KA, MCCB with thermal magnetic based release having adjustable over load and adjustable short circuit with rotary operating mechanism and spreader terminals-01 No.
29.00 | METERING
30.00 | 96 mm square flush pattern digital Voltmeter (0-500 V), accuracy class 1, suitable range for 3 phase, 4 wire operation with LED display and built-in selector switch along with 3 nos. of 2 Amp SP MCBs.- 1 set
31.00 | 96 mm sq. Flush pattern Digital Type Ammeter of suitable range to measure 0-500A, for 3 phase 4 wire operation with LED display and built-in selector switch with 3 numbers of class 1.0 accuracy, 15 VA burden & suitable range CTs.- 1 set.
32.00 | 1 Set of Indication Lamps, LED type, R, Y, B each with 2 Amp. SP MCB for protection.
33.00 | BUS BAR
34.00 | 1 set of high conductivity Aluminium electrolytic grade, bus bars of minimum 300 Amps capacity, TPN with heat shrinkable colored sleeves and non-combustible, non-hygroscopic, high strength SMC/ DMC/Polymer material bus bars supports at required intervals.
35.00 | OUTGOINGS
36.00 | 100A, FP, 18 KA, MCCB with thermal magnetic based release having adjustable over load and adjustable short circuit with rotary operating mechanism and spreader terminals and ON/OFF LED Indication lamp-2 Nos.
37.00 | 63A, FP, 18 KA, MCCB with thermal magnetic based release having adjustable over load and adjustable short circuit with rotary operating mechanism and spreader terminals and ON/OFF LED Indication lamp-5 Nos.
38.00 | Note- All MCCBs should have (i) Ics = Icu at 415 V (ii) Rotary operating mechanism and terminal extension / spreaders (iii) ON/OFF Indication (iv) All MCCBs shall be current limiting type. | 2.00 | Job | 10.00 | 168100.00 | 336200.00 | 207843.70 | 415687.40 | 281072.88 | 562145.76 | 204000.00 | 408000.00 | 190000.00 | 380000.00 | 212000.00 | 424000.00 | 176000.00 | 352000.00 | 204842.00 | 409684.00 | 245000.00 | 490000.00 | 336200.00 | ECS ENGINEERING PVT LTD
39.00 | Design, manufacture, supply, installation, testing and commissioning of Indoor type LT Panel, as per IEC 61439, cubicle & modular type, made of 2 mm thick electro galvanized steel/CRCA sheets for frame work and covers, 3mm thick for gland plates, totally enclosed, IP 54, free standing, floor mounting, dust and vermin proof, compartmentalized, including cleaning & finishing complete with all process, powder coated, painting, complete with handle and gasket, suitable for operation on 3 Phase and neutral, 415V, 50 Hz AC system with Al. bus bars, fabrication shall be done in transportation sections, entire panel shall have a common earth bar of suitable size at the rear with 2 nos. earth stud, control wiring with FRLS PVC insulated copper conductor, cable allays, cable gland plates in two half, interconnections including supply & installation of following items and as per detailed technical specification.
40.00 | INCOMINGS
41.00 | 250 A, FP, 36 KA, MCCB with thermal magnetic based release having adjustable over load and adjustable short circuit with rotary operating mechanism and spreader terminals-01 No.
42.00 | METERING
43.00 | 96 mm square flush pattern digital Voltmeter (0-500 V), accuracy class 1, suitable range for 3 phase, 4 wire operation with LED display and built-in selector switch along with 3 nos. of 2 Amp SP MCBs.- 1 set
44.00 | 96 mm sq. Flush pattern Digital Type Ammeter of suitable range to measure 0-500A, for 3 phase 4 wire operation with LED display and built-in selector switch with 3 numbers of class 1.0 accuracy, 15 VA burden & suitable range CTs.- 1 set.
45.00 | 1 Set of Indication Lamps, LED type, R, Y, B each with 2 Amp. SP MCB for protection.
46.00 | BUS BAR
47.00 | 1 set of high conductivity Aluminium electrolytic grade, bus bars of minimum 300 Amps capacity, TPN with heat shrinkable colored sleeves and non-combustible, non-hygroscopic, high strength SMC/ DMC/Polymer material bus bars supports at required intervals.
48.00 | OUTGOINGS
49.00 | 100A, FP, 18 KA, MCCB with thermal magnetic based release having adjustable over load and adjustable short circuit with rotary operating mechanism and spreader terminals and ON/OFF LED Indication lamp-2 Nos.
50.00 | 63A, FP, 18 KA, MCCB with thermal magnetic based release having adjustable over load and adjustable short circuit with rotary operating mechanism and spreader terminals and ON/OFF LED Indication lamp-8 Nos.
51.00 | Note- All MCCBs should have (i) Ics = Icu at 415 V (ii) Rotary operating mechanism and terminal extension / spreaders (iii) ON/OFF Indication (iv) All MCCBs shall be current limiting type. | 1.00 | Job | 10.00 | 200000.00 | 200000.00 | 244245.30 | 244245.30 | 435348.59 | 435348.59 | 235000.00 | 235000.00 | 190000.00 | 190000.00 | 268000.00 | 268000.00 | 208000.00 | 208000.00 | 266486.00 | 266486.00 | 285000.00 | 285000.00 | 190000.00 | M/S RAHUL ENGINEERS
52.00 | Design, manufacture, supply, installation, testing and commissioning of Indoor type LT Panel, as per IEC 61439, cubicle & modular type, made of 2 mm thick electro galvanized steel/CRCA sheets for frame work and covers, 3mm thick for gland plates, totally enclosed, IP 54, free standing, floor mounting, dust and vermin proof, compartmentalized, including cleaning & finishing complete with all process, powder coated, painting, complete with handle and gasket, suitable for operation on 3 Phase and neutral, 415V, 50 Hz AC system with Al. bus bars, fabrication shall be done in transportation sections, entire panel shall have a common earth bar of suitable size at the rear with 2 nos. earth stud, control wiring with FRLS PVC insulated copper conductor, cable allays, cable gland plates in two half, interconnections including supply & installation of following items and as per detailed technical specification.
53.00 | INCOMINGS
54.00 | 250 A, FP, 36 KA, MCCB with thermal magnetic based release having adjustable over load and adjustable short circuit with rotary operating mechanism and spreader terminals-01 No.
55.00 | METERING
56.00 | 96 mm square flush pattern digital Voltmeter (0-500 V), accuracy class 1, suitable range for 3 phase, 4 wire operation with LED display and built-in selector switch along with 3 nos. of 2 Amp SP MCBs.- 1 set
57.00 | 96 mm sq. Flush pattern Digital Type Ammeter of suitable range to measure 0-500A, for 3 phase 4 wire operation with LED display and built-in selector switch with 3 numbers of class 1.0 accuracy, 15 VA burden & suitable range CTs.- 1 set.
58.00 | 1 Set of Indication Lamps, LED type, R, Y, B each with 2 Amp. SP MCB for protection.
59.00 | BUS BAR
60.00 | 1 set of high conductivity Aluminium electrolytic grade, bus bars of minimum 300 Amps capacity, TPN with heat shrinkable colored sleeves and non-combustible, non-hygroscopic, high strength SMC/ DMC/Polymer material bus bars supports at required intervals.
61.00 | OUTGOINGS
62.00 | 63A, FP, 18 KA, MCCB with thermal magnetic based release having adjustable over load and adjustable short circuit with rotary operating mechanism and spreader terminals and ON/OFF LED Indication lamp-7 Nos.
63.00 | Note- All MCCBs should have (i) Ics = Icu at 415 V (ii) Rotary operating mechanism and terminal extension / spreaders (iii) ON/OFF Indication (iv) All MCCBs shall be current limiting type. | 1.00 | Job | 10.00 | 162000.00 | 162000.00 | 214981.00 | 214981.00 | 281072.88 | 281072.88 | 205000.00 | 205000.00 | 150000.00 | 150000.00 | 212000.00 | 212000.00 | 169000.00 | 169000.00 | 200717.00 | 200717.00 | 247000.00 | 247000.00 | 150000.00 | M/S RAHUL ENGINEERS
64.00 | Design, manufacture, supply, installation, testing and commissioning of Indoor type LT Panel, as per IEC 61439, cubicle & modular type, made of 2 mm thick electro galvanized steel/CRCA sheets for frame work and covers, 3mm thick for gland plates, totally enclosed, IP 54, free standing, floor mounting, dust and vermin proof, compartmentalized, including cleaning & finishing complete with all process, powder coated, painting, complete with handle and gasket, suitable for operation on 3 Phase and neutral, 415V, 50 Hz AC system with Al. bus bars, fabrication shall be done in transportation sections, entire panel shall have a common earth bar of suitable size at the rear with 2 nos. earth stud, control wiring with FRLS PVC insulated copper conductor, cable allays, cable gland plates in two half, interconnections including supply & installation of following items and as per detailed technical specification.
65.00 | INCOMINGS
66.00 | 400 A, FP, Ics=Icu=36 kA, MCCB with Microprocessor based release having adjustable over load and adjustable short circuit with rotary operating mechanism and spreader terminals-02 Nos.
67.00 | BUS COUPLER
68.00 | 1 Nos. of 400 A, TP, Ics=Icu=36 kA, MCCB with Microprocessor based release having adjustable over load and adjustable short circuit with rotary operating mechanism and spreader terminals.
69.00 | METERING
70.00 | 96 mm square flush pattern digital Voltmeter (0-500 V), accuracy class 1, suitable range for 3 phase, 4 wire operation with LED display and built-in selector switch along with 3 nos. of 2 Amp SP MCBs.- 2 set
71.00 | 96 mm sq. Flush pattern Digital Type Ammeter of suitable range to measure 0-500A, for 3 phase 4 wire operation with LED display and built-in selector switch with 3 numbers of class 1.0 accuracy, 15 VA burden & suitable range CTs.- 2 set.
72.00 | 3 Set of Indication Lamps, LED type, R, Y, B each with 2 Amp. SP MCB for protection.
73.00 | BUS BAR
74.00 | 1 set of high conductivity Aluminium electrolytic grade, bus bars of minimum 500 Amps capacity, TPN with heat shrinkable colored sleeves and non-combustible, non-hygroscopic, high strength SMC/ DMC/Polymer material bus bars supports at required intervals.
75.00 | ACCESSORIES FOR ELECTRICAL & MECHANICAL INTERLOCKING
76.00 | Electrical & mechanical interlocking arrangement as per specifications among 2 nos. Incomers and 1 no. Bus Coupler including interconnections etc. as required.
77.00 | OUTGOINGS
78.00 | 100A, FP, 25 KA, MCCB with thermal magnetic based release having adjustable over load and adjustable short circuit with rotary operating mechanism and spreader terminals and ON/OFF LED Indication lamp-3 Nos.
79.00 | 63A, FP, 18 KA, MCCB with thermal magnetic based release having adjustable over load and adjustable short circuit with rotary operating mechanism and spreader terminals and ON/OFF LED Indication lamp-14 Nos.
80.00 | Note- All MCCBs should have (i) Ics = Icu at 415 V (ii) Rotary operating mechanism and terminal extension / spreaders (iii) ON/OFF Indication (iv) All MCCBs shall be current limiting type. | 3.00 | Job | 10.00 | 500000.00 | 1500000.00 | 426381.00 | 1279143.00 | 650247.87 | 1950743.61 | 542500.00 | 1627500.00 | 500000.00 | 1500000.00 | 590000.00 | 1770000.00 | 474000.00 | 1422000.00 | 621830.00 | 1865490.00 | 721000.00 | 2163000.00 | 1279143.00 | Genesis
81.00 | Design, manufacture, supply, installation, testing and commissioning of Indoor type LT Panel, as per IEC 61439, cubicle & modular type, made of 2 mm thick electro galvanized steel/CRCA sheets for frame work and covers, 3mm thick for gland plates, totally enclosed, IP 54, free standing, floor mounting, dust and vermin proof, compartmentalized, including cleaning & finishing complete with all process, powder coated, painting, complete with handle and gasket, suitable for operation on 3 Phase and neutral, 415V, 50 Hz AC system with Al. bus bars, fabrication shall be done in transportation sections, entire panel shall have a common earth bar of suitable size at the rear with 2 nos. earth stud, control wiring with FRLS PVC insulated copper conductor, cable allays, cable gland plates in two half, interconnections including supply & installation of following items and as per detailed technical specification.
82.00 | INCOMINGS
83.00 | 250 A, FP, 36 KA, MCCB with thermal magnetic based release having adjustable over load and adjustable short circuit with rotary operating mechanism and spreader terminals-01 No.
84.00 | METERING
85.00 | 96 mm square flush pattern digital Voltmeter (0-500 V), accuracy class 1, suitable range for 3 phase, 4 wire operation with LED display and built-in selector switch along with 3 nos. of 2 Amp SP MCBs.- 1 set
86.00 | 96 mm sq. Flush pattern Digital Type Ammeter of suitable range to measure 0-500A, for 3 phase 4 wire operation with LED display and built-in selector switch with 3 numbers of class 1.0 accuracy, 15 VA burden & suitable range CTs.- 1 set.
87.00 | 1 Set of Indication Lamps, LED type, R, Y, B each with 2 Amp. SP MCB for protection.
88.00 | BUS BAR
89.00 | 1 set of high conductivity Aluminium electrolytic grade, bus bars of minimum 300 Amps capacity, TPN with heat shrinkable colored sleeves and non-combustible, non-hygroscopic, high strength SMC/ DMC/Polymer material bus bars supports at required intervals.
90.00 | OUTGOINGS
91.00 | 63A, FP, 18 KA, MCCB with thermal magnetic based release having adjustable over load and adjustable short circuit with rotary operating mechanism and spreader terminals and ON/OFF LED Indication lamp-5 Nos.
92.00 | 63A, FP, 18 KA, MCCB with thermal magnetic based release having adjustable over load and adjustable short circuit with rotary operating mechanism and spreader terminals and ON/OFF LED Indication lamp including Start Delta starter- 3 Nos. and DOL Starter-2 Nos. with over load relay, single phase preventer, ON/OFF indicating lighting with ON/OFF push buttons suitable for 15/20 HP mono block pump motor sets.-5 Sets.
93.00 | Note- All MCCBs should have (i) Ics = Icu at 415 V (ii) Rotary operating mechanism and terminal extension / spreaders (iii) ON/OFF Indication (iv) All MCCBs shall be current limiting type. | 1.00 | Job | 10.00 | 430000.00 | 430000.00 | 380000.00 | 380000.00 | 399021.03 | 399021.03 | 418000.00 | 418000.00 | 190000.00 | 190000.00 | 370000.00 | 370000.00 | 399000.00 | 399000.00 | 326975.00 | 326975.00 | 331000.00 | 331000.00 | 190000.00 | M/S RAHUL ENGINEERS
94.00 | Design, manufacture, supply, installation, testing and commissioning of Indoor type LT Panel, as per IEC 61439, cubicle & modular type, made of 2 mm thick electro galvanized steel/CRCA sheets for frame work and covers, 3mm thick for gland plates, totally enclosed, IP 54, free standing, floor mounting, dust and vermin proof, compartmentalized, including cleaning & finishing complete with all process, powder coated, painting, complete with handle and gasket, suitable for operation on 3 Phase and neutral, 415V, 50 Hz AC system with Al. bus bars, fabrication shall be done in transportation sections, entire panel shall have a common earth bar of suitable size at the rear with 2 nos. earth stud, control wiring with FRLS PVC insulated copper conductor, cable allays, cable gland plates in two half, interconnections including supply & installation of following items and as per detailed technical specification.
95.00 | INCOMINGS
96.00 | 400 A, FP, Ics=Icu=36 kA, MCCB with Microprocessor based release having adjustable over load and adjustable short circuit with rotary operating mechanism and spreader terminals-01 No.
97.00 | METERING
98.00 | 96 mm square flush pattern digital Voltmeter (0-500 V), accuracy class 1, suitable range for 3 phase, 4 wire operation with LED display and built-in selector switch along with 3 nos. of 2 Amp SP MCBs.- 1 set
99.00 | 96 mm sq. Flush pattern Digital Type Ammeter of suitable range to measure 0-500A, for 3 phase 4 wire operation with LED display and built-in selector switch with 3 numbers of class 1.0 accuracy, 15 VA burden & suitable range CTs.- 1 set.
100.00 | 1 Set of Indication Lamps, LED type, R, Y, B each with 2 Amp. SP MCB for protection.
101.00 | BUS BAR
102.00 | 1 set of high conductivity Aluminium electrolytic grade, bus bars of minimum 500 Amps capacity, TPN with heat shrinkable colored sleeves and non-combustible, non-hygroscopic, high strength SMC/ DMC/Polymer material bus bars supports at required intervals.
103.00 | OUTGOINGS
104.00 | 200A, FP, 36 KA, MCCB with thermal magnetic based release having adjustable over load and adjustable short circuit with rotary operating mechanism and spreader terminals and ON/OFF LED Indication lamp-1 Nos.
105.00 | 100A, FP, 25 KA, MCCB with thermal magnetic based release having adjustable over load and adjustable short circuit with rotary operating mechanism and spreader terminals and ON/OFF LED Indication lamp-4 Nos.
106.00 | Note- All MCCBs should have (i) Ics = Icu at 415 V (ii) Rotary operating mechanism and terminal extension / spreaders (iii) ON/OFF Indication (iv) All MCCBs shall be current limiting type. | 1.00 | Job | 10.00 | 191000.00 | 191000.00 | 231915.50 | 231915.50 | 290038.33 | 290038.33 | 251000.00 | 251000.00 | 190000.00 | 190000.00 | 232000.00 | 232000.00 | 202000.00 | 202000.00 | 235642.00 | 235642.00 | 268000.00 | 268000.00 | 190000.00 | M/S RAHUL ENGINEERS
107.00 | Design, Supply, installation, testing & commissioning of L.T. outdoor double door Feeder Panel made of 2 mm thick electro galvanized steel/CRCA sheets for frame work and covers, 3mm thick for gland plates, totally enclosed, IP 55, free standing, floor mounting, dust and vermin proof, indoor, compartmentalised, including cleaning & finishing completewith all process, powder coated, painting, with PU gasket complete with handle and gasket, suitable for operation on 3 Phase and neutral, 415V, 50 Hz AC system with Al. busbars extensible on both sides, fabrication shall be done in transportation sections, entire panel shall have a common earth bar of suitable size at the rear with 2 nos. earth stud, control wiring with FRLS. PVC insulated copper conductor, cable allays, cable gland plates in two half, interconnections including supply & installation of following items and as per detailed technical specification enclosed.
108.00 | INCOMINGS
109.00 | 100 A, FP, 18 KA, MCCB with thermal magnetic based release having adjustable over load and adjustable short circuit with rotary operating mechanism and spreader terminals-01 No.
110.00 | METERING
111.00 | 96 mm square flush pattern digital Voltmeter (0-500 V), accuracy class 1, suitable range for 3 phase, 4 wire operation with LED display and built-in selector switch along with 3 nos. of 2 Amp SP MCBs.- 1 set
112.00 | 96 mm sq. Flush pattern Digital Type Ammeter of suitable range to measure 0-500A, for 3 phase 4 wire operation with LED display and built-in selector switch with 3 numbers of class 1.0 accuracy, 15 VA burden & suitable range CTs.- 1 set.
113.00 | 1 Set of Indication Lamps, LED type, R, Y, B each with 2 Amp. SP MCB for protection.
114.00 | BUS BAR
115.00 | 1 set of high conductivity Aluminium electrolytic grade, bus bars of minimum 150 Amps capacity, TPN with heat shrinkable colored sleeves and non-combustible, non-hygroscopic, high strength SMC/ DMC/Polymer material bus bars supports at required intervals.
116.00 | OUTGOINGS
117.00 | 63A, FP, 18 KA, MCCB with thermal magnetic based release having adjustable over load and adjustable short circuit with rotary operating mechanism and spreader terminals and ON/OFF LED Indication lamp including Start Delta starter with over load relay, single phase preventer, ON/OFF indicating lighting with ON/OFF push buttons suitable for 15/20 HP mono block pump motor sets.-2 Sets.
118.00 | 32A, FP, 18 KA, MCCB with thermal magnetic based release having adjustable over load and adjustable short circuit with rotary operating mechanism and spreader terminals and ON/OFF LED Indication lamps.-1 Nos.
119.00 | Note- All MCCBs should have (i) Ics = Icu at 415 V (ii) Rotary operating mechanism and terminal extension / spreaders (iii) ON/OFF Indication (iv) All MCCBs shall be current limiting type. | 2.00 | Job | 10.00 | 139700.00 | 279400.00 | 209288.10 | 418576.20 | 126855.38 | 253710.76 | 185000.00 | 370000.00 | 190000.00 | 380000.00 | 160000.00 | 320000.00 | 145000.00 | 290000.00 | 180862.00 | 361724.00 | 173000.00 | 346000.00 | 253710.76 | Industrial Traders
120.00 | Design, manufacture, supply, installation, testing and commissioning of Indoor type LT Panel, as per IEC 61439, cubicle & modular type, made of 2 mm thick electro galvanized steel/CRCA sheets for frame work and covers, 3mm thick for gland plates, totally enclosed, IP 54, free standing, floor mounting, dust and vermin proof, compartmentalized, including cleaning & finishing complete with all process, powder coated, painting, complete with handle and gasket, suitable for operation on 3 Phase and neutral, 415V, 50 Hz AC system with Al. bus bars, fabrication shall be done in transportation sections, entire panel shall have a common earth bar of suitable size at the rear with 2 nos. earth stud, control wiring with FRLS PVC insulated copper conductor, cable allays, cable gland plates in two half, interconnections including supply & installation of following items and as per detailed technical specification.
121.00 | INCOMINGS
122.00 | 400 A, FP, Ics=Icu=36 kA, MCCB with Microprocessor based release having adjustable over load and adjustable short circuit. with rotary operating mechanism and spreader terminals-01 No.
123.00 | METERING
124.00 | 96 mm square flush pattern digital Voltmeter (0-500 V), accuracy class 1, suitable range for 3 phase, 4 wire operation with LED display and built-in selector switch along with 3 nos. of 2 Amp SP MCBs.- 1 set
125.00 | 96 mm sq. Flush pattern Digital Type Ammeter of suitable range to measure 0-500A, for 3 phase 4 wire operation with LED display and built-in selector switch with 3 numbers of class 1.0 accuracy, 15 VA burden & suitable range CTs.- 1 set.
126.00 | 1 Set of Indication Lamps, LED type, R, Y, B each with 2 Amp. SP MCB for protection.
127.00 | BUS BAR
128.00 | 1 set of high conductivity Aluminium electrolytic grade, bus bars of minimum 500 Amps capacity, TPN with heat shrinkable colored sleeves and non-combustible, non-hygroscopic, high strength SMC/ DMC/Polymer material bus bars supports at required intervals.
129.00 | OUTGOINGS
130.00 | 315 A, FP, Ics=Icu=36 kA, MCCB with Microprocessor based release having adjustable over load and adjustable short circuit with rotary operating mechanism and spreader terminals-01 No.
131.00 | 125A, FP, 18 KA, MCCB with thermal magnetic based release having adjustable over load and adjustable short circuit with rotary operating mechanism and spreader terminals and ON/OFF LED Indication lamp-2 Nos.
132.00 | 63A, FP, 18 KA, MCCB with thermal magnetic based release having adjustable over load and adjustable short circuit with rotary operating mechanism and spreader terminals and ON/OFF LED Indication lamp-4 Nos.
133.00 | Note- All MCCBs should have (i) Ics = Icu at 415 V (ii) Rotary operating mechanism and terminal extension / spreaders (iii) ON/OFF Indication (iv) All MCCBs shall be current limiting type. | 1.00 | Job | 10.00 | 251000.00 | 251000.00 | 257474.75 | 257474.75 | 483203.17 | 483203.17 | 201000.00 | 201000.00 | 190000.00 | 190000.00 | 325000.00 | 325000.00 | 147000.00 | 147000.00 | 319737.00 | 319737.00 | 282000.00 | 282000.00 | 147000.00 | Krishsons International Engineers And Consultants (I) Pvt. Ltd
134.00 | Design, manufacture, supply, installation, testing and commissioning of Indoor type LT Panel, as per IEC 61439, cubicle & modular type, made of 2 mm thick electro galvanized steel/CRCA sheets for frame work and covers, 3mm thick for gland plates, totally enclosed, IP 54, free standing, floor mounting, dust and vermin proof, compartmentalized, including cleaning & finishing complete with all process, powder coated, painting, complete with handle and gasket, suitable for operation on 3 Phase and neutral, 415V, 50 Hz AC system with Al. bus bars, fabrication shall be done in transportation sections, entire panel shall have a common earth bar of suitable size at the rear with 2 nos. earth stud, control wiring with FRLS PVC insulated copper conductor, cable allays, cable gland plates in two half, interconnections including supply & installation of following items and as per detailed technical specification.
135.00 | INCOMINGS
136.00 | 200A, FP, 18 KA, MCCB with thermal magnetic based release having adjustable over load and adjustable short circuit with rotary operating mechanism and spreader terminals and ON/OFF LED Indication lamp-1 Nos.
137.00 | METERING
138.00 | 96 mm square flush pattern digital Voltmeter (0-500 V), accuracy class 1, suitable range for 3 phase, 4 wire operation with LED display and built-in selector switch along with 3 nos. of 2 Amp SP MCBs.- 1 set
139.00 | 96 mm sq. Flush pattern Digital Type Ammeter of suitable range to measure 0-500A, for 3 phase 4 wire operation with LED display and built-in selector switch with 3 numbers of class 1.0 accuracy, 15 VA burden & suitable range CTs.- 1 set.
140.00 | 1 Set of Indication Lamps, LED type, R, Y, B each with 2 Amp. SP MCB for protection.
141.00 | BUS BAR
142.00 | 1 set of high conductivity Aluminium electrolytic grade, bus bars of minimum 250 Amps capacity, TPN with heat shrinkable colored sleeves and non-combustible, non-hygroscopic, high strength SMC/ DMC/Polymer material bus bars supports at required intervals.
143.00 | OUTGOINGS
144.00 | 100A, FP, 18 KA, MCCB with thermal magnetic based release having adjustable over load and adjustable short circuit with rotary operating mechanism and spreader terminals and ON/OFF LED Indication lamp-1 Nos.
145.00 | 63A, FP, 18 KA, MCCB with thermal magnetic based release having adjustable over load and adjustable short circuit with rotary operating mechanism and spreader terminals and ON/OFF LED Indication lamp-4 Nos.
146.00 | Note- All MCCBs should have (i) Ics = Icu at 415 V (ii) Rotary operating mechanism and terminal extension / spreaders (iii) ON/OFF Indication (iv) All MCCBs shall be current limiting type. | 1.00 | Job | 10.00 | 119000.00 | 119000.00 | 190881.00 | 190881.00 | 257785.98 | 257785.98 | 148000.00 | 148000.00 | 190000.00 | 190000.00 | 205000.00 | 205000.00 | 120000.00 | 120000.00 | 152218.00 | 152218.00 | 198000.00 | 198000.00 | 119000.00 | ECS ENGINEERING PVT LTD
147.00 | Design, manufacture, supply, installation, testing and commissioning of Indoor type LT Panel, as per IEC 61439, cubicle & modular type, made of 2 mm thick electro galvanized steel/CRCA sheets for frame work and covers, 3mm thick for gland plates, totally enclosed, IP 54, free standing, floor mounting, dust and vermin proof, compartmentalized, including cleaning & finishing complete with all process, powder coated, painting, complete with handle and gasket, suitable for operation on 3 Phase and neutral, 415V, 50 Hz AC system with Al. bus bars, fabrication shall be done in transportation sections, entire panel shall have a common earth bar of suitable size at the rear with 2 nos. earth stud, control wiring with FRLS PVC insulated copper conductor, cable allays, cable gland plates in two half, interconnections including supply & installation of following items and as per detailed technical specification.
148.00 | INCOMINGS
149.00 | 250 A, FP, 36 KA, MCCB with thermal magnetic based release having adjustable over load and adjustable short circuit with rotary operating mechanism and spreader terminals-01 No.
150.00 | METERING
151.00 | 96 mm square flush pattern digital Voltmeter (0-500 V), accuracy class 1, suitable range for 3 phase, 4 wire operation with LED display and built-in selector switch along with 3 nos. of 2 Amp SP MCBs.- 1 set
152.00 | 96 mm sq. Flush pattern Digital Type Ammeter of suitable range to measure 0-500A, for 3 phase 4 wire operation with LED display and built-in selector switch with 3 numbers of class 1.0 accuracy, 15 VA burden & suitable range CTs.- 1 set.
153.00 | 1 Set of Indication Lamps, LED type, R, Y, B each with 2 Amp. SP MCB for protection.
154.00 | BUS BAR
155.00 | 1 set of high conductivity Aluminium electrolytic grade, bus bars of minimum 300 Amps capacity, TPN with heat shrinkable colored sleeves and non-combustible, non-hygroscopic, high strength SMC/ DMC/Polymer material bus bars supports at required intervals.
156.00 | OUTGOINGS
157.00 | 63A, FP, 18 KA, MCCB with thermal magnetic based release having adjustable over load and adjustable short circuit with rotary operating mechanism and spreader terminals and ON/OFF LED Indication lamp-12 Nos.
158.00 | Note- All MCCBs should have (i) Ics = Icu at 415 V (ii) Rotary operating mechanism and terminal extension / spreaders (iii) ON/OFF Indication (iv) All MCCBs shall be current limiting type. | 1.00 | Job | 10.00 | 250000.00 | 250000.00 | 293000.00 | 293000.00 | 454909.59 | 454909.59 | 284000.00 | 284000.00 | 190000.00 | 190000.00 | 330000.00 | 330000.00 | 222000.00 | 222000.00 | 274912.00 | 274912.00 | 367000.00 | 367000.00 | 190000.00 | M/S RAHUL ENGINEERS
159.00 | Design, Supply, installation, testing & commissioning of L.T. outdoor double door Feeder Panel made of 2 mm thick electro galvanized steel/CRCA sheets for frame work and covers, 3mm thick for gland plates, totally enclosed, IP 55, free standing, floor mounting, dust and vermin proof, indoor, compartmentalised, including cleaning & finishing completewith all process, powder coated, painting, with PU gasket complete with handle and gasket, suitable for operation on 3 Phase and neutral, 415V, 50 Hz AC system with Al. busbars extensible on both sides, fabrication shall be done in transportation sections, entire panel shall have a common earth bar of suitable size at the rear with 2 nos. earth stud, control wiring with FRLS. PVC insulated copper conductor, cable allays, cable gland plates in two half, interconnections including supply & installation of following items and as per detailed technical specification enclosed.
160.00 | INCOMINGS
161.00 | 250 A, FP, 36 KA, MCCB with thermal magnetic based release having adjustable over load and adjustable short circuit with rotary operating mechanism and spreader terminals-01 No.
162.00 | METERING
163.00 | 96 mm square flush pattern digital Voltmeter (0-500 V), accuracy class 1, suitable range for 3 phase, 4 wire operation with LED display and built-in selector switch along with 3 nos. of 2 Amp SP MCBs.- 1 set
164.00 | 96 mm sq. Flush pattern Digital Type Ammeter of suitable range to measure 0-500A, for 3 phase 4 wire operation with LED display and built-in selector switch with 3 numbers of class 1.0 accuracy, 15 VA burden & suitable range CTs.- 1 set.
165.00 | 1 Set of Indication Lamps, LED type, R, Y, B each with 2 Amp. SP MCB for protection.
166.00 | BUS BAR
167.00 | 1 set of high conductivity Aluminium electrolytic grade, bus bars of minimum 300 Amps capacity, TPN with heat shrinkable colored sleeves and non-combustible, non-hygroscopic, high strength SMC/ DMC/Polymer material bus bars supports at required intervals.
168.00 | OUTGOINGS
169.00 | 100A, FP, 18 KA, MCCB with thermal magnetic based release having adjustable over load and adjustable short circuit with rotary operating mechanism and spreader terminals and ON/OFF LED Indication lamp-2 Nos.
170.00 | 63A, FP, 18 KA, MCCB with thermal magnetic based release having adjustable over load and adjustable short circuit with rotary operating mechanism and spreader terminals and ON/OFF LED Indication lamp-2 Nos.
171.00 | Note- All MCCBs should have (i) Ics = Icu at 415 V (ii) Rotary operating mechanism and terminal extension / spreaders (iii) ON/OFF Indication (iv) All MCCBs shall be current limiting type. | 1.00 | Job | 10.00 | 111000.00 | 111000.00 | 123498.10 | 123498.10 | 121441.18 | 121441.18 | 136000.00 | 136000.00 | 190000.00 | 190000.00 | 165000.00 | 165000.00 | 113000.00 | 113000.00 | 174295.00 | 174295.00 | 202000.00 | 202000.00 | 111000.00 | ECS ENGINEERING PVT LTD
172.00 | Design, Supply, installation, testing & commissioning of L.T. outdoor double door Feeder Panel made of 2 mm thick electro galvanized steel/CRCA sheets for frame work and covers, 3mm thick for gland plates, totally enclosed, IP 55, free standing, floor mounting, dust and vermin proof, indoor, compartmentalized, including cleaning & finishing complete with all process, powder coated, painting, with PU gasket complete with handle and gasket, suitable for operation on 3 Phase and neutral, 415V, 50 Hz AC system with Al. busbars extensible on both sides, fabrication shall be done in transportation sections, entire panel shall have a common earth bar of suitable size at the rear with 2 nos. earth stud, control wiring with FRLS. PVC insulated copper conductor, cable allays, cable gland plates in two half, interconnections including supply & installation of following items and as per detailed technical specification enclosed.
173.00 | INCOMINGS
174.00 | 200 A, FP, 36 KA, MCCB with thermal magnetic based release having adjustable over load and adjustable short circuit with rotary operating mechanism and spreader terminals-01 No.
175.00 | METERING
176.00 | 96 mm square flush pattern digital Voltmeter (0-500 V), accuracy class 1, suitable range for 3 phase, 4 wire operation with LED display and built-in selector switch along with 3 nos. of 2 Amp SP MCBs.- 1 set
177.00 | 96 mm sq. Flush pattern Digital Type Ammeter of suitable range to measure 0-500A, for 3 phase 4 wire operation with LED display and built-in selector switch with 3 numbers of class 1.0 accuracy, 15 VA burden & suitable range CTs.- 1 set.
178.00 | 1 Set of Indication Lamps, LED type, R, Y, B each with 2 Amp. SP MCB for protection.
179.00 | BUS BAR
180.00 | 1 set of high conductivity Aluminium electrolytic grade, bus bars of minimum 250 Amps capacity, TPN with heat shrinkable colored sleeves and non-combustible, non-hygroscopic, high strength SMC/ DMC/Polymer material bus bars supports at required intervals.
181.00 | OUTGOINGS
182.00 | 63 A, FP, 18 KA, MCCB with thermal magnetic based release having adjustable over load and adjustable short circuit with rotary operating mechanism and spreader terminals and ON/OFF LED Indication lamp-2 Nos.
183.00 | 32 A, FP, 18 KA, MCCB with thermal magnetic based release having adjustable over load and adjustable short circuit with rotary operating mechanism and spreader terminals and ON/OFF LED Indication lamp-2 Nos.
184.00 | 32 A, DP MCB - 4 Nos.
185.00 | Note- All MCCBs should have (i) Ics = Icu at 415 V (ii) Rotary operating mechanism and terminal extension / spreaders (iii) ON/OFF Indication (iv) All MCCBs shall be current limiting type. | 1.00 | Job | 10.00 | 116700.00 | 116700.00 | 102409.85 | 102409.85 | 122372.65 | 122372.65 | 135000.00 | 135000.00 | 190000.00 | 190000.00 | 140000.00 | 140000.00 | 118000.00 | 118000.00 | 174009.00 | 174009.00 | 183000.00 | 183000.00 | 102409.85 | Genesis
186.00 | Design, Supply, installation, testing & commissioning of L.T. outdoor double door Feeder Panel made of 2 mm thick electro galvanized steel/CRCA sheets for frame work and covers, 3mm thick for gland plates, totally enclosed, IP 55, free standing, floor mounting, dust and vermin proof, indoor, compartmentalized, including cleaning & finishing complete with all process, powder coated, painting, with PU gasket complete with handle and gasket, suitable for operation on 3 Phase and neutral, 415V, 50 Hz AC system with Al. busbars extensible on both sides, fabrication shall be done in transportation sections, entire panel shall have a common earth bar of suitable size at the rear with 2 nos. earth stud, control wiring with FRLS. PVC insulated copper conductor, cable allays, cable gland plates in two half, interconnections including supply & installation of following items and as per detailed technical specification enclosed.
187.00 | INCOMING
188.00 | 250 A, FP, 36 KA, MCCB with thermal magnetic based release having adjustable over load and adjustable short circuit with rotary operating mechanism and spreader terminals-01 No.
189.00 | METERING
190.00 | 96 mm square flush pattern digital Voltmeter (0-500 V), accuracy class 1, suitable range for 3 phase, 4 wire operation with LED display and built-in selector switch along with 3 nos. of 2 Amp SP MCBs.- 1 set
191.00 | 96 mm sq. Flush pattern Digital Type Ammeter of suitable range to measure 0-500A, for 3 phase 4 wire operation with LED display and built-in selector switch with 3 numbers of class 1.0 accuracy, 15 VA burden & suitable range CTs.- 1 set.
192.00 | 1 Set of Indication Lamps, LED type, R, Y, B each with 2 Amp. SP MCB for protection.
193.00 | BUS BAR
194.00 | 1 set of high conductivity Aluminium electrolytic grade, bus bars of minimum 300 Amps capacity, TPN with heat shrinkable colored sleeves and non-combustible, non-hygroscopic, high strength SMC/ DMC/Polymer material bus bars supports at required intervals.
195.00 | OUTGOINGS
196.00 | 100A, FP, 18 KA, MCCB with thermal magnetic based release having adjustable over load and adjustable short circuit with rotary operating mechanism and spreader terminals and ON/OFF LED Indication lamp-2 Nos.
197.00 | 63A, FP, 18 KA, MCCB with thermal magnetic based release having adjustable over load and adjustable short circuit with rotary operating mechanism and spreader terminals and ON/OFF LED Indication lamp-5 Nos.
198.00 | Note- All MCCBs should have (i) Ics = Icu at 415 V (ii) Rotary operating mechanism and terminal extension / spreaders (iii) ON/OFF Indication (iv) All MCCBs shall be current limiting type. | 1.00 | Job | 10.00 | 156800.00 | 156800.00 | 146000.00 | 146000.00 | 167316.37 | 167316.37 | 190000.00 | 190000.00 | 190000.00 | 190000.00 | 175000.00 | 175000.00 | 163000.00 | 163000.00 | 226248.00 | 226248.00 | 252000.00 | 252000.00 | 146000.00 | Genesis
199.00 | Design, Supply, installation, testing & commissioning of L.T. Indoor Feeder Panel (Qtr. Meter Panel Board) made of 2 mm thick electro galvanized steel/CRCA sheets for frame work and covers, 3mm thick for gland plates, totally enclosed, IP 54, free standing, floor mounted supported with MS angle iron and above ground level up to 1 feet, dust and vermin proof, indoor, compartmentalized, including cleaning & finishing complete with all process, powder coated, painting, with PU gasket complete with handle and gasket, suitable for operation on 3 Phase and neutral, 415V, 50 Hz AC system with Al. busbars extensible on both sides, fabrication shall be done in transportation sections, entire panel shall have a common earth bar of suitable size at the rear with 2 nos. earth stud, control wiring with FRLS. PVC insulated copper conductor, cable allays, cable gland plates in two half, interconnections including supply & installation of following items and as per detailed technical specification enclosed.
200.00 | INCOMING
201.00 | 100 A, FP, 18 KA, MCCB with thermal magnetic based release having adjustable over load and adjustable short circuit with rotary operating mechanism and spreader terminals-01 No.
202.00 | METERING
203.00 | 96 mm square flush pattern digital Voltmeter (0-500 V), accuracy class 1, suitable range for 3 phase, 4 wire operation with LED display and built-in selector switch along with 3 nos. of 2 Amp SP MCBs.- 1 set
204.00 | 96 mm sq. Flush pattern Digital Type Ammeter of suitable range to measure 0-500A, for 3 phase 4 wire operation with LED display and built-in selector switch with 3 numbers of class 1.0 accuracy, 15 VA burden & suitable range CTs.- 1 set.
205.00 | 1 Set of Indication Lamps, LED type, R, Y, B each with 2 Amp. SP MCB for protection.
206.00 | BUS BAR
207.00 | 1 set of high conductivity Aluminium electrolytic grade, bus bars of minimum 125 Amps capacity, TPN with heat shrinkable colored sleeves and non-combustible, non-hygroscopic, high strength SMC/ DMC/Polymer material bus bars supports at required intervals.
208.00 | OUTGOINGS
209.00 | 63A, FP MCB with Class 1 Base mounting Single Phase kWh meter (1P LCD Meter 5-30A) with LCD display for quarters meter reading-06 Nos.
210.00 | Note- All MCCBs should have (i) Ics = Icu at 415 V (ii) Rotary operating mechanism and terminal extension / spreaders (iii) ON/OFF Indication (iv) All MCCBs shall be current limiting type. | 8.00 | Job | 10.00 | 79000.00 | 632000.00 | 158000.00 | 1264000.00 | 111165.83 | 889326.64 | 90000.00 | 720000.00 | 190000.00 | 1520000.00 | 167000.00 | 1336000.00 | 77000.00 | 616000.00 | 186791.00 | 1494328.00 | 123000.00 | 984000.00 | 616000.00 | Krishsons International Engineers And Consultants (I) Pvt. Ltd
211.00 | Supply of following size XLPE insulated, PVC sheathed aluminium conductor armourd power cable of 1.1KV grade confiriming to IS 7098 (Part 1) with upto date amendments etc as required.
212.00 | (a) 3.5 x 120 Sq.mm | 250.00 | Meter | 10.00 | 693.00 | 173250.00 | 580.00 | 145000.00 | 481.16 | 120290.00 | 645.00 | 161250.00 | 650.00 | 162500.00 | 645.00 | 161250.00 | 650.00 | 162500.00 | 661.94 | 165485.00 | 825.00 | 206250.00 | 120290.00 | Industrial Traders
213.00 | (b) 3.5 x 35 Sq.mm | 200.00 | Meter | 10.00 | 241.00 | 48200.00 | 225.00 | 45000.00 | 165.04 | 33008.00 | 225.00 | 45000.00 | 270.00 | 54000.00 | 225.00 | 45000.00 | 340.00 | 68000.00 | 274.35 | 54870.00 | 290.00 | 58000.00 | 33008.00 | Industrial Traders
214.00 | (c) 4 x 25 Sq.mm | 500.00 | Meter | 10.00 | 214.00 | 107000.00 | 182.00 | 91000.00 | 142.63 | 71315.00 | 190.00 | 95000.00 | 250.00 | 125000.00 | 188.00 | 94000.00 | 215.00 | 107500.00 | 249.54 | 124770.00 | 255.00 | 127500.00 | 71315.00 | Industrial Traders
215.00 | (d) 4 x 16 Sq.mm | 500.00 | Meter | 10.00 | 163.00 | 81500.00 | 140.00 | 70000.00 | 103.91 | 51955.00 | 130.00 | 65000.00 | 230.00 | 115000.00 | 144.00 | 72000.00 | 172.00 | 86000.00 | 203.13 | 101565.00 | 195.00 | 97500.00 | 51955.00 | Industrial Traders
216.00 | Supplying and laying of following size DWC HDPE pipe ISI marked along with all accessories like socket, bend, couplers etc. conforming to IS 14930, Part II complete with fitting and cutting, jointing etc. direct in ground (75 cm below ground level) including excavation and refilling the trench but excluding sand cushioning and protective covering etc., complete as required. (a) 120 mm dia (OD-120 mm & ID-103 mm nominal) | 60.00 | Meter | 10.00 | 268.00 | 16080.00 | 175.00 | 10500.00 | 267.79 | 16067.40 | 550.00 | 33000.00 | 200.00 | 12000.00 | 120.00 | 7200.00 | 160.00 | 9600.00 | 165.00 | 9900.00 | 290.00 | 17400.00 | 7200.00 | Shiva Enterprises
217.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/ HUME METAL pipe as required.
218.00 | (a) Above 95 sq. mm and upto 185 sq. mm | 10.00 | Meter | 10.00 | 55.00 | 550.00 | 100.00 | 1000.00 | 29.10 | 291.00 | 80.00 | 800.00 | 200.00 | 2000.00 | 80.00 | 800.00 | 60.00 | 600.00 | 99.00 | 990.00 | 130.00 | 1300.00 | 291.00 | Industrial Traders
219.00 | (b) Above 185 sq. mm and upto 400 sq. mm | 10.00 | Meter | 10.00 | 75.00 | 750.00 | 250.00 | 2500.00 | 46.57 | 465.70 | 140.00 | 1400.00 | 300.00 | 3000.00 | 100.00 | 1000.00 | 80.00 | 800.00 | 99.00 | 990.00 | 170.00 | 1700.00 | 465.70 | Industrial Traders
220.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing masonry open duct as required. |  |  | 1.00
221.00 | (a) Above 95 sq. mm and upto 185 sq. mm | 10.00 | Meter | 10.00 | 55.00 | 550.00 | 200.00 | 2000.00 | 46.57 | 465.70 | 65.00 | 650.00 | 200.00 | 2000.00 | 80.00 | 800.00 | 50.00 | 500.00 | 99.00 | 990.00 | 130.00 | 1300.00 | 465.70 | Industrial Traders
222.00 | (b) Above 185 sq. mm and upto 400 sq. mm | 10.00 | Meter | 10.00 | 75.00 | 750.00 | 300.00 | 3000.00 | 58.21 | 582.10 | 120.00 | 1200.00 | 300.00 | 3000.00 | 100.00 | 1000.00 | 65.00 | 650.00 | 99.00 | 990.00 | 180.00 | 1800.00 | 582.10 | Industrial Traders
223.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/ HUME METAL pipe as required.
224.00 | (a) Upto 35 sq. mm (clamped with 1mm thick saddle) | 50.00 | Meter | 10.00 | 55.00 | 2750.00 | 250.00 | 12500.00 | 81.50 | 4075.00 | 60.00 | 3000.00 | 100.00 | 5000.00 | 50.00 | 2500.00 | 35.00 | 1750.00 | 99.00 | 4950.00 | 75.00 | 3750.00 | 1750.00 | Krishsons International Engineers And Consultants (I) Pvt. Ltd
225.00 | (b) Above 35 sq. mm and upto 95 sq. mm (clamped with 25x3mm MS flat clamp) | 20.00 | Meter | 10.00 | 65.00 | 1300.00 | 250.00 | 5000.00 | 116.43 | 2328.60 | 140.00 | 2800.00 | 150.00 | 3000.00 | 70.00 | 1400.00 | 100.00 | 2000.00 | 99.00 | 1980.00 | 90.00 | 1800.00 | 1300.00 | ECS ENGINEERING PVT LTD
226.00 | (c) Above 95 sq. mm and upto 185 sq. mm (clamped with 25/40x3mm MS flat clamp) | 20.00 | Meter | 10.00 | 75.00 | 1500.00 | 250.00 | 5000.00 | 139.72 | 2794.40 | 160.00 | 3200.00 | 200.00 | 4000.00 | 90.00 | 1800.00 | 110.00 | 2200.00 | 99.00 | 1980.00 | 130.00 | 2600.00 | 1500.00 | ECS ENGINEERING PVT LTD
227.00 | (d) Above 185 sq. mm and upto 400 sq. mm (clamped with 40x3mm MS flat clamp) | 20.00 | Meter | 10.00 | 95.00 | 1900.00 | 300.00 | 6000.00 | 186.29 | 3725.80 | 240.00 | 4800.00 | 300.00 | 6000.00 | 120.00 | 2400.00 | 160.00 | 3200.00 | 99.00 | 1980.00 | 170.00 | 3400.00 | 1900.00 | ECS ENGINEERING PVT LTD
228.00 | Extra for excavation of hard rock/ concrete surface by cutting the hard road/ concrete surface and getting out the excavated material, lifting and disposing of the same within a lead of 50 Mtrs. as directed by Engineer-in-charge. | 2.00 | CuM | 10.00 | 6000.00 | 12000.00 | 8500.00 | 17000.00 | 1164.34 | 2328.68 | 2000.00 | 4000.00 | 5000.00 | 10000.00 | 1500.00 | 3000.00 | 800.00 | 1600.00 | 9350.00 | 18700.00 | 2200.00 | 4400.00 | 1600.00 | Krishsons International Engineers And Consultants (I) Pvt. Ltd
229.00 | Earthing with GI earth plate 600mm X 600mm X 6 mm thick including accessories and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 mtr long etc with charcoal or coke and salt complete as required | 10.00 | Each | 10.00 | 10300.00 | 103000.00 | 1500.00 | 15000.00 | 9314.76 | 93147.60 | 16000.00 | 160000.00 | 10000.00 | 100000.00 | 8500.00 | 85000.00 | 7000.00 | 70000.00 | 9350.00 | 93500.00 | 7500.00 | 75000.00 | 15000.00 | Genesis
230.00 | Supplying and laying 25 mm X 5 mm G.l strip at 0.50 meter below ground as strip earth electrode, including connection/ terminating with nut, bolt, spring, washer etc. as required. | 100.00 | Meter | 10.00 | 270.00 | 27000.00 | 305.00 | 30500.00 | 142.05 | 14205.00 | 350.00 | 35000.00 | 300.00 | 30000.00 | 180.00 | 18000.00 | 140.00 | 14000.00 | 198.00 | 19800.00 | 240.00 | 24000.00 | 14000.00 | Krishsons International Engineers And Consultants (I) Pvt. Ltd
231.00 | Providing and fixing 25 mm x 5 mm G. I. strip in 40 mm dia. G. I. pipe from earth electrode as required. | 30.00 | Meter | 10.00 | 600.00 | 18000.00 | 705.00 | 21150.00 | 491.35 | 14740.50 | 650.00 | 19500.00 | 50.00 | 1500.00 | 400.00 | 12000.00 | 500.00 | 15000.00 | 198.00 | 5940.00 | 650.00 | 19500.00 | 1500.00 | M/S RAHUL ENGINEERS
232.00 | Providing and fixing 25 mm X 5 mm G.I. strip on surface or in recess for connections etc. as required | 100.00 | Meter | 10.00 | 180.00 | 18000.00 | 200.00 | 20000.00 | 200.26 | 20026.00 | 280.00 | 28000.00 | 300.00 | 30000.00 | 180.00 | 18000.00 | 140.00 | 14000.00 | 198.00 | 19800.00 | 200.00 | 20000.00 | 14000.00 | Krishsons International Engineers And Consultants (I) Pvt. Ltd
233.00 | Earthing with G.I. earth pipe 4.5 metre long, 40 mm dia including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe etc. with charcoal/ coke and salt as required | 25.00 | Each | 10.00 | 7000.00 | 175000.00 | 8800.00 | 220000.00 | 9547.62 | 238690.50 | 11500.00 | 287500.00 | 10000.00 | 250000.00 | 6000.00 | 150000.00 | 6000.00 | 150000.00 | 9570.00 | 239250.00 | 5000.00 | 125000.00 | 125000.00 | girnar electricals
234.00 | Providing and laying earth connection from earth electrode with 6 SWG dia G.I. Wire in 15 mm dia G.I. pipe from earth electrode including connection with G.I. thimble excavation and re-filling as required. | 150.00 | Meter | 10.00 | 122.00 | 18300.00 | 70.00 | 10500.00 | 174.65 | 26197.50 | 250.00 | 37500.00 | 200.00 | 30000.00 | 175.00 | 26250.00 | 150.00 | 22500.00 | 49.50 | 7425.00 | 185.00 | 27750.00 | 7425.00 | Virtus Techno
235.00 | Providing and fixing 6 SWG dia G.I. wire on surface or in recess for loop earthing as required. | 100.00 | Meter | 10.00 | 32.00 | 3200.00 | 38.00 | 3800.00 | 34.93 | 3493.00 | 35.00 | 3500.00 | 200.00 | 20000.00 | 20.00 | 2000.00 | 30.00 | 3000.00 | 38.50 | 3850.00 | 35.00 | 3500.00 | 2000.00 | Shiva Enterprises
236.00 | Providing and laying in position cement concrete 1:2:4 (1 cement : 2 coarse sand :4 graded stone aggregate 20 mm nominal size) in foundation of pump, DG set etc including form work etc as required. | 2.00 | CuM | 10.00 | 6000.00 | 12000.00 | 7500.00 | 15000.00 | 9314.76 | 18629.52 | 10000.00 | 20000.00 | 8000.00 | 16000.00 | 1500.00 | 3000.00 | 6000.00 | 12000.00 | 7150.00 | 14300.00 | 9000.00 | 18000.00 | 3000.00 | Shiva Enterprises
237.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of XLPE insulated PVC sheathed aluminium conductor cable of 1.1 kV grade when as required. |  |  | 1.00
238.00 | (a) 3.5x35 sqmm | 30.00 | Each | 10.00 | 300.00 | 9000.00 | 235.00 | 7050.00 | 711.41 | 21342.30 | 380.00 | 11400.00 | 100.00 | 3000.00 | 250.00 | 7500.00 | 300.00 | 9000.00 | 660.00 | 19800.00 | 270.00 | 8100.00 | 3000.00 | M/S RAHUL ENGINEERS
239.00 | (b) 3.5x120 sqmm | 16.00 | Each | 10.00 | 840.00 | 13440.00 | 550.00 | 8800.00 | 1148.04 | 18368.64 | 850.00 | 13600.00 | 200.00 | 3200.00 | 550.00 | 8800.00 | 600.00 | 9600.00 | 716.10 | 11457.60 | 700.00 | 11200.00 | 3200.00 | M/S RAHUL ENGINEERS
240.00 | (c) 3.5x185 sqmm | 10.00 | Each | 10.00 | 1450.00 | 14500.00 | 676.00 | 6760.00 | 1227.21 | 12272.10 | 1000.00 | 10000.00 | 250.00 | 2500.00 | 750.00 | 7500.00 | 900.00 | 9000.00 | 882.20 | 8822.00 | 825.00 | 8250.00 | 2500.00 | M/S RAHUL ENGINEERS
241.00 | (d) 3.5x240 sqmm | 10.00 | Each | 10.00 | 1550.00 | 15500.00 | 800.00 | 8000.00 | 1837.33 | 18373.30 | 1150.00 | 11500.00 | 300.00 | 3000.00 | 850.00 | 8500.00 | 1000.00 | 10000.00 | 1103.30 | 11033.00 | 100.00 | 1000.00 | 1000.00 | girnar electricals
242.00 | (e) 4x16 sqmm | 50.00 | Each | 10.00 | 265.00 | 13250.00 | 180.00 | 9000.00 | 626.41 | 31320.50 | 3000.00 | 150000.00 | 250.00 | 12500.00 | 200.00 | 10000.00 | 300.00 | 15000.00 | 587.40 | 29370.00 | 200.00 | 10000.00 | 9000.00 | Genesis
243.00 | (f) 4x25 sqmm | 50.00 | Each | 10.00 | 275.00 | 13750.00 | 220.00 | 11000.00 | 631.07 | 31553.50 | 300.00 | 15000.00 | 270.00 | 13500.00 | 225.00 | 11250.00 | 300.00 | 15000.00 | 610.50 | 30525.00 | 250.00 | 12500.00 | 11000.00 | Genesis
244.00 | Providing and fixing M.V. danger notice plate of 200 mm X 150 mm, made of mild steel, at least 2 mm thick, and vitreous enameled white on both sides, and with inscription in single red colour on front side as required. | 20.00 | Each | 10.00 | 175.00 | 3500.00 | 400.00 | 8000.00 | 116.43 | 2328.60 | 150.00 | 3000.00 | 300.00 | 6000.00 | 500.00 | 10000.00 | 350.00 | 7000.00 | 605.00 | 12100.00 | 400.00 | 8000.00 | 2328.60 | Industrial Traders
245.00 | Supplying and installing following size of perforated Hot Dipped Galvanised Iron cable tray (Galvanisation thickness not less than 50 microns) with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with G.I. suspenders including G.I. bolts & nuts, etc. as required. (a) 150 mm witdh X 50 mm depth X 1.6 mm thickness | 30.00 | Meter | 10.00 | 600.00 | 18000.00 | 700.00 | 21000.00 | 698.60 | 20958.00 | 675.00 | 20250.00 | 1000.00 | 30000.00 | 600.00 | 18000.00 | 700.00 | 21000.00 | 638.00 | 19140.00 | 580.00 | 17400.00 | 17400.00 | girnar electricals
246.00 | Supply of petrol-driven long-reach hedge trimmer for trimming, comfortable and flexible working on tall, long and wide hedges etc complete as required. Model No. HL 94 C-E of STIHL make or its equivalent make and model. | 1.00 | Each | 10.00 | 45000.00 | 45000.00 | 55000.00 | 55000.00 | 63644.27 | 63644.27 | 61500.00 | 61500.00 | 20000.00 | 20000.00 | 8500.00 | 8500.00 | 40000.00 | 40000.00 | 53790.00 | 53790.00 | 57000.00 | 57000.00 | 8500.00 | Shiva Enterprises
247.00 | Supply of Electric-driven long-reach hedge trimmer for trimming, comfortable and flexible working on tall, long and wide hedges etc complete as required. Model No. HSE 81 of STIHL make or its equivalent make and model. | 1.00 | Each | 10.00 | 28000.00 | 28000.00 | 22000.00 | 22000.00 | 20228.02 | 20228.02 | 24500.00 | 24500.00 | 20000.00 | 20000.00 | 8500.00 | 8500.00 | 27940.00 | 27940.00 | 23100.00 | 23100.00 | 25200.00 | 25200.00 | 8500.00 | Shiva Enterprises
248.00 | Supplying and fixing following way, horizontal type three pole and neutral, sheet steel, MCB distribution board, 415V, on surface/recess, complete with tinned copper bus bar, neutral bus bar, earth bus bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCB/RCCB/Isolator) |  |  | 1.00
249.00 | 8 way (8+24), Double door | 53.00 | Each | 10.00 | 5000.00 | 265000.00 | 4000.00 | 212000.00 | 3195.69 | 169371.57 | 5300.00 | 280900.00 | 2000.00 | 106000.00 | 2800.00 | 148400.00 | 4000.00 | 212000.00 | 4148.98 | 219895.94 | 5400.00 | 286200.00 | 106000.00 | M/S RAHUL ENGINEERS
250.00 | 12 way (8+36), Double door | 1.00 | Each | 10.00 | 6360.00 | 6360.00 | 10000.00 | 10000.00 | 4816.89 | 4816.89 | 7300.00 | 7300.00 | 3000.00 | 3000.00 | 4320.00 | 4320.00 | 5950.00 | 5950.00 | 5918.44 | 5918.44 | 8000.00 | 8000.00 | 3000.00 | M/S RAHUL ENGINEERS
251.00 | Supplying and fixing way, single pole and neutral, sheet steel, double door MCB distribution board, 240 V, on surface/recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCB/RCCB/Isolator). (a) 8 way, Double door | 7.00 | Each | 10.00 | 1700.00 | 11900.00 | 1800.00 | 12600.00 | 1321.95 | 9253.65 | 1800.00 | 12600.00 | 2000.00 | 14000.00 | 975.00 | 6825.00 | 1500.00 | 10500.00 | 1703.13 | 11921.91 | 2000.00 | 14000.00 | 6825.00 | Shiva Enterprises
252.00 | Supplying and fixing following rating, double pole, 240 V, 10 kA, "C" curve, MCB in the existing MCB DB complete with connections, testing and commissioning etc. as required (a) 63 Amps | 7.00 | Each | 10.00 | 705.00 | 4935.00 | 400.00 | 2800.00 | 616.68 | 4316.76 | 900.00 | 6300.00 | 200.00 | 1400.00 | 625.00 | 4375.00 | 840.00 | 5880.00 | 1283.92 | 8987.44 | 850.00 | 5950.00 | 1400.00 | M/S RAHUL ENGINEERS
253.00 | Supplying and fixing following rating, triple pole (TP), 240 V, 10 kA, "C" curve, MCB in the existing MCB DB complete with connections, testing and commissioning etc. as required (a) 40 Amps | 7.00 | Each | 10.00 | 1000.00 | 7000.00 | 650.00 | 4550.00 | 849.13 | 5943.91 | 1250.00 | 8750.00 | 800.00 | 5600.00 | 865.00 | 6055.00 | 1200.00 | 8400.00 | 1683.22 | 11782.54 | 1350.00 | 9450.00 | 4550.00 | Genesis
254.00 | Supplying and fixing following rating, four pole, 415 V, 10 kA, "C" curve, MCB in the existing MCB DB complete with connections, testing and commissioning etc. as required. (a) 63 Amps | 53.00 | Each | 10.00 | 1340.00 | 71020.00 | 1800.00 | 95400.00 | 1150.88 | 60996.64 | 1550.00 | 82150.00 | 700.00 | 37100.00 | 1175.00 | 62275.00 | 1350.00 | 71550.00 | 1591.04 | 84325.12 | 1700.00 | 90100.00 | 37100.00 | M/S RAHUL ENGINEERS
255.00 | Supplying and fixing 10 A to 32 A rating, 240/415 V, 10 kA, "C" curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. complete as required. (a) Single Pole. | 1000.00 | Each | 10.00 | 125.00 | 125000.00 | 130.00 | 130000.00 | 127.96 | 127960.00 | 180.00 | 180000.00 | 200.00 | 200000.00 | 110.00 | 110000.00 | 130.00 | 130000.00 | 164.30 | 164300.00 | 145.00 | 145000.00 | 110000.00 | Shiva Enterprises
256.00 | Supplying and fixing single pole blanking plate in the existing MCB DB complete etc. as required. | 30.00 | Each | 10.00 | 10.00 | 300.00 | 100.00 | 3000.00 | 23.28 | 698.40 | 15.00 | 450.00 | 100.00 | 3000.00 | 10.00 | 300.00 | 16.00 | 480.00 | 33.00 | 990.00 | 10.00 | 300.00 | 300.00 | ECS ENGINEERING PVT LTD, Shiva Enterprises, girnar electricals
257.00 | Dismantling of existing 415 volt, 50Hz LT panels/AMF with accessories by disconnecting electrical connections, earthing connections of panels and transporting the upto AAI store by engaging skilled and unskilled manpower, mechanical means with required T & P etc complete as required. (a) LT Panel / Feeder Panel (approx. size 2.3 x 2.1 x 1.1 mtr ) | 30.00 | Job | 10.00 | 6000.00 | 180000.00 | 2000.00 | 60000.00 | 698.60 | 20958.00 | 1500.00 | 45000.00 | 5000.00 | 150000.00 | 1800.00 | 54000.00 | 1000.00 | 30000.00 | 11000.00 | 330000.00 | 3500.00 | 105000.00 | 20958.00 | Industrial Traders
258.00 | Dismantling of following LT cables from ground/open masonry duct and transporting the upto AAI store by engaging skilled and unskilled manpower, mechanical means with required T & P etc complete as required. |  |  | 1.00
259.00 | (a) up to 95 sqmm | 50.00 | Meter | 10.00 | 50.00 | 2500.00 | 60.00 | 3000.00 | 58.21 | 2910.50 | 40.00 | 2000.00 | 100.00 | 5000.00 | 60.00 | 3000.00 | 30.00 | 1500.00 | 77.00 | 3850.00 | 70.00 | 3500.00 | 1500.00 | Krishsons International Engineers And Consultants (I) Pvt. Ltd
260.00 | (b) Above 95 sq. mm and upto 185 sq. mm | 25.00 | Meter | 10.00 | 60.00 | 1500.00 | 80.00 | 2000.00 | 69.86 | 1746.50 | 60.00 | 1500.00 | 100.00 | 2500.00 | 80.00 | 2000.00 | 30.00 | 750.00 | 77.00 | 1925.00 | 100.00 | 2500.00 | 750.00 | Krishsons International Engineers And Consultants (I) Pvt. Ltd
261.00 | © Above 185 sq. mm and upto 400 sq. mm | 25.00 | Meter | 10.00 | 75.00 | 1875.00 | 100.00 | 2500.00 | 81.50 | 2037.50 | 100.00 | 2500.00 | 100.00 | 2500.00 | 100.00 | 2500.00 | 30.00 | 750.00 | 55.00 | 1375.00 | 125.00 | 3125.00 | 750.00 | Krishsons International Engineers And Consultants (I) Pvt. Ltd
| Total in Figures |  |  |  |  | 7059010.00 |  | 7851800.60 |  | 9207983.03 |  | 8162300.00 |  | 8027800.00 |  | 8350000.00 |  | 6562700.00 |  | 9131469.99 |  | 9209225.00
Lowest Amount Quoted BY: Krishsons International Engineers And Consultants (I) Pvt. Ltd(6562700.00)

## BOQ Summary
BOQ Summary Details Tender Title: Augmentation of power supply system, substation and allied work at CATC, Prayagraj. SH- Replacement of existing LT Panels of Institute block and allied works Tender ID: 2025_AAI_251184_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Krishsons International Engineers And Consultants (I) Pvt. Ltd (BID ID -922552) | 6562700.00 | L1
| 2 | ECS ENGINEERING PVT LTD (BID ID -919860) | 7059010.00 | L2
| 3 | Genesis (BID ID -919898) | 7851800.60 | L3
| 4 | M/S RAHUL ENGINEERS (BID ID -922669) | 8027800.00 | L4
| 5 | Awasthi Electric Works (BID ID -922477) | 8162300.00 | L5
| 6 | Shiva Enterprises (BID ID -921914) | 8350000.00 | L6
| 7 | Virtus Techno (BID ID -922368) | 9131469.99 | L7
| 8 | Industrial Traders (BID ID -922435) | 9207983.03 | L8
| 9 | girnar electricals (BID ID -922615) | 9209225.00 | L9