## BoQ1
Government eProcurement System Created By: MAHESH PAL SINGH Created Date/Time: 12-Nov-2025 03:44 PM Tender Title: SITC of Gas suppression system at NDB Keshod Airport Tender ID: 2025_AAI_251717_1
Tender Inviting Authority: Senior Manager Engg-Ele , Keshod Airport, Keshod - 362220
Name of Work: SITC of gas suppression system at NDB Keshod Airport
Contract No: 2025_AAI_251717_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | CENTRE TAP ENGINEERING (GSTN-24AGPPP8172K1ZP) BID ID -920517 |  | Kalpataru Industries (GSTN-NA) BID ID -921555
[5 empty] | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | SITC of 34L seamless storage cylinder duly filled with NOVAC 1230 or equivalent agent (approx. 19 Kg) complete with valve assembly, pressure gauge and pressure switch and other associated standard accessories. | 1.00 | Each | 0.00 | 175000.00 | 175000.00 | 128200.00 | 128200.00 | 128200.00 | Kalpataru Industries
2.00 | ​SITC of (a)control head suitable for operating electrically from fire detection and control panel with all accessories. (b) High pressure flexible rubber discharge hose with braided reinforcement. ( c) Discharge nozzles designed to provide the proper flow and distribution of gas to flood hazard area at 180/360 degrees. (d) SITC of gas discharge pressure switch to trip A.C., electrical equipment etc. all shall be as per OEM recommendation & standards | 1.00 | Each |  | 50000.00 | 50000.00 | 74950.00 | 74950.00 | 50000.00 | CENTRE TAP ENGINEERING
3.00 | ​SITC of manual gas release station and Manual gas abort station having manual break glass push button type call points with auxiliary contacts, hammer gland etc. complete in all respect and shall be as per OEM recommendation & standards. | 1.00 | Each |  | 10000.00 | 10000.00 | 3900.00 | 3900.00 | 3900.00 | Kalpataru Industries
4.00 | ​SITC of 4 cross zone Fire Alarm Gas release panel with built in time relay, auto/maula selector switch housed in a suitable 16 SWG M.S. Sheet panel. The control panel shall have the arrangement for Audio/ Visual indications by dual lamps LED's for fire and fault in each zone with lamp test facility. The panel shall be connected to smoke detectors. The control panel shall be working on standby power supply by 2x12 volts, 7 AH sealed maintenance free batteries complete with circuit wiring etc., as per IS :2189 and have provision for testing each circuit separately including resetting and shall be as per OEM recommendation & standards | 1.00 | Set |  | 25000.00 | 25000.00 | 36616.00 | 36616.00 | 25000.00 | CENTRE TAP ENGINEERING
5.00 | SITC of photo electric smoke detectors complete with base and mounting accessories. | 6.00 | Each |  | 2000.00 | 12000.00 | 2150.00 | 12900.00 | 12000.00 | CENTRE TAP ENGINEERING
6.00 | Providing & fixing seamless pipe complete with all fittings painting with one coat of red oxide and 2 coats of enamel paint, piping to be fixed on ceiling with MS suspended supports, clamps, anchor fasteners, cutting chases / holes in valve ceiling and making good the same as required for the following sizes:- a) 32mm All shall be as per OEM recommendation & Meter | 6.00 | Meter |  | 1000.00 | 6000.00 | 2935.00 | 17610.00 | 6000.00 | CENTRE TAP ENGINEERING
7.00 | Providing & fixing seamless pipe complete with all fittings painting with one coat of red oxide and 2 coats of enamel paint, piping to be fixed on ceiling with MS suspended supports, clamps, anchor fasteners, cutting chases / holes in valve ceiling and making good the same as required for the following sizes:- a) 25mm All shall be as per OEM recommendation & Meter | 6.00 | Meter |  | 800.00 | 4800.00 | 2545.00 | 15270.00 | 4800.00 | CENTRE TAP ENGINEERING
8.00 | ​Supply of 2C x 1.5 sq.mm armoured, FRLS, Flexible, Multi strand, copper conductor cable and laying/fixing the same on ceiling/wall/false ceiling/in pipe/trunking etc connection, testing and commissioning complete as required as per OEM. | 50.00 | Meter |  | 150.00 | 7500.00 | 195.00 | 9750.00 | 7500.00 | CENTRE TAP ENGINEERING
9.00 | ​Supply, installation, connection, testing and commissioning of Sounder/Hooter complete including base plate, box, necessary accessories etc. complete as required as per OEM. | 1.00 | Each |  | 5000.00 | 5000.00 | 2410.00 | 2410.00 | 2410.00 | Kalpataru Industries
| Total in Figures |  |  |  |  | 295300.00 |  | 301606.00
Lowest Amount Quoted BY: CENTRE TAP ENGINEERING(295300.00)

## BOQ Summary
BOQ Summary Details Tender Title: SITC of Gas suppression system at NDB Keshod Airport Tender ID: 2025_AAI_251717_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | CENTRE TAP ENGINEERING (BID ID -920517) | 295300.00 | L1
| 2 | Kalpataru Industries (BID ID -921555) | 301606.00 | L2