## BoQ1
Government eProcurement System Created By: Shridhar Gupta Created Date/Time: 27-Nov-2025 04:14 PM Tender Title: Construction of New Terminal Building and Other Allied structures Phase I II at Patna Airport SH Miscellaneous Internal External Electrical works at JPNI Airport Patna Tender ID: 2025_AAI_251898_1
Tender Inviting Authority: Airports Authority of India
Name of Work: Construction of New Domestic Terminal Building and Other Structures (Phase I & II) at Patna Airport.
Contract No:
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Ascent Electrification Engineers (GSTN-24AAOFA2574R1ZU) BID ID -923173 |  | Awasthi Electric Works (GSTN-09ABAPA1866D1Z5) BID ID -923262 |  | SAURABH ENTERPRISES (GSTN-NA) BID ID -921844
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | SUB HEAD 1: CPWD DSR (E&M)-2025 ITEMS.
1.01 | Execution of works as per CPWD DSR (E&M)- 2025 (Excluding items in SH-2 from ) excluding GST for Rs.85,00,000/- as and when required. Note for contractor: For 10% above contractor shall quote 8500000+10%= 93,50,000. Similarly for 10% below contractor shall quote 8500000-10%= 76,50,000. (The work assigned shall be executed on priority within justified time as per direction of EIC) | 1.00 | Job |  | 6393700.00 | 6393700.00 | 7140000.00 | 7140000.00 | 3000000.00 | 3000000.00 | 3000000.00 | SAURABH ENTERPRISES
2.00 | SUB HEAD 1: CPWD DSR (E&M)-2025 ITEMS. DB dressing including Tracing of circuits as per drawing, providing ferrules, lugs, thimbal as per drawing and as per site conditions of following DBs including testing and commissioning of DBs etc. complete as required as per site requirement.
2.01 | 8 way, Double door SPN DB | 25.00 | Each |  | 1200.00 | 30000.00 | 1250.00 | 31250.00 | 400.00 | 10000.00 | 10000.00 | SAURABH ENTERPRISES
2.02 | 12 way, Double door SPN DB | 25.00 | Each |  | 1200.00 | 30000.00 | 1500.00 | 37500.00 | 500.00 | 12500.00 | 12500.00 | SAURABH ENTERPRISES
2.03 | 4 way (4 + 12), Double door horizontal type TPN DB | 5.00 | Each |  | 1200.00 | 6000.00 | 4500.00 | 22500.00 | 800.00 | 4000.00 | 4000.00 | SAURABH ENTERPRISES
2.04 | 6 way (4 + 18), Double door horizontal type TPN DB | 10.00 | Each |  | 1200.00 | 12000.00 | 5350.00 | 53500.00 | 900.00 | 9000.00 | 9000.00 | SAURABH ENTERPRISES
2.05 | 8 way (4 + 24), Double door horizontal type TPN DB | 20.00 | Each |  | 1800.00 | 36000.00 | 6400.00 | 128000.00 | 1500.00 | 30000.00 | 30000.00 | SAURABH ENTERPRISES
2.06 | 12 way (8 + 36), Double door horizontal type TPN DB | 20.00 | Each |  | 1800.00 | 36000.00 | 8800.00 | 176000.00 | 1700.00 | 34000.00 | 34000.00 | SAURABH ENTERPRISES
2.07 | 4 way (8 + 12), Double door VTPN DB | 10.00 | Each |  | 1200.00 | 12000.00 | 6500.00 | 65000.00 | 1700.00 | 17000.00 | 12000.00 | Ascent Electrification Engineers
3.00 | Supply and fixing of 25 mm x 16 mm PVC Casing beat as per site requirement. | 1000.00 | Mtr. |  | 32.00 | 32000.00 | 35.00 | 35000.00 | 200.00 | 200000.00 | 32000.00 | Ascent Electrification Engineers
4.00 | Supplying and fixing following rating, double pole / four pole, 240 / 415 volts, RCBO having a sensitivity current upto 300 milliamperes in the existing MCB DB complete with connections, testing and commissioning etc. as required.
4.01 | 25 amps DP 2 module | 50.00 | Each |  | 1757.00 | 87850.00 | 2500.00 | 125000.00 | 450.00 | 22500.00 | 22500.00 | SAURABH ENTERPRISES
4.02 | 40 amps DP 2 module | 80.00 | Each |  | 1757.00 | 140560.00 | 2500.00 | 200000.00 | 450.00 | 36000.00 | 36000.00 | SAURABH ENTERPRISES
4.03 | 40 amps FP 4 module | 50.00 | Each |  | 2167.00 | 108350.00 | 3000.00 | 150000.00 | 900.00 | 45000.00 | 45000.00 | SAURABH ENTERPRISES
4.04 | 63 amps FP 4 module | 100.00 | Each |  | 2586.00 | 258600.00 | 3350.00 | 335000.00 | 950.00 | 95000.00 | 95000.00 | SAURABH ENTERPRISES
5.00 | SITC of Exhaust Fans
5.01 | SITC of single phase 1400 RPM, 300 mm dia, sweep heavy exhaust fan with louver and shutter/ guard etc. complete as required | 25.00 | Each |  | 2940.00 | 73500.00 | 2000.00 | 50000.00 | 1500.00 | 37500.00 | 37500.00 | SAURABH ENTERPRISES
5.02 | SITC of single phase 1400 RPM, 450 mm dia, sweep heavy exhaust fan with louver and shutter/ guard etc. complete as required | 25.00 | Each |  | 4560.00 | 114000.00 | 3400.00 | 85000.00 | 1500.00 | 37500.00 | 37500.00 | SAURABH ENTERPRISES
5.03 | SITC of single phase 1400 RPM, 600 mm dia, sweep heavy exhaust fan with louver and shutter/ guard etc. complete as required | 25.00 | Each |  | 9000.00 | 225000.00 | 8500.00 | 212500.00 | 1500.00 | 37500.00 | 37500.00 | SAURABH ENTERPRISES
6.00 | SITC of Wall Fans
6.01 | SITC of 300 mm dia, sweep wall fan oscillating type complete with built in spring type speed regulator and mounting arrangement. | 50.00 | Each |  | 2400.00 | 120000.00 | 1900.00 | 95000.00 | 1400.00 | 70000.00 | 70000.00 | SAURABH ENTERPRISES
6.02 | SITC of 450 mm dia, sweep wall fan oscillating type complete with built in spring type speed regulator and mounting arrangement. | 25.00 | Each |  | 3600.00 | 90000.00 | 2900.00 | 72500.00 | 4600.00 | 115000.00 | 72500.00 | Awasthi Electric Works
7.00 | SITC of storage type electric water heater, capacity 10 L, single phase, 230 V, 05 star (Similar to model Bianca, make Havells or equivalent ) | 10.00 | Each |  | 6000.00 | 60000.00 | 9500.00 | 95000.00 | 13000.00 | 130000.00 | 60000.00 | Ascent Electrification Engineers
8.00 | Supply and laying of following size of HDPE pipe PE-100, PN-10 at a depth of 1.2 mtr below the ground as per site condition incl. excavation and re-filing etc. complete as required.
8.01 | 25 mm | 500.00 | Mtr. |  | 127.00 | 63500.00 | 250.00 | 125000.00 | 70.00 | 35000.00 | 35000.00 | SAURABH ENTERPRISES
8.02 | 40 mm | 250.00 | Mtr. |  | 166.00 | 41500.00 | 300.00 | 75000.00 | 120.00 | 30000.00 | 30000.00 | SAURABH ENTERPRISES
9.00 | Supply of following sizes of Copper Power Cables, multi stranded conductor, XLPE Insulated, cores laid up, PVC tape/ Extruded Inner sheathed, Un Armoured or Armoured, FRLS at outer sheathed, 1100 V grade as per IS 7098 (Part 1) 1988.
9.01 | 3C x 4 sqmm cu armoured cable | 1000.00 | Mtr. |  | 159.00 | 159000.00 | 220.00 | 220000.00 | 315.00 | 315000.00 | 159000.00 | Ascent Electrification Engineers
9.02 | 3C x 2.5 sqmm cu armoured cable | 2500.00 | Mtr. |  | 110.00 | 275000.00 | 150.00 | 375000.00 | 215.00 | 537500.00 | 275000.00 | Ascent Electrification Engineers
9.03 | 3C x 1.5 sqmm cu armoured cable | 2500.00 | Mtr. |  | 77.00 | 192500.00 | 110.00 | 275000.00 | 170.00 | 425000.00 | 192500.00 | Ascent Electrification Engineers
9.04 | 3C x 6 sqmm cu unarmoured cable | 1500.00 | Mtr. |  | 213.00 | 319500.00 | 300.00 | 450000.00 | 400.00 | 600000.00 | 319500.00 | Ascent Electrification Engineers
9.05 | 3C x 4 sqmm cu unarmoured cable | 2500.00 | Mtr. |  | 144.00 | 360000.00 | 200.00 | 500000.00 | 280.00 | 700000.00 | 360000.00 | Ascent Electrification Engineers
9.06 | 4C x 6 sqmm cu unarmoured cable | 2500.00 | Mtr. |  | 262.00 | 655000.00 | 360.00 | 900000.00 | 490.00 | 1225000.00 | 655000.00 | Ascent Electrification Engineers
9.07 | 3C x 2.5 sqmm Cu Unarmoured cable | 2500.00 | Mtr. |  | 100.00 | 250000.00 | 140.00 | 350000.00 | 200.00 | 500000.00 | 250000.00 | Ascent Electrification Engineers
9.08 | 3C x 1.5 sqmm Cu Unarmoured cable | 1500.00 | Mtr. |  | 67.00 | 100500.00 | 90.00 | 135000.00 | 150.00 | 225000.00 | 100500.00 | Ascent Electrification Engineers
10.00 | Supply of following sizes of Armoured/ Unarmoured copper Power Cables, multi stranded conductor, XLPE Insulated, cores laid up, PVC tape/ Extruded Inner sheathed, FRLS at outer sheathed, 1100 V grade as per IS 7098 (Part 1) 1988.
10.01 | 1 Core 300 sqmm Cu UnArmoured XLPE Cable | 1500.00 | Mtr. |  | 3571.00 | 5356500.00 | 4690.00 | 7035000.00 | 6000.00 | 9000000.00 | 5356500.00 | Ascent Electrification Engineers
11.00 | Existing MRS HT panel extension work - Supply, Installation, Testing and Commissioning of indoor cubicle type floor mounted metal clad 33KV VCB Panel Board with additional incoming VCB of same rating in 6 panel board and additional out going VCB of same rating in 3 Panel board. CT ratio 200/5 with integral / separate floor rolling trolley for VCBs, horizontal draw out, horizontal/ vertical Isolation type breaker as per IS / IEC 62271-100 for breaker & 62271-200 for panels and of capacity as mentioned below, single break, trip free mechanism, motorised and manually operated spring assisted closing mechanism, emergency trip push button, interconnections, space heaters, copper earthing bus, auto, manual closing breaker suitable for use on 33kV 3 phase 50 Hz AC power supply with short circuit fault level of 1500 MVA complete with self contained short time current 26.3kA for 3 seconds, fully interlocked with close door operation and rear door interlock for enhanced safety, rack in and rack out mechanism, air insulated encapsulated/ pre-insulated copper bus bars, Breaker featured with mechanical ON/ OFF indication with hand trip device, breaker control TNC switch and all accessories such as spring release coil, shunt trip coil and auxiliary switch of 6 NO + 6 NC (minimum) and equipped with switchgears mentioned below. The Panels shall be tested for Internal Arc classification AFLR for 26.3kA for 1 second at individual compartments i.e. Busbar, VCB and Cable compartment. Panel Board shall be made out of 2 mm thick CRCA sheet steel/ Aluzinc material, totally enclosed, IP 4X, free standing, floor mounting, dust and vermin proof, indoor, compartmentalized, powder coated painting including internally wired/ interconnected with suitable provision for end termination of XLPE power cable with heat shrinkable jointing material etc. (Bottom entry) as required (Note cost of end termination not included in this item).
11.01 | A SITC of additional incoming VCB of same rating in 6 panel board. CT ratio 200/5. i 1 No. 1250 Amp, 33kV, 26.3 KA Vacuum Circuit Breaker with motorised and manual spring charged and auto, manual closing mechanism, shunt trip coil, closing coil, auxilary switch etc complete with all accessories. ii 3 Nos. Line PT 33KV/ √3, 110V/ √3, 100VA class 0.5 epoxy cast resin draw out type with backup PT fuses at Primary side and MCB at Secondary side. iii 3 Nos. Single Phase double core double ratio current transformer 100/100/ 5A/ 5A Amp, 15 VA epoxy cast insulated class of insulation class E, having accuracy class 0.5 for metering and 5P10 for protection. iv 1 Nos. Microprocessor based digital Numerical IDMT relay with 3 O/C and 1 E/F element with highset hand reset contacts & indicator (flag) for protection for O/C and E/F (O/C- setting 20-200% & E/F setting 10-80%) with communication facility RS485 port. v 1 No. microprocessor based digital UV/ OV relay with communication port RS485 vi 1 No. Anti Pumping Relay. vii 1 No.Trip circuit supervision Relay, viii 1 No. Master Trip Relay, ix 1 No. Circuit breaker control switch for electrical (T/N/C). x 1 Set. limit switch for test & service position. xi 1 No. 3 phase digital Voltmeter of class 0.5 to read (0-36KV) of size 96 x 96 sqmm with inbuilt selector switch. xii 1 No. 3 phase digital Ammeter of class 0.5 to read (0-100 Amp) of size 96 x 96 sqmm with inbuilt selector switch. xiii 1 No. Intelligent digital multi function meter of class 0.5 to read V, A, KVA, KW, KVAR, KWAH, KVAH, PF, Hz, maximum demand, THD and Individual order harmonics upto 31st order with communication facility (RS485 port) having LED/ LCD display, with 2 Amp protection MCB. xiv 1 No. Digital type Maximum Demand Indicator cum Controller. xv 1 Set LED type phase indications lamps for R,Y,B, Breaker ON, OFF, TRIP, Trip circuit healthy, spring charge etc. xvi 1 No. 8 Window Digital Annouciator xvii 3 Nos. 33 KV grade type 1 surge arrestors. B SITC of additional out going VCB of same rating in 3 Panel board. CT ratio 200/5. i 1 No. 1250 Amp, 33KV, 26.3 KA Vacuum Circuit Breaker with motorised and manual spring charged and auto, manual closing mechanism, shunt trip coil, closing coil, auxilary switch etc. complete with all accessories. ii 3 No. Single Phase double core double ratio current transformer of suitable ratio as per requirement, 15 VA epoxy cast insulated class of insulation class E, having accuracy class 0.5 for metering and 5P10 for protection. iii 1 no. microprocessor based numerical relay with 3 O/L, E/F and S/C protection with communication port RS 485. iv 1 No. Anti Pumping Relay. v 1 No. Circuit breaker control switch for electrical (T/N/C). vi 1 Set. limit switch for test & service position. vii 1 No. 3 phase digital Ammeter of class 0.5 (96mm square) with inbuilt selector switch viii 1 No. Intelligent digital multi function meter of class 0.5 to read V, A, KVA, KW, KVAR, KWAH, KVAH, PF, Hz, maximum demand, THD and Individual order harmonics upto 31st order with communication facility (RS485 port) having LED/ LCD display with required Nos of CTs, with 2 Amp protection MCB. ix 1 No. Maximum Demand Indicator cum Controller x 1 Set LED type indications lamps for Breaker ON, OFF, TRIP, Trip circuit healthy, spring charge etc. xi 1 No. Trip circuit supervision Relay xii 1 No. Master Trip Relay xiii 1 No. 8 window Digital Annouciator xiv 1 No. auxilary relay C OTHER ACCESSORIES i 230 V AC Space Heater controlled with thermostat with protection MCB in each breaker compartment ii Panel Illumination Lamp, LED type, 230V AC iii 6 Amp, 230 V AC power socket with switch in each breaker control compartment. iv Common Buzzer, 230V AC v Emergency push button for each breaker vi All metering and protection devices, interconnections, necessary control wiring and all other accessories shall be provided as per Technical specifications & technical particulars. | 1.00 | Job |  | 8640000.00 | 8640000.00 | 3545000.00 | 3545000.00 | 976111.00 | 976111.00 | 976111.00 | SAURABH ENTERPRISES
12.00 | SITC of 33 kV Outdoor HT metering panel cubicle with kiosk, made out of 2 mm thickness CRCA sheet steel with RAL 7032 siemens gray color along with base frame, Cable entry Top/ bottom, Gland plate 3mm, Base channel minimum 75x40x6 mm ISMC, base frame - Black in color, Aluminimum Bus bar, minimum 50x10 mm, minimum current rating 320 A, Cu Earth Bus bar minimum 50x6 mm, 33 kV indoor resin cast current transformer 100/1A, 0.2S, 5VA- 3 nos, 33 kV indoor resin voltage transformer Fixed type, 33 kV/1.732/110V/1.732 0.2, 10 VA- 3 nos., 33 kV Epoxy resin cast insulators, Thermostart, Space heater etc. complete as required as per site requirement. | 1.00 | Job |  | 498000.00 | 498000.00 | 375000.00 | 375000.00 | 200000.00 | 200000.00 | 200000.00 | SAURABH ENTERPRISES
| Total in Figures |  |  |  |  | 24776560.00 |  | 23468750.00 |  | 18711111.00
Lowest Amount Quoted BY: SAURABH ENTERPRISES(18711111.00)

## BOQ Summary
BOQ Summary Details Tender Title: Construction of New Terminal Building and Other Allied structures Phase I II at Patna Airport SH Miscellaneous Internal External Electrical works at JPNI Airport Patna Tender ID: 2025_AAI_251898_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | SAURABH ENTERPRISES (BID ID -921844) | 18711111.00 | L1
| 2 | Awasthi Electric Works (BID ID -923262) | 23468750.00 | L2
| 3 | Ascent Electrification Engineers (BID ID -923173) | 24776560.00 | L3