## BoQ1
Government eProcurement System Created By: Shridhar Gupta Created Date/Time: 11-Nov-2025 12:47 PM Tender Title: Construction of New Terminal Building and Other Allied structures Phase I and II at Patna Airport SH Provision of Aerosol Based Green Gas based Fire Suppression System for DG Generators Sets Tender ID: 2025_AAI_251925_1
Tender Inviting Authority: AIRPORTS AUTHORITY OF INDIA
Name of Work:Construction of New Domestic Terminal Building and other allied structures (Phase I & II) at Patna Airport . SH : Provision of Aerosole Based Green Gas based Fire Suppression System for DG Generators Sets.
Contract No:
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Vrinda Nano Technologies Pvt Ltd (GSTN-06AABCV6699N1ZG) BID ID -921526 |  | Nexpo Power Solutions Private Limited (GSTN-NA) BID ID -919806
[5 empty] | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | AEROSOL BASED AUTOMATIC FIRE SUPPRESSION SYSTEM
1.01 | SITC of Aerosol Generator having aerosol mass of 1500gm shall be electrically actuated by means of Fire Alarm cum Release Panel. The housing shall be constructed of stainless steel shell.Housing shall be sealed with a non permeable membrane. Units shall have passed salt spray corrosion testing per UL Standard 2127 and having UL/EN/VDS as part of their listing. Aerosol generated shall be potassium based. Agent shall have no ozone depletion potential and no global warming potential. Agent shall be listed by the US EPA under the SNAP program. Aerosol generators shall be listed by Underwriter’s Laboratories (UL) to UL Subject 2775 covering Fixed Condensed Aerosol Systems per NFPA 2010. UL approved design density of the aerosol should be less than 100g/cu.mtr for Class A, B & C fires as per NFPA. The Aerosol generator should have self life of 15 years. Aerosol generator shall be supplied with Stainless steel Bracket & Gland. DG SET | 4.00 | SET |  | 310000.00 | 1240000.00 | 227650.00 | 910600.00 | 910600.00 | Nexpo Power Solutions Private Limited
1.02 | SITC of Aerosol Generator having aerosol mass of 2500gm shall be electrically actuated by means of Fire Alarm cum Release Panel. The housing shall be constructed of stainless steel shell.Housing shall be sealed with a non permeable membrane. Units shall have passed salt spray corrosion testing per UL Standard 2127 and having UL/EN/VDS as part of their listing. Aerosol generated shall be potassium based. Agent shall have no ozone depletion potential and no global warming potential. Agent shall be listed by the US EPA under the SNAP program. Aerosol generators shall be listed by Underwriter’s Laboratories (UL) to UL Subject 2775 covering Fixed Condensed Aerosol Systems per NFPA 2010. UL approved design density of the aerosol should be less than 100g/cu.mtr for Class A, B & C fires as per NFPA. The Aerosol generator should have self life of 15 years. Aerosol generator shall be supplied with Stainless steel Bracket & Gland. DG SET | 15.00 | SET |  | 368507.00 | 5527605.00 | 350000.00 | 5250000.00 | 5250000.00 | Nexpo Power Solutions Private Limited
1.03 | Supply, Installation & testing of First Responder The unit housing shall be constructed of metal and incorporate insulating/cooling material. Discharge ports for agent release shall be located around the circumference of the housing. Housing shall accept a M201 specification MIL-DTL-51353 certificate for purpose modified grenade type fuze initiator and shall be non-pressurized prior to system activation. Initiator and CSIRO Activefire certification. The initiator shall be subject to 100% inspection by means of x-ray. Safety. Units shall incorporate dual safety devices – a crimped safety pin which is withdrawn by means of a pull ring, and a safety clip which locks the pull ring and requires that the pull ring be twisted to allow the pull ring to withdraw the safety pin. The initiator shall incorporate a minimum 3.5 second delay timer prior to activation. Aerosol Agent. Aerosol generated shall be potassium based and shall have no ozone depletion potential and no global warming potential. Agent shall be approved for commercial sale by the US EPA. Dimensions. Unit shall contain 500 grams of aerosol forming composition and shall be of nominal dimensions 5.7 inches tall (7.0 including initiator mechanism) with a body diameter of 3.19 inches. | 5.00 | Set |  | 165000.00 | 825000.00 | 275000.00 | 1375000.00 | 825000.00 | Vrinda Nano Technologies Pvt Ltd
2.00 | GAS RELEASE AND FIRE DETECTION SYSTEM
2.01 | Design, Supply, Installation, Testing and Commissioning of UL listed Digital Linear Heat Detection System to protect the DG sets with an inbuilt monitoring system having twin-conductor switching heat sensing conductors, effective monitoring at precise point of risk and having 5 detection temprature ranges. The detection can identify the exact location and can be resettable features from local control panel and may have provision for fire alarm integration along with all necessary accessories. | 5.00 | No's. |  | 257500.00 | 1287500.00 | 223850.00 | 1119250.00 | 1119250.00 | Nexpo Power Solutions Private Limited
2.02 | Supply, installation testing & commissioning of Conventional agent release control panel with battery back up for 30 minutes in alarm condition having UL Certified approval. Panel shall be of zones with necessary manual release switch, zone indication, fault indication, alarm display. Quoted rate shall include necessary battery & interconnections. | 5.00 | No's. |  | 185000.00 | 925000.00 | 155350.00 | 776750.00 | 776750.00 | Nexpo Power Solutions Private Limited
2.03 | Supply, installation, testing & commissioning of CE Listed Conventional Sounder cum strobe with 24V DC, Audiable Sound 75 db @ 1 mtr range (16 V DC). It is used for Fire, Burglar & Emergency Alarm System, Low current consume @ 47 -73 mA Candela: flashing every second, 4 candela settings:15/30/75/110cd output and 2 different tone audiable sound. | 5.00 | No's. |  | 22500.00 | 112500.00 | 17500.00 | 87500.00 | 87500.00 | Nexpo Power Solutions Private Limited
2.04 | Supply and Laying of 2C X 1.5 sq. mm. FRLS armored Cable with accessories Llike juction boxes, shaddle, clamp, screws etc. | 250.00 | Mtr. |  | 250.00 | 62500.00 | 350.00 | 87500.00 | 62500.00 | Vrinda Nano Technologies Pvt Ltd
| Total in Figures |  |  |  |  | 9980105.00 |  | 9606600.00
Lowest Amount Quoted BY: Nexpo Power Solutions Private Limited(9606600.00)

## BOQ Summary
BOQ Summary Details Tender Title: Construction of New Terminal Building and Other Allied structures Phase I and II at Patna Airport SH Provision of Aerosol Based Green Gas based Fire Suppression System for DG Generators Sets Tender ID: 2025_AAI_251925_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Nexpo Power Solutions Private Limited (BID ID -919806) | 9606600.00 | L1
| 2 | Vrinda Nano Technologies Pvt Ltd (BID ID -921526) | 9980105.00 | L2