## BoQ1
Government eProcurement System Created By: Amitabh Ranjan Created Date/Time: 27-Nov-2025 05:51 PM Tender Title: Upgradation of low side HVAC system at Amritsar Airport Tender ID: 2025_AAI_251964_1
Tender Inviting Authority: <DGM Engg (Elect), Airports Authority of India, Sri Guru Ram Dass Jee, International Airport, Amritsar - 143101>
Name of Work: <Upgradation of low side HVAC system at Amritsar Airport.>
Contract No: <AAI/ASR/ENGG-ELECT/eNIT-07/2025-26>
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | SNOWMEX ENGINEERS LIMITED (GSTN-07AAMCS8717P1ZF) BID ID -920434 |  | BRITE INDUSTRIES (GSTN-27AAKFM6551E1Z6) BID ID -920670 |  | Ingenious Industries (GSTN-27AADFI4734Q1ZV) BID ID -921675 |  | Skyline Airconditioning Engineers Pvt. Ltd. (GSTN-09AAKCS1530L1Z4) BID ID -921994 |  | Arctic Engineering Services (GSTN-07AAWFA5497P1ZA) BID ID -922055 |  | Mvac Engineers (GSTN-NA) BID ID -921651 |  | Powermech Services Private Limited (GSTN-NA) BID ID -920214 |  | Blue Star Ltd (GSTN-NA) BID ID -919445
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply, Installation, Testing and commissioning of factory built floor mounted chilled water double skin type horizontal air handling unit (for chilled water centralised AC plant) made of 25 mm thick panels consisting of pre plasctized G.I. casing of thickness 0.8 mm outside layer and 0.8 mm inside layer with polyurethane foam (PUF) insulation factory injected between them by injection moulding machine, complete with blower section with blower suitable for static pressure as required, minimum 2 bend GSS/PVC eliminators, cooling coil section with aluminium finned copper tubes (tube thickness not less than 0.5 mm) cooling coil of following row deep, filter section with 50 mm thick metal viscous/ washable synthetic type air prefilters, belt drive package with TEFC drive motor of efficiency class IE 3 suitable for 415 ± 10 % volts, 50 Hz , 3 Phase AC supply suitably designed for variable frequency drive applications, drain connections, stainless steel (18 G) drain pan with PUF insulation, 150 mm dia. dial type pressure guages (2 nos.) and industrial type thermometers (2 nos.) at the inlet and outlet of coil, auto purge valve wherever required, necessary vibration isolation arrangement etc. complete as per specifications and of following capacities.
1.01 | 40900 CFM (8 Row deep) | 1.00 | Nos. |  | 1355000.00 | 1355000.00 | 1210000.00 | 1210000.00 | 1259940.00 | 1259940.00 | 1250000.00 | 1250000.00 | 1236000.00 | 1236000.00 | 1213390.00 | 1213390.00 | 989534.00 | 989534.00 | 1146280.00 | 1146280.00 | 989534.00 | Powermech Services Private Limited
1.02 | 39300 CFM (8 Row deep) | 1.00 | Nos. |  | 1285000.00 | 1285000.00 | 1100000.00 | 1100000.00 | 1197702.00 | 1197702.00 | 1200000.00 | 1200000.00 | 1177500.00 | 1177500.00 | 1165930.00 | 1165930.00 | 970529.00 | 970529.00 | 1100790.00 | 1100790.00 | 970529.00 | Powermech Services Private Limited
1.03 | 30950 CFM (8 Row deep) | 1.00 | Nos. |  | 1025000.00 | 1025000.00 | 900000.00 | 900000.00 | 952683.00 | 952683.00 | 1050000.00 | 1050000.00 | 930000.00 | 930000.00 | 918200.00 | 918200.00 | 742805.00 | 742805.00 | 857120.00 | 857120.00 | 742805.00 | Powermech Services Private Limited
1.04 | 29623 CFM (8 Row deep) | 1.00 | Nos. |  | 985000.00 | 985000.00 | 850000.00 | 850000.00 | 920460.00 | 920460.00 | 1025000.00 | 1025000.00 | 898000.00 | 898000.00 | 878840.00 | 878840.00 | 727008.00 | 727008.00 | 822385.00 | 822385.00 | 727008.00 | Powermech Services Private Limited
1.05 | 35000 CFM (6 Row deep) | 2.00 | Nos. |  | 1015000.00 | 2030000.00 | 1000000.00 | 2000000.00 | 973452.00 | 1946904.00 | 1040000.00 | 2080000.00 | 951000.00 | 1902000.00 | 860560.00 | 1721120.00 | 810462.00 | 1620924.00 | 960475.00 | 1920950.00 | 1620924.00 | Powermech Services Private Limited
1.06 | 31700 CFM (6 Row deep) | 1.00 | Nos. |  | 975000.00 | 975000.00 | 910000.00 | 910000.00 | 840765.00 | 840765.00 | 945000.00 | 945000.00 | 817000.00 | 817000.00 | 779420.00 | 779420.00 | 685365.00 | 685365.00 | 870290.00 | 870290.00 | 685365.00 | Powermech Services Private Limited
1.07 | 31500 CFM (6 Row deep) | 1.00 | Nos. |  | 895000.00 | 895000.00 | 915000.00 | 915000.00 | 838350.00 | 838350.00 | 942000.00 | 942000.00 | 842000.00 | 842000.00 | 774500.00 | 774500.00 | 683456.00 | 683456.00 | 870290.00 | 870290.00 | 683456.00 | Powermech Services Private Limited
1.08 | 30700 CFM (6 Row deep) | 2.00 | Nos. |  | 875000.00 | 1750000.00 | 901000.00 | 1802000.00 | 828690.00 | 1657380.00 | 845000.00 | 1690000.00 | 832000.00 | 1664000.00 | 754830.00 | 1509660.00 | 662728.00 | 1325456.00 | 850820.00 | 1701640.00 | 1325456.00 | Powermech Services Private Limited
1.09 | 23700 CFM (6 Row deep) | 1.00 | Nos. |  | 685000.00 | 685000.00 | 721000.00 | 721000.00 | 638112.00 | 638112.00 | 650000.00 | 650000.00 | 663500.00 | 663500.00 | 582720.00 | 582720.00 | 538736.00 | 538736.00 | 696670.00 | 696670.00 | 538736.00 | Powermech Services Private Limited
1.10 | 18500 CFM (6 Row deep) | 1.00 | Nos. |  | 585000.00 | 585000.00 | 600000.00 | 600000.00 | 528264.00 | 528264.00 | 498000.00 | 498000.00 | 520000.00 | 520000.00 | 478830.00 | 478830.00 | 445966.00 | 445966.00 | 570335.00 | 570335.00 | 445966.00 | Powermech Services Private Limited
1.11 | 12000 CFM (6 Row deep) | 2.00 | Nos. |  | 390000.00 | 780000.00 | 310000.00 | 620000.00 | 347484.00 | 694968.00 | 375000.00 | 750000.00 | 307000.00 | 614000.00 | 310600.00 | 621200.00 | 287537.00 | 575074.00 | 353015.00 | 706030.00 | 575074.00 | Powermech Services Private Limited
1.12 | 5000 CFM (6 Row deep) | 1.00 | Nos. |  | 202800.00 | 202800.00 | 190000.00 | 190000.00 | 181608.00 | 181608.00 | 200000.00 | 200000.00 | 164000.00 | 164000.00 | 152660.00 | 152660.00 | 160004.00 | 160004.00 | 183985.00 | 183985.00 | 152660.00 | Mvac Engineers
2.00 | Supply, Installation, Testing and commissioning of factory built floor mounted chilled water double skin type Vertical type air handling unit (for chilled water centralized AC plant) made of 43± 2 mm thick panels consisting of Pre-coated G.I. Sheet casing of thickness 0.6 mm outside layer and 0.6 mm inside layer with polyurethane foam (PUF) insulation factory injected between them by injection molding machine with 40±2 kg /M³ of density , complete with blower section with blower suitable for static pressure as required, cooling coil section with aluminum finned copper tubes (tube thickness not less than 0.41 mm) cooling coil of following row deep, filter section with 50 mm thick metal viscous/ washable synthetic type Pre filters having efficiency 90% down to 10 micron, belt drive package with TEFC drive motor of efficiency class IE 3 suitable for 415 ± 10 % volts, 50 Hz , 3 Phase AC supply suitably designed for variable frequency drive applications, drain connections, stainless steel (18 G) drain pan with PUF insulation, vibration isolation arrangement etc. complete as per specifications and of following capacities.AHU Coil shall be AHRI Certified. Bidder has to submit the AHRI certificate along with technical data sheet approval. AHU Motor & blower shall be compatible to operate with VFD. Outlet velocity of air should not be more than 9.26 m/s.The Face velocity of coils should not be more than 500 . AHU should have protection like Limit Switch, Door Lamp, Inspection Glass etc.
2.10 | 10000 CFM (6 Row deep) Vertical | 4.00 | Nos. |  | 316800.00 | 1267200.00 | 310000.00 | 1240000.00 | 291663.00 | 1166652.00 | 300000.00 | 1200000.00 | 263000.00 | 1052000.00 | 278130.00 | 1112520.00 | 234805.00 | 939220.00 | 354010.00 | 1416040.00 | 939220.00 | Powermech Services Private Limited
3.00 | Supply, installation, balancing and commissioning of fabricated at site/factory GSS sheet metal rectangular/round ducting complete with neoprene rubber gaskets, elbows, splitter dampers, vanes, hangers, supports etc. as per approved drawings and specifications of following sheet thickness complete as required.
3.10 | Thickness 0.63 mm sheet | 200.00 | SqM |  | 926.00 | 185200.00 | 950.00 | 190000.00 | 820.00 | 164000.00 | 1000.00 | 200000.00 | 1030.00 | 206000.00 | 970.00 | 194000.00 | 1087.00 | 217400.00 | 650.00 | 130000.00 | 130000.00 | Blue Star Ltd
3.20 | Thickness 0.80 mm sheet | 120.00 | SqM |  | 1025.00 | 123000.00 | 1050.00 | 126000.00 | 910.00 | 109200.00 | 1400.00 | 168000.00 | 1150.00 | 138000.00 | 1110.00 | 133200.00 | 1274.00 | 152880.00 | 825.00 | 99000.00 | 99000.00 | Blue Star Ltd
3.30 | Thickness 1.00 mm sheet | 110.00 | SqM |  | 300.00 | 33000.00 | 1250.00 | 137500.00 | 1300.00 | 143000.00 | 2000.00 | 220000.00 | 1480.00 | 162800.00 | 1260.00 | 138600.00 | 1467.00 | 161370.00 | 165.00 | 18150.00 | 18150.00 | Blue Star Ltd
3.40 | Thickness 1.25 mm sheet | 90.00 | SqM |  | 400.00 | 36000.00 | 1400.00 | 126000.00 | 1600.00 | 144000.00 | 2100.00 | 189000.00 | 1600.00 | 144000.00 | 1460.00 | 131400.00 | 1685.00 | 151650.00 | 170.00 | 15300.00 | 15300.00 | Blue Star Ltd
4.00 | Supply, fixing, testing and commissioning of following insulated valves as per specification
4.10 | Butterfly valve (Manual) with C I body SS Disc, Nitrile Rubber Seal & O- Ring PN 16 pressure rating for chilled water/hot eater circulation as specified.
4.11 | 32 mm dia. | 2.00 | No. |  | 150.00 | 300.00 | 1695.00 | 3390.00 | 2400.00 | 4800.00 | 1500.00 | 3000.00 | 3125.00 | 6250.00 | 2700.00 | 5400.00 | 3482.00 | 6964.00 | 2070.00 | 4140.00 | 300.00 | SNOWMEX ENGINEERS LIMITED
4.12 | 65 mm dia. | 4.00 | No. |  | 100.00 | 400.00 | 2244.00 | 8976.00 | 2340.00 | 9360.00 | 3000.00 | 12000.00 | 4045.00 | 16180.00 | 3870.00 | 15480.00 | 6713.00 | 26852.00 | 3020.00 | 12080.00 | 400.00 | SNOWMEX ENGINEERS LIMITED
4.13 | 80 mm dia. | 12.00 | No. |  | 3650.00 | 43800.00 | 2490.00 | 29880.00 | 2688.00 | 32256.00 | 3500.00 | 42000.00 | 4325.00 | 51900.00 | 4440.00 | 53280.00 | 8020.00 | 96240.00 | 3395.00 | 40740.00 | 29880.00 | BRITE INDUSTRIES
4.14 | 100 mm dia. | 20.00 | No. |  | 5650.00 | 113000.00 | 2960.00 | 59200.00 | 3580.80 | 71616.00 | 5000.00 | 100000.00 | 5930.00 | 118600.00 | 5490.00 | 109800.00 | 10263.00 | 205260.00 | 4425.00 | 88500.00 | 59200.00 | BRITE INDUSTRIES
4.20 | Balancing valve with built in measuring facility with C I body flanged construction with EPDM coated disc with long pitch with protected out pipe insulation & PN 16 pressure rating for chilled / hot water circulation as specified.
4.21 | 32 mm dia. | 1.00 | No. |  | 150.00 | 150.00 | 4590.00 | 4590.00 | 5640.00 | 5640.00 | 2500.00 | 2500.00 | 6800.00 | 6800.00 | 4040.00 | 4040.00 | 8265.00 | 8265.00 | 4830.00 | 4830.00 | 150.00 | SNOWMEX ENGINEERS LIMITED
4.22 | 65 mm dia. | 2.00 | No. |  | 150.00 | 300.00 | 8010.00 | 16020.00 | 7800.00 | 15600.00 | 5500.00 | 11000.00 | 11000.00 | 22000.00 | 9250.00 | 18500.00 | 12326.00 | 24652.00 | 8700.00 | 17400.00 | 300.00 | SNOWMEX ENGINEERS LIMITED
4.23 | 80 mm dia. | 6.00 | No. |  | 13500.00 | 81000.00 | 9128.00 | 54768.00 | 8634.00 | 51804.00 | 8500.00 | 51000.00 | 12295.00 | 73770.00 | 10600.00 | 63600.00 | 20661.00 | 123966.00 | 10010.00 | 60060.00 | 51000.00 | Skyline Airconditioning Engineers Pvt. Ltd.
4.24 | 100 mm dia. | 10.00 | No. |  | 23500.00 | 235000.00 | 12000.00 | 120000.00 | 12362.40 | 123624.00 | 12500.00 | 125000.00 | 17755.00 | 177550.00 | 14600.00 | 146000.00 | 28901.00 | 289010.00 | 14200.00 | 142000.00 | 120000.00 | BRITE INDUSTRIES
4.30 | 3 way motorized valve, CI body, brass seating, S.S 304 spindle, spring loaded packing with teflon rings and rubber seal, PN-16 rating and flange end connection max temperature 90°C with 24V AC/DC linear motion electric actuator, IP-64 rated.
4.31 | 32 mm dia. | 1.00 | No. |  | 150.00 | 150.00 | 13000.00 | 13000.00 | 27956.00 | 27956.00 | 6500.00 | 6500.00 | 22500.00 | 22500.00 | 9910.00 | 9910.00 | 14968.00 | 14968.00 | 9245.00 | 9245.00 | 150.00 | SNOWMEX ENGINEERS LIMITED
4.32 | 65 mm dia. | 2.00 | No. |  | 150.00 | 300.00 | 23000.00 | 46000.00 | 52269.00 | 104538.00 | 8500.00 | 17000.00 | 39500.00 | 79000.00 | 19480.00 | 38960.00 | 21381.00 | 42762.00 | 21010.00 | 42020.00 | 300.00 | SNOWMEX ENGINEERS LIMITED
4.33 | 80 mm dia. | 6.00 | No. |  | 35220.00 | 211320.00 | 28000.00 | 168000.00 | 59993.00 | 359958.00 | 15000.00 | 90000.00 | 46500.00 | 279000.00 | 25890.00 | 155340.00 | 30952.00 | 185712.00 | 26240.00 | 157440.00 | 90000.00 | Skyline Airconditioning Engineers Pvt. Ltd.
4.34 | 100 mm dia. | 10.00 | No. |  | 41510.00 | 415100.00 | 33000.00 | 330000.00 | 68862.00 | 688620.00 | 25000.00 | 250000.00 | 83500.00 | 835000.00 | 31360.00 | 313600.00 | 39841.00 | 398410.00 | 32180.00 | 321800.00 | 250000.00 | Skyline Airconditioning Engineers Pvt. Ltd.
4.40 | Y - Strainer of ductile CI Body flanged ends with stainless steel strainer for chilled/ hot water circulation including insulation as specified.
4.41 | 32 mm dia. | 1.00 | No. |  | 100.00 | 100.00 | 2400.00 | 2400.00 | 2760.00 | 2760.00 | 2500.00 | 2500.00 | 3930.00 | 3930.00 | 2660.00 | 2660.00 | 7433.00 | 7433.00 | 1600.00 | 1600.00 | 100.00 | SNOWMEX ENGINEERS LIMITED
4.42 | 65 mm dia. | 2.00 | No. |  | 100.00 | 200.00 | 3600.00 | 7200.00 | 4025.00 | 8050.00 | 4800.00 | 9600.00 | 7110.00 | 14220.00 | 5770.00 | 11540.00 | 10715.00 | 21430.00 | 4050.00 | 8100.00 | 200.00 | SNOWMEX ENGINEERS LIMITED
4.43 | 80 mm dia. | 6.00 | No. |  | 8150.00 | 48900.00 | 4700.00 | 28200.00 | 4418.00 | 26508.00 | 6500.00 | 39000.00 | 8825.00 | 52950.00 | 6740.00 | 40440.00 | 14680.00 | 88080.00 | 5270.00 | 31620.00 | 26508.00 | Ingenious Industries
4.44 | 100 mm dia. | 10.00 | No. |  | 9150.00 | 91500.00 | 6500.00 | 65000.00 | 6057.00 | 60570.00 | 8500.00 | 85000.00 | 13115.00 | 131150.00 | 7990.00 | 79900.00 | 20697.00 | 206970.00 | 7290.00 | 72900.00 | 60570.00 | Ingenious Industries
5.00 | Supplying, fixing, testing and commissioning of fire dampers in supply air duct / main branch and return air path as and where required of required sizes i/c control wiring. The damper shall be motorized and spring return so as to close the damper in the event of power failure automatically and open the same in case of power being restored. The spring return action shall be inbuilt mechanism and not externally mounted. The damper shall also be closed in the event of fire signal complete as requried and as per specifications.
5.10 | Fire damper | 30.00 | SqM |  | 7800.00 | 234000.00 | 8000.00 | 240000.00 | 7981.00 | 239430.00 | 8500.00 | 255000.00 | 9515.00 | 285450.00 | 9700.00 | 291000.00 | 11713.00 | 351390.00 | 8755.00 | 262650.00 | 234000.00 | SNOWMEX ENGINEERS LIMITED
5.20 | Actuator | 19.00 | No. |  | 9500.00 | 180500.00 | 7840.00 | 148960.00 | 8395.00 | 159505.00 | 10500.00 | 199500.00 | 14500.00 | 275500.00 | 8400.00 | 159600.00 | 11205.00 | 212895.00 | 10005.00 | 190095.00 | 148960.00 | BRITE INDUSTRIES
6.00 | Supply & Fixing of new waterproof/fire retardant canvass connection for new AHUs complete with GI frame and hardware. | 15.00 | No. |  | 4500.00 | 67500.00 | 3360.00 | 50400.00 | 8000.00 | 120000.00 | 1000.00 | 15000.00 | 5000.00 | 75000.00 | 1540.00 | 23100.00 | 18285.00 | 274275.00 | 2000.00 | 30000.00 | 15000.00 | Skyline Airconditioning Engineers Pvt. Ltd.
7.00 | SITC of 15mm Automatic Air purge valve. | 19.00 | Each |  | 1320.00 | 25080.00 | 495.00 | 9405.00 | 750.00 | 14250.00 | 1500.00 | 28500.00 | 2965.00 | 56335.00 | 700.00 | 13300.00 | 795.00 | 15105.00 | 570.00 | 10830.00 | 9405.00 | BRITE INDUSTRIES
8.00 | SITC of 15mm Ball Valve. | 38.00 | Each |  | 1483.00 | 56354.00 | 299.00 | 11362.00 | 990.00 | 37620.00 | 1000.00 | 38000.00 | 1060.00 | 40280.00 | 530.00 | 20140.00 | 689.00 | 26182.00 | 390.00 | 14820.00 | 11362.00 | BRITE INDUSTRIES
9.00 | SITC of Dial type pressure gauge along with the syphon tube and ball cock. | 38.00 | Each |  | 1050.00 | 39900.00 | 1456.00 | 55328.00 | 2450.00 | 93100.00 | 1000.00 | 38000.00 | 2245.00 | 85310.00 | 1160.00 | 44080.00 | 1166.00 | 44308.00 | 940.00 | 35720.00 | 35720.00 | Blue Star Ltd
10.00 | SITC of mercury-in glass thermometer. | 38.00 | Each |  | 1050.00 | 39900.00 | 1680.00 | 63840.00 | 2450.00 | 93100.00 | 1500.00 | 57000.00 | 890.00 | 33820.00 | 710.00 | 26980.00 | 689.00 | 26182.00 | 440.00 | 16720.00 | 16720.00 | Blue Star Ltd
11.00 | Supply and Installation testing of Digital thermostat for AHU's Temperature control. | 19.00 | Each |  | 3150.00 | 59850.00 | 4032.00 | 76608.00 | 6500.00 | 123500.00 | 2500.00 | 47500.00 | 4800.00 | 91200.00 | 2450.00 | 46550.00 | 4505.00 | 85595.00 | 3880.00 | 73720.00 | 46550.00 | Mvac Engineers
12.00 | Supply, laying , connecting , fixing and testing of Chilled water MS ERW class "C" pipe complete with all fitting duly insulated as mentioned their in for closed cell elastomeric insulation 30 to 40 kg /cum density & 26 G Aluminum cladding laid underground / floor etc complete all as specified and directed for the following pipes : -
12.10 | 150 mm - 32 mm thick insulation | 42.00 | Each |  | 700.00 | 29400.00 | 3240.00 | 136080.00 | 4616.00 | 193872.00 | 100.00 | 4200.00 | 3820.00 | 160440.00 | 3370.00 | 141540.00 | 4057.00 | 170394.00 | 500.00 | 21000.00 | 4200.00 | Skyline Airconditioning Engineers Pvt. Ltd.
12.20 | 125 mm - 32 mm thick insulation | 36.00 | Each |  | 650.00 | 23400.00 | 2760.00 | 99360.00 | 3718.00 | 133848.00 | 75.00 | 2700.00 | 3340.00 | 120240.00 | 2900.00 | 104400.00 | 3475.00 | 125100.00 | 425.00 | 15300.00 | 2700.00 | Skyline Airconditioning Engineers Pvt. Ltd.
12.30 | 100 mm - 25 mm thick insulation | 580.00 | Each |  | 2271.00 | 1317180.00 | 2280.00 | 1322400.00 | 3100.00 | 1798000.00 | 50.00 | 29000.00 | 2660.00 | 1542800.00 | 2390.00 | 1386200.00 | 2635.00 | 1528300.00 | 330.00 | 191400.00 | 29000.00 | Skyline Airconditioning Engineers Pvt. Ltd.
12.40 | 80 mm - 25 mm thick insulation | 108.00 | Each |  | 1563.00 | 168804.00 | 1750.00 | 189000.00 | 2354.00 | 254232.00 | 100.00 | 10800.00 | 1990.00 | 214920.00 | 1880.00 | 203040.00 | 2289.00 | 247212.00 | 1910.00 | 206280.00 | 10800.00 | Skyline Airconditioning Engineers Pvt. Ltd.
12.50 | 65 mm - 25 mm thick insulation | 36.00 | Each |  | 960.00 | 34560.00 | 1460.00 | 52560.00 | 2008.00 | 72288.00 | 75.00 | 2700.00 | 1600.00 | 57600.00 | 1600.00 | 57600.00 | 2051.00 | 73836.00 | 1555.00 | 55980.00 | 2700.00 | Skyline Airconditioning Engineers Pvt. Ltd.
12.60 | 32 mm - 25 mm thick insulation | 18.00 | Each |  | 150.00 | 2700.00 | 860.00 | 15480.00 | 1117.00 | 20106.00 | 50.00 | 900.00 | 935.00 | 16830.00 | 960.00 | 17280.00 | 1535.00 | 27630.00 | 3225.00 | 58050.00 | 900.00 | Skyline Airconditioning Engineers Pvt. Ltd.
13.00 | Supply, laying and fixing of drain pipe of GI Tubing Medium grade with all fittings for cable protection laid in trenches or fixed to wall / laid in flooring, complete all as specified and directed.
13.10 | 25 mm | 108.00 | Each |  | 450.00 | 48600.00 | 210.00 | 22680.00 | 380.00 | 41040.00 | 1250.00 | 135000.00 | 325.00 | 35100.00 | 370.00 | 39960.00 | 237.00 | 25596.00 | 370.00 | 39960.00 | 22680.00 | BRITE INDUSTRIES
13.20 | 32 mm | 78.00 | Each |  | 250.00 | 19500.00 | 250.00 | 19500.00 | 485.00 | 37830.00 | 2800.00 | 218400.00 | 425.00 | 33150.00 | 440.00 | 34320.00 | 358.00 | 27924.00 | 470.00 | 36660.00 | 19500.00 | SNOWMEX ENGINEERS LIMITED, BRITE INDUSTRIES
14.00 | Supply & Fixing of closed cell elastomeric nitrile rubber having thermal conductivity not exceeding 0.037 W/mK at mean temperature of 20° C as per EN 12667, moisture diffusion resistance factor or ‘µ’ value of minimum 7,000 for base insulation material without the foil as per EN 12086, fire performance such that it passes Class" O" as per BS476 Part 7 for surface spread of flame , density without the foil between 40 to 55 kg/cum. The insulation material shall be dust & fibre free. The Aluminum foil shall be 60 microns thick and its weight shall be 193 gsm as per EN ISO 2286-2, tensile strength 90 N / 15 mm as per EN ISO 527-3 with elongation > 10% as per EN ISO 527-3, complete for following thickness of insulation all as specified and directed.
14.10 | 19 mm thick thermal insulation | 400.00 | Sqmtr |  | 850.00 | 340000.00 | 500.00 | 200000.00 | 672.00 | 268800.00 | 700.00 | 280000.00 | 675.00 | 270000.00 | 600.00 | 240000.00 | 777.00 | 310800.00 | 175.00 | 70000.00 | 70000.00 | Blue Star Ltd
15.00 | Supply, Installation, Testing and Commissioning of Acoustic lining inside ducts/plenum using open cell nitrile rubber foam having micro-ban anti- microbial/ anti fungal product protection and of 160-180 kg / m³ density as per ASTM D3575, class 1 rating As per BS476,PART-7, cut to required sizes and to be stuck to the inside of duct surfaces with adhesive as approved by the manufacturer. (Rubber based solvent). as per specifications
15.10 | 10mm thick sound board | 150.00 | Sqmtr |  | 850.00 | 127500.00 | 850.00 | 127500.00 | 678.00 | 101700.00 | 750.00 | 112500.00 | 875.00 | 131250.00 | 730.00 | 109500.00 | 949.00 | 142350.00 | 202.00 | 30300.00 | 30300.00 | Blue Star Ltd
16.00 | Supply, installation, testing and commissioning of GI volume control duct damper complete with neoprene rubber gaskets, nuts, bolts, screws linkages, flanges etc, as per specifications. | 15.00 | Sqmtr |  | 5600.00 | 84000.00 | 6440.00 | 96600.00 | 6600.00 | 99000.00 | 4000.00 | 60000.00 | 6290.00 | 94350.00 | 8620.00 | 129300.00 | 6837.00 | 102555.00 | 7500.00 | 112500.00 | 60000.00 | Skyline Airconditioning Engineers Pvt. Ltd.
17.00 | SITC of Aluminum Construction Supply air grill with aluminum VCD | 20.00 | Sqmtr |  | 7500.00 | 150000.00 | 8624.00 | 172480.00 | 8500.00 | 170000.00 | 7500.00 | 150000.00 | 8130.00 | 162600.00 | 8590.00 | 171800.00 | 11130.00 | 222600.00 | 2000.00 | 40000.00 | 40000.00 | Blue Star Ltd
18.00 | SITC of Aluminum Construction Return air grill without VCD | 20.00 | Sqmtr |  | 7000.00 | 140000.00 | 5152.00 | 103040.00 | 6000.00 | 120000.00 | 6500.00 | 130000.00 | 5275.00 | 105500.00 | 4970.00 | 99400.00 | 5671.00 | 113420.00 | 1800.00 | 36000.00 | 36000.00 | Blue Star Ltd
19.00 | Supplying, fixing testing commissioning of Aluminum Supply air diffusers of powder coated with aluminum volume control dampers with anti smudge ring & removable core. | 15.00 | Sqmtr |  | 9963.00 | 149445.00 | 10752.00 | 161280.00 | 9500.00 | 142500.00 | 10000.00 | 150000.00 | 10880.00 | 163200.00 | 12010.00 | 180150.00 | 11713.00 | 175695.00 | 2500.00 | 37500.00 | 37500.00 | Blue Star Ltd
20.00 | Supplying, fixing testing commissioning of Aluminum Return air diffusers of powder coated without volume control dampers with anti smudge ring & removable core. | 15.00 | Sqmtr |  | 8500.00 | 127500.00 | 7280.00 | 109200.00 | 8500.00 | 127500.00 | 7500.00 | 112500.00 | 7250.00 | 108750.00 | 7750.00 | 116250.00 | 10547.00 | 158205.00 | 2000.00 | 30000.00 | 30000.00 | Blue Star Ltd
21.00 | Supplying, installation, testing and commissioning of 300 mm dia Jet diffuser with volume control dampers for supply air as per specifications, complete all as specified and directed. | 25.00 | Nos. |  | 3600.00 | 90000.00 | 2744.00 | 68600.00 | 5100.00 | 127500.00 | 4500.00 | 112500.00 | 2900.00 | 72500.00 | 2520.00 | 63000.00 | 4081.00 | 102025.00 | 975.00 | 24375.00 | 24375.00 | Blue Star Ltd
22.00 | Supplying, fixing, testing and commissioning of powder coated extruded aluminum section fresh air grill in weather maker room with volume control dampers complete as required as per site condition. | 10.00 | Sqmtr |  | 7500.00 | 75000.00 | 8624.00 | 86240.00 | 7020.00 | 70200.00 | 7000.00 | 70000.00 | 10190.00 | 101900.00 | 11520.00 | 115200.00 | 11130.00 | 111300.00 | 2000.00 | 20000.00 | 20000.00 | Blue Star Ltd
23.00 | Supply, fabrication, installation and testing of flexible connection constructed of fire resistant double resin sleeve as per approved shop drawings and specifications, complete all as specified and directed. | 15.00 | Each |  | 1200.00 | 18000.00 | 3136.00 | 47040.00 | 5050.00 | 75750.00 | 2000.00 | 30000.00 | 5000.00 | 75000.00 | 1540.00 | 23100.00 | 4664.00 | 69960.00 | 2000.00 | 30000.00 | 18000.00 | SNOWMEX ENGINEERS LIMITED
24.00 | SITC of Aluminum Construction damper for existing grill | 30.00 | Sqmtr |  | 5250.00 | 157500.00 | 4784.00 | 143520.00 | 4000.00 | 120000.00 | 3500.00 | 105000.00 | 4500.00 | 135000.00 | 4270.00 | 128100.00 | 5777.00 | 173310.00 | 4500.00 | 135000.00 | 105000.00 | Skyline Airconditioning Engineers Pvt. Ltd.
25.00 | SITC of Air balancing of AHU for proper Air flow through NADCA certified Agency Vendor has to submit the Report & NADCA certificate of agency before starting of work.
25.01 | AHU No 1 - 39300 CFM | 1.00 | Each |  | 7500.00 | 7500.00 | 20000.00 | 20000.00 | 19650.00 | 19650.00 | 25000.00 | 25000.00 | 100000.00 | 100000.00 | 19970.00 | 19970.00 | 124974.00 | 124974.00 | 2500.00 | 2500.00 | 2500.00 | Blue Star Ltd
25.02 | AHU No 2 - 29623 CFM | 1.00 | Each |  | 7500.00 | 7500.00 | 20000.00 | 20000.00 | 14811.00 | 14811.00 | 20000.00 | 20000.00 | 80000.00 | 80000.00 | 15050.00 | 15050.00 | 94202.00 | 94202.00 | 2500.00 | 2500.00 | 2500.00 | Blue Star Ltd
25.03 | AHU No 3 - 23 700 CFM | 1.00 | Each |  | 7500.00 | 7500.00 | 20000.00 | 20000.00 | 11850.00 | 11850.00 | 15000.00 | 15000.00 | 65000.00 | 65000.00 | 12040.00 | 12040.00 | 75366.00 | 75366.00 | 2500.00 | 2500.00 | 2500.00 | Blue Star Ltd
25.04 | AHU No 4 & 5 - 30700 CFM | 2.00 | Each |  | 7500.00 | 15000.00 | 20000.00 | 40000.00 | 15350.00 | 30700.00 | 12000.00 | 24000.00 | 80000.00 | 160000.00 | 15600.00 | 31200.00 | 97626.00 | 195252.00 | 4000.00 | 8000.00 | 8000.00 | Blue Star Ltd
25.05 | AHU No 6 - 31500 CFM | 1.00 | Each |  | 7500.00 | 7500.00 | 20000.00 | 20000.00 | 15750.00 | 15750.00 | 15000.00 | 15000.00 | 80000.00 | 80000.00 | 16010.00 | 16010.00 | 100170.00 | 100170.00 | 4000.00 | 4000.00 | 4000.00 | Blue Star Ltd
25.06 | AHU No 7 - 40900 CFM | 1.00 | Each |  | 7500.00 | 7500.00 | 20000.00 | 20000.00 | 20450.00 | 20450.00 | 12000.00 | 12000.00 | 100000.00 | 100000.00 | 20780.00 | 20780.00 | 130062.00 | 130062.00 | 4000.00 | 4000.00 | 4000.00 | Blue Star Ltd
25.07 | AHU No 8 - 30950 CFM | 1.00 | Each |  | 7500.00 | 7500.00 | 20000.00 | 20000.00 | 15475.00 | 15475.00 | 12000.00 | 12000.00 | 80000.00 | 80000.00 | 15730.00 | 15730.00 | 98421.00 | 98421.00 | 4000.00 | 4000.00 | 4000.00 | Blue Star Ltd
25.08 | AHU No 9 & 10 - 35000 CFM | 2.00 | Each |  | 7500.00 | 15000.00 | 20000.00 | 40000.00 | 17500.00 | 35000.00 | 15000.00 | 30000.00 | 90000.00 | 180000.00 | 17780.00 | 35560.00 | 111300.00 | 222600.00 | 4000.00 | 8000.00 | 8000.00 | Blue Star Ltd
25.09 | AHU No 11 - 18500 CFM | 1.00 | Each |  | 7500.00 | 7500.00 | 20000.00 | 20000.00 | 9250.00 | 9250.00 | 8500.00 | 8500.00 | 45000.00 | 45000.00 | 9400.00 | 9400.00 | 58803.00 | 58803.00 | 2500.00 | 2500.00 | 2500.00 | Blue Star Ltd
25.10 | AHU No 12 & 13 - 12000 CFM | 2.00 | Each |  | 7500.00 | 15000.00 | 20000.00 | 40000.00 | 6000.00 | 12000.00 | 7500.00 | 15000.00 | 25000.00 | 50000.00 | 6100.00 | 12200.00 | 38160.00 | 76320.00 | 2000.00 | 4000.00 | 4000.00 | Blue Star Ltd
25.11 | AHU No 11 - 31700 CFM | 1.00 | Each |  | 7500.00 | 7500.00 | 20000.00 | 20000.00 | 15850.00 | 15850.00 | 12000.00 | 12000.00 | 80000.00 | 80000.00 | 16110.00 | 16110.00 | 100806.00 | 100806.00 | 4000.00 | 4000.00 | 4000.00 | Blue Star Ltd
25.12 | AHU No 13 - 5000 CFM | 1.00 | Each |  | 7500.00 | 7500.00 | 20000.00 | 20000.00 | 2560.00 | 2560.00 | 5000.00 | 5000.00 | 2000.00 | 2000.00 | 2540.00 | 2540.00 | 15900.00 | 15900.00 | 2000.00 | 2000.00 | 2000.00 | Blue Star Ltd, Arctic Engineering Services
26.00 | Robotic Duct Cleaning : Removing refixing and cleaning of inside surface of supply & return air ducts, grills & diffusers of HVAC system by busing high power vacuum having HEPA filter, air compressor, robotic camera, air hammer, special nozzles, air sweep with all other required accessories and inspection of duct duct before and after cleaning using colour video minimum at 4 place in each AHU and mopping with the recommended chemical disinfectant such as Korsole/Microbac forte Sokrena or Equivalent inside the surface if supply air duct. Note : All the cleaning work should be carried out by NADCA certified approved agency only .Contractor has to submit the NADCA certificate of agency before starting of execution activity. Mode of Measurement : Mode Of Measurement : Carpet area of Air conditioning space, AHU room and the area where duct is fixed . | 250000.00 | Sqft |  | 5.00 | 1250000.00 | 7.00 | 1750000.00 | 3.00 | 750000.00 | 10.00 | 2500000.00 | 6.25 | 1562500.00 | 3.50 | 875000.00 | 8.00 | 2000000.00 | 5.00 | 1250000.00 | 750000.00 | Ingenious Industries
27.00 | Supply and laying of 3 c x 1.5 Sqmm PVC insulated flexible control cable . | 975.00 | Mtr |  | 110.00 | 107250.00 | 160.00 | 156000.00 | 145.00 | 141375.00 | 250.00 | 243750.00 | 110.00 | 107250.00 | 100.00 | 97500.00 | 104.00 | 101400.00 | 125.00 | 121875.00 | 97500.00 | Mvac Engineers
28.00 | SITC of wall mountable LT panel made of 1.6 mm thick mild steel CRCA steel confirming to IP 43 having suitable size of Al. Bus bars suitable for 3 Phase , 4 wire , 50 Hz AC supply system with following switchgear and accessories – Incomer : (i) 80 A, 415 V, Ics = Icu = 25 kA, 50 Hz FP MCCB with adjustable overload settings, adjustable short-circuit settings and Thermal Magnetic based trip . Incomer have one multifunction meter along with Indicating light. Outgoing : (i) AHU starter shall be design with VFD (matching with AHU motor capacity . Suggested >22 kw to <=30 KW) of capacity as per approved TDS of AHU motor with bypass starter arrangement. There should be Auto manual selector switch for VFD & by pass starter along with indicating light push button on off & Manual VFD Frequency control switch/Regulator to control the VFD speed manually. (ii)6 AMP DP MCB with contactor, toggle switch, indicating light shall be provided for 3 way valve & Fire Damper Actuator/Humidifier- 3 nos. | 4.00 | Each |  | 136500.00 | 546000.00 | 220000.00 | 880000.00 | 143750.00 | 575000.00 | 175000.00 | 700000.00 | 198000.00 | 792000.00 | 99830.00 | 399320.00 | 12850.00 | 51400.00 | 190000.00 | 760000.00 | 51400.00 | Powermech Services Private Limited
29.00 | SITC of wall mountable LT panel made of 1.6 mm thick mild steel CRCA steel confirming to IP 43 having suitable size of Al. Bus bars suitable for 3 Phase , 4 wire , 50 Hz AC supply system with following switchgear and accessories – Incomer : (i) 63 A, 415 V, Ics = Icu = 25 kA, 50 Hz FP MCCB with adjustable overload settings, adjustable short-circuit settings and Thermal Magnetic based trip . Incomer have one multifunction meter along with Indicating light. Outgoing : (i) AHU starter shall be design with VFD ( matching with AHU motor capacity . Suggested >15 kw to <=22 KW) of capacity as per approved TDS of AHU motor with bypass starter arrangement. There should be Auto manual selector switch for VFD & by pass starter along with indicating light push button on off & Manual VFD Frequency control switch/Regulator to control the VFD speed manually. (ii)6 AMP DP MCB with contactor , toggle switch, indicating light shall be provided for 3 way valve & Fire Damper Actuator/Humidifier- 3 nos. | 6.00 | Each |  | 115000.00 | 690000.00 | 200000.00 | 1200000.00 | 120750.00 | 724500.00 | 135000.00 | 810000.00 | 170000.00 | 1020000.00 | 88970.00 | 533820.00 | 134090.00 | 804540.00 | 140000.00 | 840000.00 | 533820.00 | Mvac Engineers
30.00 | SITC of wall mountable LT panel made of 1.6 mm thick mild steel CRCA steel confirming to IP 43 having suitable size of Al. Bus bars suitable for 3 Phase , 4 wire , 50 Hz AC supply system with following switchgear and accessories – Incomer : (i) 63 A, 415 V, Ics = Icu = 25 kA, 50 Hz FP MCCB with adjustable overload settings, adjustable short-circuit settings and Thermal Magnetic based trip . Incomer have one multifunction meter along with Indicating light. Outgoing : (i) AHU starter shall be design with VFD ( matching with AHU motor capacity . Suggested >7.5 kw to <=15 KW) of capacity as per approved TDS of AHU motor with bypass starter arrangement. There should be Auto manual selector switch for VFD & by pass starter along with indicating light push button on off & Manual VFD Frequency control switch/Regulator to control the VFD speed manually. (ii)6 AMP DP MCB with contactor , toggle switch, indicating light shall be provided for 3 way valve & Fire Damper Actuator/Humidifier- 3 nos. | 2.00 | Each |  | 66210.00 | 132420.00 | 150000.00 | 300000.00 | 99820.00 | 199640.00 | 125000.00 | 250000.00 | 130000.00 | 260000.00 | 79380.00 | 158760.00 | 109710.00 | 219420.00 | 105000.00 | 210000.00 | 132420.00 | SNOWMEX ENGINEERS LIMITED
31.00 | SITC of wall mountable LT panel made of 1.6 mm thick mild steel CRCA steel confirming to IP 43 having suitable size of Al. Bus bars suitable for 3 Phase , 4 wire , 50 Hz AC supply system with following switchgear and accessories – (i) 32 A, 415 V, Ics = Icu = 16 kA, 50 Hz FP MCCB with adjustable overload settings, adjustable short-circuit settings and Thermal Magnetic based trip . Incomer have one multifunction meter along with Indicating light. Outgoing : (i) AHU starter shall be design with VFD ( matching with AHU motor capacity . Suggested >3.7 kw to <=7.5 KW) of capacity as per approved TDS of AHU motor with bypass starter arrangement. There should be Auto manual selector switch for VFD & by pass starter along with indicating light push button on off & Manual VFD Frequency control switch/Regulator to control the VFD speed manually. (ii)6 AMP DP MCB with contactor , toggle switch, indicating light shall be provided for 3 way valve & Fire Damper Actuator/Humidifier- 3 nos. | 3.00 | Each |  | 49800.00 | 149400.00 | 110000.00 | 330000.00 | 73600.00 | 220800.00 | 105000.00 | 315000.00 | 94000.00 | 282000.00 | 69170.00 | 207510.00 | 91425.00 | 274275.00 | 90000.00 | 270000.00 | 149400.00 | SNOWMEX ENGINEERS LIMITED
32.00 | SITC of wall mountable LT panel made of 1.6 mm thick mild steel CRCA steel confirming to IP 43 having suitable size of Al. Bus bars suitable for 3 Phase , 4 wire , 50 Hz AC supply system with following switchgear and accessories – Incomer : (i) 16 A, 415 V, Ics = Icu = 10 kA, 50 Hz FP MCCB with adjustable overload settings, adjustable short-circuit settings and Thermal Magnetic based trip . Incomer have one multifunction meter along with Indicating light. Outgoing : (i) AHU starter shall be design with VFD ( matching with AHU motor capacity . Suggested <=3.7 KW) of capacity as per approved TDS of AHU motor with bypass starter arrangement. There should be Auto manual selector switch for VFD & by pass starter along with indicating light push button on off & Manual VFD Frequency control switch/Regulator to control the VFD speed manually. (ii)6 AMP DP MCB with contactor , toggle switch, indicating light shall be provided for 3 way valve & Fire Damper Actuator/Humidifier- 3 nos. | 4.00 | Each |  | 49800.00 | 199200.00 | 90000.00 | 360000.00 | 59800.00 | 239200.00 | 75000.00 | 300000.00 | 80000.00 | 320000.00 | 60230.00 | 240920.00 | 67045.00 | 268180.00 | 85000.00 | 340000.00 | 199200.00 | SNOWMEX ENGINEERS LIMITED
33.00 | Supplying & installing following sizes of perforated Galavanised Iron cable tray with perforation more than 17.5 % in convenient sections, joined with connectors, suspended from ceiling with GI suspender's including GI Bolts & nuts etc. as required
33.10 | 300 mm x50mm x 1.6mm | 200.00 | Mtr |  | 495.00 | 99000.00 | 535.00 | 107000.00 | 655.00 | 131000.00 | 650.00 | 130000.00 | 995.00 | 199000.00 | 820.00 | 164000.00 | 892.00 | 178400.00 | 170.00 | 34000.00 | 34000.00 | Blue Star Ltd
33.20 | 100 mmX 50 mm X 1.6 mm | 200.00 | Mtr |  | 295.00 | 59000.00 | 448.00 | 89600.00 | 449.00 | 89800.00 | 750.00 | 150000.00 | 595.00 | 119000.00 | 510.00 | 102000.00 | 510.00 | 102000.00 | 600.00 | 120000.00 | 59000.00 | SNOWMEX ENGINEERS LIMITED
34.00 | SITC of MS iron for support including one coat of red oxide & one coat of black paint . | 900.00 | Kg |  | 100.00 | 90000.00 | 135.00 | 121500.00 | 125.00 | 112500.00 | 150.00 | 135000.00 | 135.00 | 121500.00 | 120.00 | 108000.00 | 160.00 | 144000.00 | 90.00 | 81000.00 | 81000.00 | Blue Star Ltd
35.00 | SITC of GI strip of size 25 mm x 3 mm as earth lead fixed to wall on batten or recess or chases or buried in ground or drawn in cable tray for loop earthing etc complete all as specified and directed. | 150.00 | Mtr |  | 125.00 | 18750.00 | 112.00 | 16800.00 | 100.00 | 15000.00 | 300.00 | 45000.00 | 160.00 | 24000.00 | 120.00 | 18000.00 | 66.00 | 9900.00 | 160.00 | 24000.00 | 9900.00 | Powermech Services Private Limited
36.00 | Providing and fixing 8 SWG dia G.I. wire on surface or in recess for loop earthing as required. | 100.00 | Mtr |  | 20.00 | 2000.00 | 22.00 | 2200.00 | 110.00 | 11000.00 | 45.00 | 4500.00 | 70.00 | 7000.00 | 30.00 | 3000.00 | 17.00 | 1700.00 | 35.00 | 3500.00 | 1700.00 | Powermech Services Private Limited
37.00 | Dismantling of existing AHU of following CFM and shifting the dismantled material to AAI stores as directed by EIC.
37.10 | 29000 CFM | 3.00 | Nos. |  | 15000.00 | 45000.00 | 5600.00 | 16800.00 | 7500.00 | 22500.00 | 25000.00 | 75000.00 | 15000.00 | 45000.00 | 36830.00 | 110490.00 | 26898.00 | 80694.00 | 4000.00 | 12000.00 | 12000.00 | Blue Star Ltd
37.20 | 24500 CFM | 3.00 | Nos. |  | 15000.00 | 45000.00 | 5600.00 | 16800.00 | 7500.00 | 22500.00 | 25000.00 | 75000.00 | 12000.00 | 36000.00 | 31120.00 | 93360.00 | 22724.00 | 68172.00 | 4000.00 | 12000.00 | 12000.00 | Blue Star Ltd
37.30 | 23000 CFM | 3.00 | Nos. |  | 15000.00 | 45000.00 | 5600.00 | 16800.00 | 7500.00 | 22500.00 | 25000.00 | 75000.00 | 10000.00 | 30000.00 | 29210.00 | 87630.00 | 21333.00 | 63999.00 | 4000.00 | 12000.00 | 12000.00 | Blue Star Ltd
37.40 | 19167 CFM | 1.00 | Nos. |  | 15000.00 | 15000.00 | 5600.00 | 5600.00 | 7500.00 | 7500.00 | 20000.00 | 20000.00 | 9000.00 | 9000.00 | 24350.00 | 24350.00 | 17778.00 | 17778.00 | 4000.00 | 4000.00 | 4000.00 | Blue Star Ltd
37.50 | 18500 CFM | 5.00 | Nos. |  | 15000.00 | 75000.00 | 5600.00 | 28000.00 | 7500.00 | 37500.00 | 20000.00 | 100000.00 | 8000.00 | 40000.00 | 23500.00 | 117500.00 | 17159.00 | 85795.00 | 4000.00 | 20000.00 | 20000.00 | Blue Star Ltd
37.60 | 13530 CFM | 1.00 | Nos. |  | 15000.00 | 15000.00 | 5600.00 | 5600.00 | 6575.00 | 6575.00 | 18000.00 | 18000.00 | 6000.00 | 6000.00 | 17190.00 | 17190.00 | 12550.00 | 12550.00 | 4000.00 | 4000.00 | 4000.00 | Blue Star Ltd
37.70 | 12000 CFM | 2.00 | Nos. |  | 15000.00 | 30000.00 | 5600.00 | 11200.00 | 7500.00 | 15000.00 | 15000.00 | 30000.00 | 5000.00 | 10000.00 | 15240.00 | 30480.00 | 11130.00 | 22260.00 | 4000.00 | 8000.00 | 8000.00 | Blue Star Ltd
38.00 | Supply of following sqmm, 1.1 KV grade, XLPE insulated, PVC sheathed, armoured, aluminum conductor power cable conform to IS 7098 (part -1) with up to date amendments etc complete as required.
38.10 | 4 C x 10 sqmm | 20.00 | Mtr. |  | 10.00 | 200.00 | 92.00 | 1840.00 | 294.00 | 5880.00 | 250.00 | 5000.00 | 175.00 | 3500.00 | 170.00 | 3400.00 | 243.00 | 4860.00 | 150.00 | 3000.00 | 200.00 | SNOWMEX ENGINEERS LIMITED
38.20 | 4 C x 6 sqmm | 60.00 | Mtr. |  | 10.00 | 600.00 | 114.00 | 6840.00 | 214.00 | 12840.00 | 200.00 | 12000.00 | 126.00 | 7560.00 | 130.00 | 7800.00 | 177.00 | 10620.00 | 120.00 | 7200.00 | 600.00 | SNOWMEX ENGINEERS LIMITED
38.30 | 3.5 C x 35 sqmm | 40.00 | Mtr. |  | 10.00 | 400.00 | 235.00 | 9400.00 | 450.00 | 18000.00 | 350.00 | 14000.00 | 277.00 | 11080.00 | 270.00 | 10800.00 | 386.00 | 15440.00 | 290.00 | 11600.00 | 400.00 | SNOWMEX ENGINEERS LIMITED
38.40 | 3.5 C x 25 sqmm | 60.00 | Mtr. |  | 10.00 | 600.00 | 196.00 | 11760.00 | 400.00 | 24000.00 | 275.00 | 16500.00 | 230.00 | 13800.00 | 220.00 | 13200.00 | 317.00 | 19020.00 | 110.00 | 6600.00 | 600.00 | SNOWMEX ENGINEERS LIMITED
38.50 | 3 C x 35 sqmm | 180.00 | Mtr. |  | 285.00 | 51300.00 | 212.00 | 38160.00 | 425.00 | 76500.00 | 340.00 | 61200.00 | 250.00 | 45000.00 | 240.00 | 43200.00 | 347.00 | 62460.00 | 115.00 | 20700.00 | 20700.00 | Blue Star Ltd
38.60 | 3 C x 25 sqmm | 120.00 | Mtr. |  | 110.00 | 13200.00 | 170.00 | 20400.00 | 430.00 | 51600.00 | 265.00 | 31800.00 | 193.00 | 23160.00 | 190.00 | 22800.00 | 273.00 | 32760.00 | 105.00 | 12600.00 | 12600.00 | Blue Star Ltd
38.70 | 3 C x 10 sqmm | 40.00 | Mtr. |  | 150.00 | 6000.00 | 122.00 | 4880.00 | 245.00 | 9800.00 | 250.00 | 10000.00 | 140.00 | 5600.00 | 140.00 | 5600.00 | 191.00 | 7640.00 | 150.00 | 6000.00 | 4880.00 | BRITE INDUSTRIES
38.80 | 3 C x 4 sqmm | 160.00 | Mtr. |  | 110.00 | 17600.00 | 80.00 | 12800.00 | 150.00 | 24000.00 | 200.00 | 32000.00 | 87.00 | 13920.00 | 90.00 | 14400.00 | 120.00 | 19200.00 | 80.00 | 12800.00 | 12800.00 | Blue Star Ltd, BRITE INDUSTRIES
39.00 | Supply of 4 C x 4 sqmm, 1.1 KV grade, XLPE insulated, PVC sheathed, armoured, copper conductor power cable conform to IS 7098 (part -1) with up to date amendments etc complete as required. | 40.00 | Mtr. |  | 150.00 | 6000.00 | 242.00 | 9680.00 | 490.00 | 19600.00 | 300.00 | 12000.00 | 365.00 | 14600.00 | 280.00 | 11200.00 | 385.00 | 15400.00 | 320.00 | 12800.00 | 6000.00 | SNOWMEX ENGINEERS LIMITED
40.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 kV grade of following size on wall surface/existing cable tray as required. - upto 35 Sq. mm. | 720.00 | Mtr. |  | 35.00 | 25200.00 | 156.00 | 112320.00 | 50.00 | 36000.00 | 100.00 | 72000.00 | 75.00 | 54000.00 | 60.00 | 43200.00 | 53.00 | 38160.00 | 60.00 | 43200.00 | 25200.00 | SNOWMEX ENGINEERS LIMITED
41.00 | Supplying and making end termination with brass compression gland and aluminum lugs for following size of PVC insulated and PVC sheathed / XLPE Al. conductor cable of 1.1 kV grade as required.
41.10 | 4 C x 10 sqmm (25 mm) | 2.00 | Set |  | 10.00 | 20.00 | 1120.00 | 2240.00 | 5000.00 | 10000.00 | 200.00 | 400.00 | 975.00 | 1950.00 | 320.00 | 640.00 | 563.00 | 1126.00 | 560.00 | 1120.00 | 20.00 | SNOWMEX ENGINEERS LIMITED
41.20 | 4 C x 6 sqmm (25 mm) | 8.00 | Set |  | 10.00 | 80.00 | 1120.00 | 8960.00 | 1500.00 | 12000.00 | 200.00 | 1600.00 | 975.00 | 7800.00 | 260.00 | 2080.00 | 540.00 | 4320.00 | 500.00 | 4000.00 | 80.00 | SNOWMEX ENGINEERS LIMITED
41.30 | 3.5 C x 35 sqmm (32 mm) | 6.00 | Set |  | 10.00 | 60.00 | 1120.00 | 6720.00 | 1800.00 | 10800.00 | 350.00 | 2100.00 | 1250.00 | 7500.00 | 390.00 | 2340.00 | 948.00 | 5688.00 | 680.00 | 4080.00 | 60.00 | SNOWMEX ENGINEERS LIMITED
41.40 | 3.5 C x 25 sqmm (28 mm) | 6.00 | Set |  | 192.00 | 1152.00 | 1120.00 | 6720.00 | 1400.00 | 8400.00 | 350.00 | 2100.00 | 1250.00 | 7500.00 | 390.00 | 2340.00 | 752.00 | 4512.00 | 300.00 | 1800.00 | 1152.00 | SNOWMEX ENGINEERS LIMITED
41.50 | 3 C x 35 sqmm (28 mm) | 20.00 | Set |  | 248.00 | 4960.00 | 1120.00 | 22400.00 | 1400.00 | 28000.00 | 400.00 | 8000.00 | 1250.00 | 25000.00 | 390.00 | 7800.00 | 760.00 | 15200.00 | 300.00 | 6000.00 | 4960.00 | SNOWMEX ENGINEERS LIMITED
41.60 | 3 C x 25 sqmm (25 mm) | 14.00 | Set |  | 248.00 | 3472.00 | 1120.00 | 15680.00 | 1200.00 | 16800.00 | 350.00 | 4900.00 | 975.00 | 13650.00 | 390.00 | 5460.00 | 747.00 | 10458.00 | 300.00 | 4200.00 | 3472.00 | SNOWMEX ENGINEERS LIMITED
41.70 | 3 C x 10 sqmm (22 mm) | 4.00 | Set |  | 192.00 | 768.00 | 1120.00 | 4480.00 | 900.00 | 3600.00 | 350.00 | 1400.00 | 975.00 | 3900.00 | 320.00 | 1280.00 | 556.00 | 2224.00 | 560.00 | 2240.00 | 768.00 | SNOWMEX ENGINEERS LIMITED
41.80 | 3 C x 4 sqmm (22 mm) | 16.00 | Set |  | 192.00 | 3072.00 | 1120.00 | 17920.00 | 1000.00 | 16000.00 | 300.00 | 4800.00 | 975.00 | 15600.00 | 260.00 | 4160.00 | 420.00 | 6720.00 | 495.00 | 7920.00 | 3072.00 | SNOWMEX ENGINEERS LIMITED
42.00 | Supplying, laying/ fixing, testing and commissioning of following nominal sizes of chilled water piping inside the building (with necessary clamps, vibration isolators and fittings but excluding valves, strainers, gauges etc.) duly insulated with following closed cell elastometric nitrile rubber of minimum 45 Kg / cu m density, thermal conductivity 0.037 W/MK or better at 20 deg mean temperature class ‘O’insulation applied by suitable rubber based adhesive complete including repairing of damage to building etc. as per specifications and as required complete in all respect.
42.10 | Chilled water piping of nominal size - 200mm dia. (32mm thick nitrile rubber) | 180.00 | Mtr. |  | 4250.00 | 765000.00 | 3433.00 | 617940.00 | 5743.00 | 1033740.00 | 6700.00 | 1206000.00 | 5850.00 | 1053000.00 | 3870.00 | 696600.00 | 4770.00 | 858600.00 | 3970.00 | 714600.00 | 617940.00 | BRITE INDUSTRIES
42.20 | Chilled water piping of nominal size - 150mm dia. (32mm thick nitrile rubber) | 180.00 | Mtr. |  | 2950.00 | 531000.00 | 2360.00 | 424800.00 | 4009.00 | 721620.00 | 3800.00 | 684000.00 | 4010.00 | 721800.00 | 2800.00 | 504000.00 | 4057.00 | 730260.00 | 2735.00 | 492300.00 | 424800.00 | BRITE INDUSTRIES
42.30 | Chilled water piping of nominal size - 100mm dia. (32mm thick nitrile rubber) | 40.00 | Mtr. |  | 1200.00 | 48000.00 | 2095.00 | 83800.00 | 2696.00 | 107840.00 | 3000.00 | 120000.00 | 2790.00 | 111600.00 | 1950.00 | 78000.00 | 2635.00 | 105400.00 | 1970.00 | 78800.00 | 48000.00 | SNOWMEX ENGINEERS LIMITED
43.00 | Supplying, laying/ fixing, testing and commissioning of following nominal sizes of chilled water piping in ground (with necessary fittings but excluding valves, strainers, gauges etc.) duly insulated with following closed cell elastometric nitrile rubber of minimum 45 Kg / cu m density, thermal conductivity 0.037 W/MK or better at 20 deg mean temperature class ‘O’insulation applied by suitable rubber based adhesive complete including exavation & providing cement concrete blocks as supports, etc. as per specifications and as required complete in all respect
43.10 | Chilled water piping of nominal size - 200mm dia. (32mm thick nitrile rubber) | 30.00 | Mtr. |  | 4250.00 | 127500.00 | 3450.00 | 103500.00 | 6295.00 | 188850.00 | 8500.00 | 255000.00 | 6410.00 | 192300.00 | 5210.00 | 156300.00 | 4770.00 | 143100.00 | 4215.00 | 126450.00 | 103500.00 | BRITE INDUSTRIES
43.20 | Chilled water piping of nominal size - 150mm dia. (32mm thick nitrile rubber) | 30.00 | Mtr. |  | 2950.00 | 88500.00 | 2340.00 | 70200.00 | 4423.00 | 132690.00 | 4000.00 | 120000.00 | 4390.00 | 131700.00 | 3430.00 | 102900.00 | 4057.00 | 121710.00 | 2920.00 | 87600.00 | 70200.00 | BRITE INDUSTRIES
44.00 | Supplying and fixing aluminium sheet cladding on 200mm dia. (32mm thick nitrile rubber) of chilled water piping complete as per specifications and as required complete in all respect. | 180.00 | Mtr. |  | 950.00 | 171000.00 | 1240.00 | 223200.00 | 1180.00 | 212400.00 | 2000.00 | 360000.00 | 650.00 | 117000.00 | 810.00 | 145800.00 | 636.00 | 114480.00 | 1200.00 | 216000.00 | 114480.00 | Powermech Services Private Limited
45.00 | Supplying and fixing aluminium sheet cladding on 150mm dia. (32mm thick nitrile rubber) of chilled water piping complete as per specifications and as required complete in all respect. | 180.00 | Mtr. |  | 850.00 | 153000.00 | 970.00 | 174600.00 | 528.00 | 95040.00 | 1000.00 | 180000.00 | 550.00 | 99000.00 | 660.00 | 118800.00 | 530.00 | 95400.00 | 750.00 | 135000.00 | 95040.00 | Ingenious Industries
| Total in Figures |  |  |  |  | 24989097.00 |  | 26147727.00 |  | 26255555.00 |  | 26884350.00 |  | 28279395.00 |  | 23159050.00 |  | 26022592.00 |  | 22157575.00
Lowest Amount Quoted BY: Blue Star Ltd(22157575.00)

## BOQ Summary
BOQ Summary Details Tender Title: Upgradation of low side HVAC system at Amritsar Airport Tender ID: 2025_AAI_251964_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Blue Star Ltd (BID ID -919445) | 22157575.00 | L1
| 2 | Mvac Engineers (BID ID -921651) | 23159050.00 | L2
| 3 | SNOWMEX ENGINEERS LIMITED (BID ID -920434) | 24989097.00 | L3
| 4 | Powermech Services Private Limited (BID ID -920214) | 26022592.00 | L4
| 5 | BRITE INDUSTRIES (BID ID -920670) | 26147727.00 | L5
| 6 | Ingenious Industries (BID ID -921675) | 26255555.00 | L6
| 7 | Skyline Airconditioning Engineers Pvt. Ltd. (BID ID -921994) | 26884350.00 | L7
| 8 | Arctic Engineering Services (BID ID -922055) | 28279395.00 | L8