## BoQ1
Government eProcurement System Created By: Bhuwnesh Gupta Created Date/Time: 16-Dec-2025 03:53 PM Tender Title: Construction of new civil enclave at Jammu Airport SH SITC of airfield ground light facility at Jammu airport Tender ID: 2025_AAI_253602_1
Tender Inviting Authority: Airports Authority of India
Name of Work: Construction of new civil enclave at Jammu Airport SH: SITC of airfield ground light facility at Jammu airport”
Contract No: 2025_AAI_253602_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | AMA Private Limited (GSTN-27AAACA1016F1ZE) BID ID -929126 |  | JCC ENGINEERS PRIVATE LIMITED (GSTN-NA) BID ID -928399 |  | Vardhman Airport Solutions Limited (GSTN-NA) BID ID -928997
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply of elevated type Omni-directional, medium intensity LED Taxiway Edge Light fitting suitable for Taxiway Edge Lights, Apron Edge Lights for operation at 2.8 to 6.6 Amps, series circuit supply, complete with Omni-directional Blue lens, Lens clamping mechanism, breakable coupling, gasket, two pin secondary leads, base plate with 06 Nos , M - 10 stainless steel bolts and other accessories ready for site installation conforming to approved make list and meeting technical specifications. Omni-directonal Blue. | 90.00 | Each | 6299.00 | 3500.00 | 315000.00 | 12500.00 | 1125000.00 | 3850.00 | 346500.00 | 315000.00 | AMA Private Limited
2.00 | Supply of LED type inset omnidirectional fitting for aviation visual aid for Taxiway Edge light/APRON edge light complete with LED, shallow base & matching body, single plug, inner & outer cover complete with other accessories, ready for site installation suitable for 2.8 to 6.6A etc. as required and as per approved make list and meeting technical specifications. Omni-directonal Blue. | 23.00 | Each | 48783.00 | 68487.00 | 1575201.00 | 30000.00 | 690000.00 | 45000.00 | 1035000.00 | 690000.00 | JCC ENGINEERS PRIVATE LIMITED
3.00 | Supply of LED type inset bidirectional fitting for aviation visual aid at Taxiway centre line suitable for straight section/ straight section (Off set)/curved section complete with LED, shallow base & matching body, single plug, inner & outer cover complete with other accessories, ready for site installation suitable for 2.8 to 6.6A etc. as required and as per approved make list and meeting technical specifications. Bi-directional. Green/Green, Green/Yellow. (Note: Quantity of Green/Green & Green/Yellow shall be as per approved design of the system) | 360.00 | Each | 46662.00 | 60416.00 | 21749760.00 | 40000.00 | 14400000.00 | 53200.00 | 19152000.00 | 14400000.00 | JCC ENGINEERS PRIVATE LIMITED
4.00 | Supply of Bi-directional Inset type High Intensity Runway Edge light fitting for aviation visual aids requirements & meeting ICAO requirments complete with shallow base and matching body of the fitting, inner body and outer cover made of die cast aluminium complete with 2 x 105 Watts, 2.8 to 6.6 amps pre-focused reflector halogen lamp with connected heat resistant accessories, prism assesembly, optical assembly, "0" ring seal, pressure relief test plug, hardware, clear / yellow lenses and all standard accessories and ready for site Installation as required and as per the enclosed specifications. Clear / Yellow | 5.00 | Each | 63630.00 | 100090.00 | 500450.00 | 90000.00 | 450000.00 | 52000.00 | 260000.00 | 260000.00 | Vardhman Airport Solutions Limited
5.00 | Supply of LED type inset unidirectional fitting for aviation visual aid at stop bar light complete with LED, shallow base & matching body, single plug, inner & outer cover complete with other accessories, ready for site installation suitable for 2.8 to 6.6A etc. as required and as per approved make list and meeting technical specifications. Uni-directonal Red. | 20.00 | Each | 48783.00 | 60416.00 | 1208320.00 | 30000.00 | 600000.00 | 37000.00 | 740000.00 | 600000.00 | JCC ENGINEERS PRIVATE LIMITED
6.00 | Supply of LED type high intensity elevated type Uni-directional Runway Guard Light fitting for suitable for operation at 2.8 to 6.6 Amps series circuit supply, complete with Lens clamping mechanism, breakable coupling , gasket, two pin secondary leads, base plate with 06 Nos , M - 10 stainless steel bolts and other accessories ready for site installation conforming to approved make list and meeting technical specifications. | 5.00 | Set | 190890.00 | 400000.00 | 2000000.00 | 125000.00 | 625000.00 | 125000.00 | 625000.00 | 625000.00 | JCC ENGINEERS PRIVATE LIMITED, Vardhman Airport Solutions Limited
7.00 | Supply of LED type inset omnidirectional fitting for aviation visual aid stand Manoeuvring Guidance Lights complete with LED, shallow base & matching body, single plug, inner & outer cover complete with other accessories, ready for site installation suitable for 2.8 to 6.6A etc. as required as required and as per approved make list and meeting technical specifications. Omni-directonal Yellow. | 199.00 | Each | 47723.00 | 60000.00 | 11940000.00 | 30000.00 | 5970000.00 | 45000.00 | 8955000.00 | 5970000.00 | JCC ENGINEERS PRIVATE LIMITED
8.00 | Supply of LED type inset unidirectional fitting for aviation visual aid at manoeuvring guidance stop position light complete with LED, shallow base & matching body, single plug, inner & outer cover complete with other accessories, ready for site installation suitable for 2.8 to 6.6A etc. as required and as per approved make list and meeting technical specifications. Uni-directonal Red. | 14.00 | Each | 50904.00 | 67095.00 | 939330.00 | 30000.00 | 420000.00 | 38000.00 | 532000.00 | 420000.00 | JCC ENGINEERS PRIVATE LIMITED
9.00 | Supply of airfield lighting (AFL) 5KV grade 1Cx6sqmm copper conduter unshieled, XLPE insulated, and with inner and outer semi-conducter, polyethylene (PE) outer sheathed, and unarmoured underground cable for airfield lighting in primary circuit, conforming to specification as specified in technical specification. | 66000.00 | Meter | 117.00 | 95.00 | 6270000.00 | 180.00 | 11880000.00 | 155.00 | 10230000.00 | 6270000.00 | AMA Private Limited
10.00 | Supply of 2C x 4 sqmm 600V Grade Flexible Copper Conductor, EPR insulated & CPE (Chlorinated Polythelen, cross-linked , heavy duty) outer sheath Secondary cable for Airport lighting circuits conforming as specified in particular specification. | 24000.00 | Meter | 165.00 | 155.00 | 3720000.00 | 220.00 | 5280000.00 | 170.00 | 4080000.00 | 3720000.00 | AMA Private Limited
11.00 | Supply of 1 X 4 sq.mm FRLSH PVC insulated copper conductor single core wire for end to end termination for earthing, preferably green colour conforming to conforming to IS:694 as amended up to date and technical specifications etc. complete as required. | 6000.00 | Meter | 52.13 | 60.00 | 360000.00 | 100.00 | 600000.00 | 85.00 | 510000.00 | 360000.00 | AMA Private Limited
12.00 | Laying of Secondary Cable along with 01(one) no. 1x4 sqmm. wire for earthing, in Runway Pavement at suitable depth (as per site requirement upto 0.18 m) including Kerf cutting by suitable cutter machine, binding the secondary cable with earth wire and covering the same with cotton tape for protection as per site requirement and as per direction of Engineer-in-Charge, making end termination of earth wire with shallow base of inset fitting and isolating transformer housing box, cleaning, filling the gap with backer rod and suitable sealing material (as per site requirement) above the cable, finishing, making good the runway surface and matching the same with existing runway surface level, painting the surface (if needed), cleaning the area etc. complete as required.Length of kerf cutting shall be consider for measurement.
12.01 | One Layer of secondary cable & earthing wires allowed in single kerf as per site requirement and approvals. | 5000.00 | Meter | 474.00 | 275.00 | 1375000.00 | 250.00 | 1250000.00 | 150.00 | 750000.00 | 750000.00 | Vardhman Airport Solutions Limited
12.02 | Above 1 Layer and upto 4 Layer of secondary cable & earthing wires allowed in single kerf as per site requirement and approvals. | 15000.00 | Meter | 477.00 | 300.00 | 4500000.00 | 250.00 | 3750000.00 | 175.00 | 2625000.00 | 2625000.00 | Vardhman Airport Solutions Limited
13.00 | Supply of 5 KV 50 Hz, isolating transformer encapsulated in cross linked polychloroprene compound like TPE/TPR/TPV for individual series lamps airport lighting circuits. The transformer shall be designed to be water proof and suitable for direct burial in the earth or installation in a base complete as per specifications attached.15 watt, 6.6A/ 6.6A | 115.00 | Each | 2969.00 | 2800.00 | 322000.00 | 4800.00 | 552000.00 | 2500.00 | 287500.00 | 287500.00 | Vardhman Airport Solutions Limited
14.00 | Supply of 5 KV 50 Hz, isolating transformer encapsulated in cross linked polychloroprene compound like TPE/TPR/TPV for individual series lamps airport lighting circuits. The transformer shall be designed to be water proof and suitable for direct burial in the earth or installation in a base complete as per specifications attached.30 watt, 6.6A/ 6.6A | 380.00 | Each | 4242.00 | 3400.00 | 1292000.00 | 5000.00 | 1900000.00 | 3000.00 | 1140000.00 | 1140000.00 | Vardhman Airport Solutions Limited
15.00 | Supply of 5 KV 50 Hz, encapsulated in cross linked polychloroprene compound like TPE/TPR/TPV suitable for individual series lamps airport lighting circuits. The transformer shall be designed to be water proof and suitable for direct burial in the earth or installation in a base complete as per specifications attached. 45 watt, 6.6A/6.6A | 220.00 | Each | 4772.00 | 3400.00 | 748000.00 | 5500.00 | 1210000.00 | 2850.00 | 627000.00 | 627000.00 | Vardhman Airport Solutions Limited
16.00 | Supply of 5 KV 50 Hz, encapsulated in cross linked polychloroprene compound like TPE/TPR/TPV suitable for individual series lamps airport lighting circuits. The transformer shall be designed to be water proof and suitable for direct burial in the earth or installation in a base complete as per specifications attached. 200 watt, 6.6A/ 6.6A | 30.00 | Each | 6363.00 | 4500.00 | 135000.00 | 7000.00 | 210000.00 | 4250.00 | 127500.00 | 127500.00 | Vardhman Airport Solutions Limited
17.00 | Supply of 5 KV 50 Hz, encapsulated in cross linked polychloroprene compound like TPE/TPR/TPV suitable for individual series lamps airport lighting circuits. The transformer shall be designed to be water proof and suitable for direct burial in the earth or installation in a base complete as per specifications attached.300 W, 20/2.8 to 6.6A | 5.00 | Each | 6363.00 | 6000.00 | 30000.00 | 8000.00 | 40000.00 | 5800.00 | 29000.00 | 29000.00 | Vardhman Airport Solutions Limited
18.00 | DSITC of LED Guidance Sign Board of various sizes made out of anodized 3 mm corrosive resistant aluminum extrusion frame (thickness of signboard should be less than 45 mm) and Facia should not be more than 50 mm at all sides of the display. The extrusions frame should be interlocked/bolted with each other creating a sealed unit and 2 mm thick aluminium backcover, 4 mm thick polycarbonate sheet with glare free front face, the letter & symbol should be made by of vinyl and pasted on 4mm thick polycarbonate sheet at the inner side of the sign face with required colouring, 4mm acrylic LGP sheet, signboard shall be uniformly inernally illuminated with LED strip mounted on the top of LGP sheet to achieve illumination level and can operate on series circuit without flickering, suitable arrangement shall be made for water tighness & locking arrangement, including supporting frangible legs & frame etc., grouting of each mouting leg by providing & laying 1:2:4 (1 Cement : 2 Coarse sand : 3 graded stone aggregate 20mm nominal size) cement concrete foundation including excavation, shuttering & centering, refilling, leveling etc, fixing of coupling through anchor bolts, secondary cable laying, connection to isolating tranformer, testing and commissioning etc complete as required as per technical specification and meeting ICAO Annex 14 specifications. | 31.00 | Sqmtr | 40299.00 | 38000.00 | 1178000.00 | 50000.00 | 1550000.00 | 55000.00 | 1705000.00 | 1178000.00 | AMA Private Limited
19.00 | Design and supply of three sided aircraft stand identification sign board of approximate size 800mm x 600mm made out of 2 mm thick aluminium frame with suitable angle support, 1.5 mm thick aluminium backcover, 4 mm thick polycarbonate sheet with glare free face, screen printed letter & symbol on self adhesive vinyl sheet applied on the inside face of ploycarbonate sheet, water tight & locking arrangement, uniformly internally illuminated with required LEDs to achieve illumination level, convertor/driver, operate without flickering on single phase 230 V, 50 Hz AC supply, installation of sign on existing GI octagonal pole with help of suppoting structure, connection, testing and commissioning etc complete as required and meeting ICAO Annex 14 specifications. | 13.00 | Each | 36587.00 | 50000.00 | 650000.00 | 60000.00 | 780000.00 | 60000.00 | 780000.00 | 650000.00 | AMA Private Limited
20.00 | Design and supply of aircraft stand coordinates sign board of approximate size 1000mm x 500mm made out of 2 mm thick aluminium frame with suitable angle support, 1.5 mm thick aluminium backcover, 4 mm thick polycarbonate sheet with glare free face, screen printed letter & symbol on self adhesive venyl sheet applied on the inside face of ploycarbonate sheet, water tight & locking arrangement, uniformly internally illuminated with required LEDs to achieve illumination level, convertor/driver, operate on single phase 230 V, 50 Hz AC supply without flickering, installation of sign on existing GI octagonal pole with help of suppoting structure, connection, testing and commissioning complete as required and meeting ICAO Annex 14 specifications. | 13.00 | Each | 21210.00 | 33000.00 | 429000.00 | 50000.00 | 650000.00 | 19500.00 | 253500.00 | 253500.00 | Vardhman Airport Solutions Limited
21.00 | Supply and installation of day night sensor switch for automatic on and off of guidance sign boards suitable to operate on single phase 230 V, 50 Hz AC supply including connection, testing and commissioning etc complete as required. | 13.00 | Each | 2121.00 | 650.00 | 8450.00 | 3000.00 | 39000.00 | 2350.00 | 30550.00 | 8450.00 | AMA Private Limited
22.00 | Supply of weather proof IP66 thermoplastic cable junction box suitable for termination of 2x10 sqmm armoured cable including one number 6 A, 10 kA, DP MCB, connector kit etc and fixing on existing GI octagonal pole by clamps, bolts, nuts etc complete as required. | 13.00 | Each | 1379.00 | 4000.00 | 52000.00 | 5000.00 | 65000.00 | 2750.00 | 35750.00 | 35750.00 | Vardhman Airport Solutions Limited
23.00 | Design, Fabrication & Supply of 6 mtrs. height GI OCTAGONAL continuously tapered galvanised pole without GI bracket and without arm for installation of signages, suitable for wind velocity as per IS 875 (but not less than 50 m/sec.), fabricated out of 3 mm thick high tensile sheet steel in single piece construction having 130 mm bottom, 70 mm top, suitable for installation on a precast foundation with supply of 4 nos. of foundation bolts & anchor plate, rigid flange plate (200x200x12mm min.) welded with the base of pole for fixing on foundation bolts complete as required for structural stability as specified, earthing bolts for continuous earth connection complete, as required as per technical specifications. | 13.00 | Each | 13256.00 | 60000.00 | 780000.00 | 20000.00 | 260000.00 | 11500.00 | 149500.00 | 149500.00 | Vardhman Airport Solutions Limited
24.00 | Erection of metallic pole of followings length in cement concrete 1:3:6(1 cement:3 coarse sand:6 graded stone aggregate 40 mm nominal size) foundation including excavation and refilling etc. as required. Above 4.5 meter and upto 6.5 meter | 13.00 | Nos | 5343.00 | 30000.00 | 390000.00 | 5000.00 | 65000.00 | 4750.00 | 61750.00 | 61750.00 | Vardhman Airport Solutions Limited
25.00 | Supply of C.I. Isolating Transformer housing box,water tight round type,metal container of outside size 330mm height 450mm made of 10mm thick cast iron moulding all round, except the top surface, which is 15 mm thick, cast iron moulding suitable to receive a light fitting base plate on the top and underground housing associated with transformer power cable and having a clear holes at the surface centre 75mm above bottom surface suitable to receive one/ two/three No. of 50mm dia "B" class HDPE pipe and including check nuts as required and another hole at 175mm from the bottom of the CI Box to receive one no. 15mm dia "B" class GI pipe and check nut as required.The box should have two SS earth bolts of M10 x 30mm tapped inside near the hole (4" away from the hole centre) and having a drain hole at the bottom suitably tapped to receive 15mm dia "B" class GI pipe and having clear opening of 220 mm at the top surface and 6 nos. M10 tapped hole at the hole centre 260 mm to receive fitting base plate and bolts as required holes as per the site requirements / drawings. One hole/Two Hole/Three Hole as per site requirement. | 539.00 | Each | 5727.00 | 4900.00 | 2641100.00 | 8000.00 | 4312000.00 | 5000.00 | 2695000.00 | 2641100.00 | AMA Private Limited
26.00 | Supply of 6 sqmm size 5 KV grade plug and receptacle of type I, class 'B' connector and suitable field attachment with 5 KV grade XLPE insulated, polyethylene (PE) outer sheathed, single core copper conductor cable as required and confirming to the specifications. | 1500.00 | Set | 848.00 | 450.00 | 675000.00 | 1000.00 | 1500000.00 | 450.00 | 675000.00 | 675000.00 | Vardhman Airport Solutions Limited, AMA Private Limited
27.00 | Supply of 2 x 4 sqmm, 600 V grade plug & receptacle of type II, class 'B' connector and suitable field attachment for EPR insulated & CPE (Chlorinated Polythelen, cross-linked , heavy duty) outer sheath, two core copper conductor secondary cable as required. | 600.00 | Set | 848.00 | 850.00 | 510000.00 | 1000.00 | 600000.00 | 450.00 | 270000.00 | 270000.00 | Vardhman Airport Solutions Limited
28.00 | SITC of 2.5 KW Indoor Type Air Cooled Constant Current Regulator (CCR) of Micro Processor Controlled thyristor type suitable for operation on single phase 230V + PE ± 10%, 50 Hz input AC supply with 5 steps variation of current output (2.8, 3.4, 4.0, 5.2 and 6.6 Amp) and able to communicate with PC or PLC controlled system with digital output ammeter (0-10 Amps), over current, over voltage, open circuit and earth fault protection and earth leakage meter, two stage earth leakage detector, positive back indication Equipments, hours run counter, LCD display complete as required and confirm to specifications enclosed and suitable for operation on the Airfield Lighting Control and Monitoring System (ALCMS) with communication, local and remote control and monitoring and data recording and history keeping etc complete as required. | 11.00 | Each | 265125.00 | 200000.00 | 2200000.00 | 175000.00 | 1925000.00 | 200000.00 | 2200000.00 | 1925000.00 | JCC ENGINEERS PRIVATE LIMITED
29.00 | SITC of 4 KW Indoor Type Air Cooled Constant Current Regulator (CCR) of Micro Processor Controlled thyristor type suitable for operation on single phase 230V + PE ± 10%, 50 Hz input AC supply with 5 steps variation of current output (2.8, 3.4, 4.0, 5.2 and 6.6 Amp) and able to communicate with PC or PLC controlled system with digital output ammeter (0-10 Amps), over current, over voltage, open circuit and earth fault protection and earth leakage meter, two stage earth leakage detector, positive back indication Equipments, hours run counter, LCD display complete as required and confirm to specifications enclosed and suitable for operation on the Airfield Lighting Control and Monitoring System (ALCMS) with communication, local and remote control and monitoring and data recording and history keeping etc complete as required. | 5.00 | Each | 318150.00 | 275000.00 | 1375000.00 | 180000.00 | 900000.00 | 225000.00 | 1125000.00 | 900000.00 | JCC ENGINEERS PRIVATE LIMITED
30.00 | Design, Supply, Assembling, installation, testing and commissioning of ICAO and FAA compliant Computerised Airfield Lighting Control and Monitoring System (ALCMS) through HMI, Type L890 BB to the requirements of FAA advisory circular No. AC 150/5345-56B amended upto date and additional circuits/ mechanism/ interfaces for control and monitoring of constant current regulator (CCR's) & fixed circuits such as guard light, Taxi centre light,Taxi edge light,APRON edge light stand manenvering light,Stop bar light etc. to make them compatible with ALCMS, data & power cabling & earthing etc., including spare PLC and I/O modules, all hardware and software, licenses and other items as required for succesful operation of the system in line with the scope of work, details of equipments, specification, performance criteria etc. Two vault processor should be provided both running in parallel for full redundancy in operation at ATC tower (control working position) and two vault at CCR room (maintenance working position) and also ALCMS to work in fail safe mode complete as required as per technical specifications including cable terminations, provision of SPD, media converters etc complete as required including additional vault processor. The display graphics shall be as per user requirement in ATC tower. (Note: does not include the cost of communication cable) | 1.00 | set | 3393600.00 | 1800000.00 | 1800000.00 | 1200000.00 | 1200000.00 | 2500000.00 | 2500000.00 | 1200000.00 | JCC ENGINEERS PRIVATE LIMITED
31.00 | Installation, testing and commissioning of all types of inset fitting including core cutting/drilling in PQC/bitumin, aligning and setting i/c installation of Isolating Transformer, Crimping / Jointing of secondary connectors, and other accessories required for commissioning i/c supply of all materials except lighting fixture, secondary lead, plug & receptacles, lamp & isolating transformer etc. as required. | 535.00 | Job | 7954.00 | 5000.00 | 2675000.00 | 1200.00 | 642000.00 | 3650.00 | 1952750.00 | 642000.00 | JCC ENGINEERS PRIVATE LIMITED
32.00 | Installation, testing & commissioning of all types of elevated fittings i/c installation of isolating transformer, crimping/jointing of plug & receptacles, i/c supply of all materials excluding fixture, secondary lead, plug & receptacles, Lamp & isolating transformer etc. as required. | 107.00 | Job | 848.00 | 300.00 | 32100.00 | 100.00 | 10700.00 | 100.00 | 10700.00 | 10700.00 | JCC ENGINEERS PRIVATE LIMITED, Vardhman Airport Solutions Limited
33.00 | ITC of CI housing box round type, of size 330 mm dia and 450 mm deep inside bitumen macadum/PQC surface of runway/shoulder/taxiway/in soil i/c cutting of surface, with a base concrete of 1:3:6 of size 630 x 630 x 100 mm thick all round concrete of 1:2:4 150 mm thick. The top stoped with 1:2:4 cement concrete including providing and fixing 10" long 15 mm dia "B" class GI pipe complete as required. | 539.00 | Job | 3182.00 | 3500.00 | 1886500.00 | 500.00 | 269500.00 | 2200.00 | 1185800.00 | 269500.00 | JCC ENGINEERS PRIVATE LIMITED
34.00 | Horizontal Directional Drilling including supply & laying of 50 mm dia HDPE Pipe (OD-50mm & ID-38 mm nominal) PN6 PE80 through boring by "No Dig" method using trench-less technology and other associated works along road and under operational area in all type of soil (including soft rock & hard rock) at suitable depth including all civil works and supply of all tested lifting tools and tackling of other required equipments and consumables, labour etc. and making all such necessary arrangements are under agency scope. | 600.00 | Mtr | 1061.00 | 950.00 | 570000.00 | 400.00 | 240000.00 | 475.00 | 285000.00 | 240000.00 | JCC ENGINEERS PRIVATE LIMITED
35.00 | Supply of 1.1 KV grade XLPE insulated, PVC sheathed, armoured alunimum conductor cable conforming to IS 7098 (Part 1) amended upto date.
35.01 | 3 x 25 sqmm | 700.00 | Mtr | 172.00 | 364.00 | 254800.00 | 400.00 | 280000.00 | 160.00 | 112000.00 | 112000.00 | Vardhman Airport Solutions Limited
35.02 | 3.5 x 50 sqmm | 700.00 | Mtr | 329.00 | 710.00 | 497000.00 | 500.00 | 350000.00 | 305.00 | 213500.00 | 213500.00 | Vardhman Airport Solutions Limited
35.03 | 4 x 16 sqmm | 700.00 | Mtr | 163.00 | 372.00 | 260400.00 | 350.00 | 245000.00 | 151.00 | 105700.00 | 105700.00 | Vardhman Airport Solutions Limited
35.04 | 3 x 4 sqmm | 700.00 | Mtr | 75.00 | 172.00 | 120400.00 | 200.00 | 140000.00 | 71.00 | 49700.00 | 49700.00 | Vardhman Airport Solutions Limited
35.05 | 2 x 10 Sqmm | 800.00 | Mtr | 108.00 | 251.00 | 200800.00 | 250.00 | 200000.00 | 100.00 | 80000.00 | 80000.00 | Vardhman Airport Solutions Limited
36.00 | Supply of 3 core 2.5 sqmm XLPE Insulated Armoured copper conductor control cable with working voltage 1.1 kv grade confirming to IS 7098 (part1) with up to date amendments etc. as required. | 600.00 | Mtr | 134.00 | 315.00 | 189000.00 | 300.00 | 180000.00 | 135.00 | 81000.00 | 81000.00 | Vardhman Airport Solutions Limited
37.00 | Supply of 8 core 2.5 sqmm XLPE Insulated Armoured copper conductor control cable with working voltage 1.1 kv grade confirming to IS 7098 (part1) with up to date amendments etc. as required. | 1850.00 | Mtr | 344.00 | 727.00 | 1344950.00 | 600.00 | 1110000.00 | 355.00 | 656750.00 | 656750.00 | Vardhman Airport Solutions Limited
38.00 | Supply of Single mode 06 fibre, armoured Optic Fibre Cable (OFC) (ISI marked) conforming to ITU-T G.652 and IEC-60794 with up to date amendments, etc complete as required as per technical specification. | 5500.00 | Mtr | 21.00 | 150.00 | 825000.00 | 50.00 | 275000.00 | 25.00 | 137500.00 | 137500.00 | Vardhman Airport Solutions Limited
39.00 | Supplying and making joint of 06 fibre single mode optical fibre cable fibre cable with splicing including complete kit and accessories etc. as required. | 20.00 | Job | 10605.00 | 135.00 | 2700.00 | 2000.00 | 40000.00 | 10000.00 | 200000.00 | 2700.00 | AMA Private Limited
40.00 | Supplying and making straight through joint with heat shrinkable kit including ferrules and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required
40.01 | 3.5 x 50 sqmm | 5.00 | Job | 2449.00 | 9500.00 | 47500.00 | 2000.00 | 10000.00 | 1100.00 | 5500.00 | 5500.00 | Vardhman Airport Solutions Limited
40.02 | 4 x 16 sqmm | 5.00 | Job | 2308.00 | 5500.00 | 27500.00 | 1000.00 | 5000.00 | 900.00 | 4500.00 | 4500.00 | Vardhman Airport Solutions Limited
41.00 | Supplying and making end termination with brass compression gland and copper lugs for following size of airfield copper cable of 5 KV grade as required.1 X 6 sq. mm | 28.00 | Job | 1385.00 | 3000.00 | 84000.00 | 200.00 | 5600.00 | 200.00 | 5600.00 | 5600.00 | JCC ENGINEERS PRIVATE LIMITED, Vardhman Airport Solutions Limited
42.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
42.01 | 3 x 25 sqmm | 34.00 | Set | 281.00 | 3000.00 | 102000.00 | 200.00 | 6800.00 | 750.00 | 25500.00 | 6800.00 | JCC ENGINEERS PRIVATE LIMITED
42.02 | 3.5 x 50 sqmm | 2.00 | Set | 499.00 | 3000.00 | 6000.00 | 300.00 | 600.00 | 950.00 | 1900.00 | 600.00 | JCC ENGINEERS PRIVATE LIMITED
42.03 | 4 x 16 sqmm | 2.00 | Set | 314.00 | 3000.00 | 6000.00 | 200.00 | 400.00 | 750.00 | 1500.00 | 400.00 | JCC ENGINEERS PRIVATE LIMITED
42.04 | 2 x 10 Sqmm | 26.00 | Set | 237.00 | 3000.00 | 78000.00 | 200.00 | 5200.00 | 500.00 | 13000.00 | 5200.00 | JCC ENGINEERS PRIVATE LIMITED
43.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/ HUME/ METAL/DWC HDPE/HDPE pipe as required.Upto 35sq mm. | 60000.00 | Mtr | 37.00 | 20.00 | 1200000.00 | 8.00 | 480000.00 | 12.00 | 720000.00 | 480000.00 | JCC ENGINEERS PRIVATE LIMITED
44.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing masonry open duct as required.Upto 35sq mm | 1050.00 | Mtr | 28.00 | 22.00 | 23100.00 | 8.00 | 8400.00 | 12.00 | 12600.00 | 8400.00 | JCC ENGINEERS PRIVATE LIMITED
45.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on wall surface/Cable Tray as required. Upto 35 Sqmm (clamped with 1mm thick saddle) . | 600.00 | Mtr | 55.00 | 30.00 | 18000.00 | 50.00 | 30000.00 | 18.00 | 10800.00 | 10800.00 | Vardhman Airport Solutions Limited
46.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/ HUME/ METAL/DWC HDPE pipe as required. Above 35 sq. mm and upto 95 sq. mm | 500.00 | Mtr | 58.00 | 30.00 | 15000.00 | 20.00 | 10000.00 | 18.00 | 9000.00 | 9000.00 | Vardhman Airport Solutions Limited
47.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing masonry open duct as required. Above 35 sq. mm and upto 95 sq. mm | 10.00 | Mtr | 46.00 | 30.00 | 300.00 | 20.00 | 200.00 | 18.00 | 180.00 | 180.00 | Vardhman Airport Solutions Limited
48.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on wall surface/Cable Tray as required. Above 35 sq. mm and upto 95 sq. mm (clamped with 25x3mm MS flat clamp) | 50.00 | Mtr | 129.00 | 30.00 | 1500.00 | 100.00 | 5000.00 | 18.00 | 900.00 | 900.00 | Vardhman Airport Solutions Limited
49.00 | Supplying and installing following size of perforated painted with powder coating M.S. cable trays with perforation not more than 17.5%, in convenient sections, joinedwith connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc as required.
49.01 | 300mm width X 50mm depthX 1.6mm thickness | 100.00 | Mtr | 596.00 | 3000.00 | 300000.00 | 600.00 | 60000.00 | 950.00 | 95000.00 | 60000.00 | JCC ENGINEERS PRIVATE LIMITED
49.02 | 150mm width X 50mm depth X 1.60mm thickness | 100.00 | Mtr | 765.00 | 2400.00 | 240000.00 | 500.00 | 50000.00 | 500.00 | 50000.00 | 50000.00 | JCC ENGINEERS PRIVATE LIMITED, Vardhman Airport Solutions Limited
50.00 | Supplying and laying of following size DWC HDPE pipe ISI marked along with all accessories like socket, bend, couplers etc. conforming to IS 14930, Part II complete with fitting and cutting, jointing etc. direct in ground (75 cm below ground level) including excavation and refilling the trench but excluding sand cushioning and protective covering etc. complete as required.63 mm dia (OD-63 mm & ID-51 mm nominal) | 2100.00 | Meter | 258.00 | 235.00 | 493500.00 | 180.00 | 378000.00 | 175.00 | 367500.00 | 367500.00 | Vardhman Airport Solutions Limited
51.00 | Supplying and laying of 50mm dia sizes PN 6, PE 80 rating HDPE pipe ISI marked along with all accessories like socket, bend, couplers etc. complete with fitting and cutting, jointing etc.direct in ground (75 cm below ground level) including excavation and refilling the trench but excluding sand cushioning and protective covering etc., complete as required. | 49000.00 | Meter | 223.00 | 260.00 | 12740000.00 | 180.00 | 8820000.00 | 165.00 | 8085000.00 | 8085000.00 | Vardhman Airport Solutions Limited
52.00 | Supplying and making cable route marker with cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size ) of size 60 cm X 60 cm at the bottom and 50 cm X 50 cm at the top with a thickness of 10cm including inscription duly engraved as required. | 50.00 | each | 627.00 | 750.00 | 37500.00 | 500.00 | 25000.00 | 2000.00 | 100000.00 | 25000.00 | JCC ENGINEERS PRIVATE LIMITED
53.00 | SITC of 50 KVA PWM IGBT based level 3 True-On-Line Double Conversion Microprocessor Controlled Modular UPS System (Each UPS shall have modules in N +1 for internal redundancy; each module capacity shall be from 10 KVA to 25 KVA) in parallel configuration of suitable size to be installed for Air Field Ground Lighting System working on 3 phase, 4 Wire, 415 Volt, 50 Hz and delivering output 3 phase, 4 Wire, 415 Volt, 50 Hz , High Efficiency ≥95% , having SMF Batteries to support minimum 30 minutes back up with each UPS, THD less than 3% at full load , Input Phase Sequence Correction should be inbuilt in UPS, Input Power Factor ≥0.99 and Output Power Factor unity, having transfer time of 0 m sec, up along with all accessories i.e. breakers, DC cables, cabinets, battery racks, interconnecting links and related items etc as per site requirement for making the UPS Operational and meeting the standard of IEC and as per specification. | 2.00 | Nos | 1491063.00 | 1650000.00 | 3300000.00 | 1700000.00 | 3400000.00 | 1850000.00 | 3700000.00 | 3300000.00 | AMA Private Limited
54.00 | Design, Fabrication,Supply, Installation, Testing & Commissioning of Distribution LT panel ,cubicle type, made out of 2 mm thick CRCA sheet, totally enclosed, IP 42, free standing, Floor mounting, dust and vermin proof, indoor, compartmentalised, suitable for operation on 3 phase and neutral, 415 V, 50 Hz AC system with busbars extensible on both sides, making interlocking arrangement between incomers, including internal wiring with suitable size wires/cable, interconnection, duly powder coated painting etc., including supply & installation of following switchgears, metering instruments and accessories in the LT Panel confirming to IEC 61439 specifications. INCOMERS 150 A, FP, 35 kA(Ics = 100% of Icu ), MCCB with thermal magnetic release, adjustable thermal & adjustable magnetic setting, spreader links, extended rotory handle etc. - 02 sets Digital voltmeter (0-500 V) with inbuilt selector switch - 02 sets Digital ammeter (0-150 A) with CTs and selector switch - 02 sets R-Y-B phase indicating,on,off tripping lamps LED type- 02 sets Control MCBs for meter & indicators Multifunction Meter-02 Sets BUSBARS 200 Amp, 415 V, TPN busbars of high conductivity electrolytic quality aluminium alloy duly insulated with coloured heat shrinkable sleeve and supported by FRP insulator - 01 set ON indicating lamps(Red) LED type with control MCBs - 19 Nos. Outgoings 32 A, DP , MCB 10KA C-Series for Single phase load. - 13 Nos. Outgoings 63 A, DP, MCB 10KA C-Series for Single phase load. - 6 Nos. | 1.00 | Job | 222705.00 | 650000.00 | 650000.00 | 500000.00 | 500000.00 | 185000.00 | 185000.00 | 185000.00 | Vardhman Airport Solutions Limited
55.00 | Design, Fabrication,Supply, Installation, Testing & Commissioning of Distribution LT panel ,cubicle type, made out of 2 mm thick CRCA sheet, totally enclosed, IP 42, free standing, Floor mounting, dust and vermin proof, indoor, compartmentalised, suitable for operation on 3 phase and neutral, 415 V, 50 Hz AC system with busbars extensible on both sides, making interlocking arrangement between incomers, including internal wiring with suitable size wires/cable, interconnection, duly powder coated painting etc., including supply & installation of following switchgears, metering instruments and accessories in the LT Panel confirming to IEC 61439 specifications. INCOMERS 200 A, FP, 35 kA(Ics = 100% of Icu ), MCCB with thermal magnetic release, adjustable thermal & adjustable magnetic setting, spreader links, extended rotory handle etc. - 02 sets Digital voltmeter (0-500 V) with inbuilt selector switch - 02 sets Digital ammeter (0-150 A) with CTs and selector switch - 02 sets R-Y-B phase indicating,on,off tripping lamps LED type- 02 sets Control MCBs for meter & indicators Multifunction Meter-02 Sets BUSBARS 250 Amp, 415 V, TPN busbars of high conductivity electrolytic quality aluminium alloy duly insulated with coloured heat shrinkable sleeve and supported by FRP insulator - 01 set ON indicating lamps(Red) LED type with control MCBs - 4 Nos. Outgoings 150 A, FP , 35 kA(Ics = 100% of Icu ) for - 4 Nos. | 1.00 | Job | 312848.00 | 550000.00 | 550000.00 | 400000.00 | 400000.00 | 285000.00 | 285000.00 | 285000.00 | Vardhman Airport Solutions Limited
56.00 | Carrying out the field surveys as per following: i) for installation of Inset/Elevated LED/halogen light fittings and all items considered under this contract including taxiway centre line, maneouvering lights as per ICAO / DGCA CAR. ii) after installation of fittings, survey of complete Airfield Ground Lighting facilities viz. visual aids, cable layout, earthings etc. as per site including mapping and depicting of visual ground aids, underground facilities etc. complete as required as per instruction of Engineer-in-charge. This job includes surveys as many times as required with total station/DGPS and other required instruments to complete above i) and ii). The Final layout indicating coordinates shall be submitted as one free size legible colour print copy with frame and hanging arrangement, Three hard colour copy for office file, one copy in PDF and one soft copy in AutoCAD, conforming to technical specifications and complete as required at site. | 1.00 | Job | 318150.00 | 200000.00 | 200000.00 | 100000.00 | 100000.00 | 110000.00 | 110000.00 | 100000.00 | JCC ENGINEERS PRIVATE LIMITED
57.00 | Photometric testing of all Taxiway Centreline lights,Stop Bar,Signages : Carrying out/making in-field measurement of intensity, beam spread, orientation, chromaticity, luminous factor by using vehicle mounted mobile testing equipment / portable hand held system submission of test reports etc as per requirement of ICAO/DGCA Civil Aviation Requirements section-4, Aerodrome standards and licensing, Series-B, Part-I etc complete as required. | 1.00 | Job | 510050.00 | 300000.00 | 300000.00 | 200000.00 | 200000.00 | 230000.00 | 230000.00 | 200000.00 | JCC ENGINEERS PRIVATE LIMITED
58.00 | Earthing with G.I. earth pipe 4.5 metre long, 40 mm dia including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe etc. (with charcoal/ coke and salt ) as required. | 40.00 | Each | 6779.00 | 9000.00 | 360000.00 | 5000.00 | 200000.00 | 8200.00 | 328000.00 | 200000.00 | JCC ENGINEERS PRIVATE LIMITED
59.00 | Earthing with G.I. earth plate 600 mm X 600 mm X 6 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with charcoal/ coke and salt as required. | 4.00 | Each | 7385.00 | 17500.00 | 70000.00 | 5000.00 | 20000.00 | 10900.00 | 43600.00 | 20000.00 | JCC ENGINEERS PRIVATE LIMITED
60.00 | Earthing with copper earth plate 600 mm X 600 mm X 3 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7-metre-long etc. with charcoal/ coke and salt as required. | 4.00 | Each | 13601.00 | 19500.00 | 78000.00 | 20000.00 | 80000.00 | 20000.00 | 80000.00 | 78000.00 | AMA Private Limited
61.00 | Supplying and laying 6 SWG G.I. wire at 0.50 metre below ground level for conductor earth electrode, including connection/ termination with GI thimble etc. as required | 200.00 | Mtr | 51.00 | 30.00 | 6000.00 | 30.00 | 6000.00 | 25.00 | 5000.00 | 5000.00 | Vardhman Airport Solutions Limited
62.00 | Supply and laying of 25 mm X 5 mm G.I. strip in 40 mm dia G.I. pipe from earth electrode including connection with G.I. nut, bolt, spring, washer excavation and re-filling etc. as required | 16.00 | Mtr | 693.00 | 550.00 | 8800.00 | 500.00 | 8000.00 | 700.00 | 11200.00 | 8000.00 | JCC ENGINEERS PRIVATE LIMITED
63.00 | Providing and fixing 25 mm X 5 mm copper strip in 40 mm dia G.I. pipe from earth electrode including connection with brass nut, bolt, spring, washer excavation and re-filling etc. as required. | 12.00 | Mtr | 1517.00 | 550.00 | 6600.00 | 1500.00 | 18000.00 | 2000.00 | 24000.00 | 6600.00 | AMA Private Limited
64.00 | Supply and laying 25 mm X 5 mm G.I. strip on surface or in recess for connections etc. as required | 40.00 | Mtr | 243.00 | 550.00 | 22000.00 | 200.00 | 8000.00 | 220.00 | 8800.00 | 8000.00 | JCC ENGINEERS PRIVATE LIMITED
65.00 | Providing and fixing 25 mm X 5 mm copper strip on surface or in recess for connections etc. as required. | 20.00 | Mtr | 1139.00 | 550.00 | 11000.00 | 1200.00 | 24000.00 | 1450.00 | 29000.00 | 11000.00 | AMA Private Limited
66.00 | Providing and fixing 6 SWG dia G.I. wire on surface or in recess for loop earthing for continuous earthing as required | 60000.00 | Mtr | 70.00 | 20.00 | 1200000.00 | 12.00 | 720000.00 | 19.00 | 1140000.00 | 720000.00 | JCC ENGINEERS PRIVATE LIMITED
67.00 | Supply and Fixing Earth connection from earth electrode with 6 SWG Dia G.I. Wire in 15 mm dia G.I. pipe from earth electrode including connection with G.I. thimble excavation and re-filling as required. | 200.00 | Mtr | 283.00 | 325.00 | 65000.00 | 200.00 | 40000.00 | 400.00 | 80000.00 | 40000.00 | JCC ENGINEERS PRIVATE LIMITED
68.00 | Dismantling of existing elevated runway edge/thershold/runway end/turning pad type light fitting from runway & cleaning of transformer housing box and depositing in AAI store. | 25.00 | Job | 94.00 | 200.00 | 5000.00 | 100.00 | 2500.00 | 75.00 | 1875.00 | 1875.00 | Vardhman Airport Solutions Limited
| Total in Figures |  |  |  |  | 102779561.00 |  | 84406900.00 |  | 85372905.00
Lowest Amount Quoted BY: JCC ENGINEERS PRIVATE LIMITED(84406900.00)

## BOQ Summary
BOQ Summary Details Tender Title: Construction of new civil enclave at Jammu Airport SH SITC of airfield ground light facility at Jammu airport Tender ID: 2025_AAI_253602_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | JCC ENGINEERS PRIVATE LIMITED (BID ID -928399) | 84406900.00 | L1
| 2 | Vardhman Airport Solutions Limited (BID ID -928997) | 85372905.00 | L2
| 3 | AMA Private Limited (BID ID -929126) | 102779561.00 | L3