## BoQ1
Government eProcurement System Created By: Yarava Jaya Subba Reddy Created Date/Time: 03-Dec-2025 04:14 PM Tender Title: Construction of NDB Building at Puducherry Airport SH Tender ID: 2025_AAI_253723_1
Tender Inviting Authority: MANAGER (ENGG-ELECTRICAL), AAI, RHQ-SR, PUDUCHERRY AIRPORT-605008
Name of Work: Construction of NDB Building at Puducherry Airport SH: Provision of Fire Suppression System and its Associated Works including AICMC for 05 Years after 02 Years DLP
Contract No: 2025_AAI_253723_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | GLOBE DETECTIVE AGENCY PVT. LTD., Electronics Division (GSTN-NA) BID ID -922787 |  | Kalpataru Industries (GSTN-NA) BID ID -930129
[5 empty] | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | SH I : DSITC of Fire Suppression System and Fire Alarm System
1.01 | Design, Supply, Installation, Testing & Commissioning of Fire Suppression System for following areas using Gas (clean agent) as per NFPA 2001 complete with the following: Supply of Cylinder UL listed/FM/VDS/LPCB/CCOE(PESO) Approved, complete with valve assembly and arrangement, supervisory switch connection for monitoring cylinder pressure, a pressure gauge with a safety burst disc, electronic control head / Solenoid, pressure operated control, head, flexible hose, strap, NRV, safety cap, Gas discharge Warning sign etc. complete as required. Gas - Quantity would be as per the design volume and as per the necessary codal specifications UL Certifications. Clean agent shall be of FK-5-1-12 Gas flooding System. All the necessary inteconnections by supplying and Laying of MS Pipes as per design with Nozzles, Supply, Installation, Testing and Commissioning of Gas Release Panel complete with timer, battery back up, Gas Release / Gas Abort Switch, Integration with Fire Alarm panel, all connections, accessories required for commissioning of the system etc. complete as required (Make : As per AAI List of Preferred makes) Note: The System will be provided in specified areas only as below.
1.02 | The contractor will design the system as per NFPA 2001. The contractor will get the design approved by AAI before execution. Statutory Approvals will be taken from concerned authorities. The piping design and pressure calaculations using manufacturer design software for a given dimension of room duly approved by manufacturer/distributors shall be submitted prior to starting of the work. Complete system design using certified design software, shall be duly vetted by the manufacturer (OEM) and submitted to the Engineer-in-Charge for approval before the commencement of work.
1.03 | Equipment Room: LxB = 3750 mm x 5000 mm ; Height till false ceiling = 3175 mm ; False ceiling height = 300 mm; Independent fire suppression system with individual gas release panel shall be provided.
1.04 | Battery Room : LxB = 2175 mm x 3250 mm ; Height = 3475 mm ; No False Height Independent fire suppression system with individual gas release panel shall be provided.
1.05 | Electrical room : 2675 mm x 3250 mm; Height = 3475 mm ; No false height. Independent fire suppression system with individual gas release panel shall be provided for each rooms.
1.06 | Total (1.01 to 1.05) | 1.00 | Job |  | 1752578.00 | 1752578.00 | 749856.00 | 749856.00 | 749856.00 | Kalpataru Industries
1.20 | Supply, Installation, Testing & Commissioning of UL/LPCB/ EN listed (latest version) Modular Microprocessor based expandable Intelligent Addressable Type Fire Alarm Control Panel of Minimum two loops, with minimum 160 character graphics / LCD display with touch screen or other keypad and minimum 1000 events history log in the non volatile memory (EPROM), Graphical Display, sufficient numbers of programmable relay controls, Modules, 230 volts, 50 Hz AC power supply, automatic battery charger, 12/24 volts sealed maintenance free lead acid batteries etc. complete as required. The panel shall be capable of activating Gas Releasing Control Module on activation of MCP for operating the Gas based Fire Suppression System. (Make : As per AAI List of Preferred makes) | 3.00 | Each |  | 159840.00 | 479520.00 | 105398.00 | 316194.00 | 316194.00 | Kalpataru Industries
1.30 | Supply, Installation, Testing & Commissioning of UL / EN listed (latest version) intelligent addressable multi criteria detector {Smoke + heat } with inbuilt fault isolator / isolator base and with visible LED, fully coated circuit board, superior RF / Transient protection suitable for 2 wires loop connection, complete with plug into common separate base & housing complete with connections etc. as required and to be installed below / above false ceiling roof and concealed space and as per enclosed specifications, etc. complete as required. (Cost of plug in common base shall deemed to be included in cost of detectors) (Make : As per AAI List of Preferred makes) | 16.00 | Each |  | 4664.00 | 74624.00 | 2900.00 | 46400.00 | 46400.00 | Kalpataru Industries
1.40 | Supply, installation, Testing and Commissioning of UL / EN listed (Latest Version) Response Indicators for getting fire indications of detectors i/c mounting boxes installed above false ceiling area interconnecting to loop cable etc. complete as required. | 8.00 | Each |  | 709.00 | 5672.00 | 1644.00 | 13152.00 | 5672.00 | GLOBE DETECTIVE AGENCY PVT. LTD., Electronics Division
1.50 | Supply, Installation, Testing & Commissioning of UL / EN listed (latest version) intelligent addressable Manual call station (Resetable pull / push lever type) suitable for semi flush mounting, IP 54 for indoor use & IP 65 for outdoor use with inbuilt fault isolator / isolator module with double gang outlet box, equipment for key operated test-reset lock, electronic or rotary switches for address setting. Manual pull station shall be connected with two wire to SLC loop of Fire Control Panel etc. complete as required. (Make : As per AAI List of Preferred makes) | 4.00 | Each |  | 7158.00 | 28632.00 | 3990.00 | 15960.00 | 15960.00 | Kalpataru Industries
1.60 | Supply, installation, testing and commissioning of UL / EN listed (latest version) loop powered addressable Hooter - Cum - Strobe with inbuilt fault isolator/isolator, Power supply unit, Input/Output module, termination, etc. complete as required. (Make : As per AAI List of Preferred makes) | 4.00 | Each |  | 6039.00 | 24156.00 | 8680.00 | 34720.00 | 24156.00 | GLOBE DETECTIVE AGENCY PVT. LTD., Electronics Division
1.70 | Supply, installation, testing and commissioning of auto dialer with landline dialer capability along with SIM Card compatible to addressable fire control panel , capable of delivering pre recorded voice to reset telephone no. in case of fire through mobile network, complete with all necessary accessories, connections etc. as required. | 4.00 | Each |  | 26224.00 | 104896.00 | 17800.00 | 71200.00 | 71200.00 | Kalpataru Industries
1.80 | Supplying & laying of Fire Survival cable 2Cx1.5 sqmm armoured cable, 600/1000V rated with annealed copper conductor having XLPE insulation, steel wire armouring etc. complete as required. (Make : As per AAI List of Preferred makes) | 300.00 | Mtr |  | 312.00 | 93600.00 | 168.00 | 50400.00 | 50400.00 | Kalpataru Industries
2.00 | SH: II -All Inclusive Comprehensive Maintenance Contract (AICMC) of Fire Suppression System and Fire Alarm System
2.01 | All Inclusive Comprehensive Maintenance (AICMC) of Automatic Gaseous Fire Suppression System along with Fire Alarm System installed in NDB Building at Puducherry Airport as per SH-I including supply and replacement of all Mechanical & Electrical components like Pipe lines, Valves, Panels, Spares & Consumables (Except Supply of Clean agent) etc. as and when required to keep the system in 100% service condition. The scope of work includes unlimited breakdown visits, providing full support during breakdown & trouble shooting, including refilling, transportation cost and testing of the clean agent, programming, carrying out QUARTERLY routine maintenance checks, preventive and breakdown maintenance as required as per good engineering practices, Recommendations of the respective Original Equipment Manufacturer (OEM) and instructions of Engineer-In-Charge for maintaining the systems, submission of Quarterly maintenance service records and Reporting etc. complete as required.
2.02 | First Year after Completion of 02 (Two) year DLP (Considered 5% of SITC Cost of item No 1.1 to 1.8 i.e SH I) | 1.00 | Annum |  | 128183.90 | 128183.90 | 64894.10 | 64894.10 | 64894.10 | Kalpataru Industries
2.03 | Second Year after Completion of First Year after DLP (Considered 6% Cumulative enhancement on 1st Year AICMC Rate ) | 1.00 | Annum |  | 135874.93 | 135874.93 | 68787.75 | 68787.75 | 68787.75 | Kalpataru Industries
2.04 | Third Year after Completion of Second Year after DLP (Considered 6% Cumulative enhancement on 2nd Year AICMC Rate ) | 1.00 | Annum |  | 144027.43 | 144027.43 | 72915.02 | 72915.02 | 72915.02 | Kalpataru Industries
2.05 | Fourth Year after Completion of Third Year after DLP (Considered 6% Cumulative enhancement on 3rd Year AICMC Rate ) | 1.00 | Annum |  | 152669.08 | 152669.08 | 77289.92 | 77289.92 | 77289.92 | Kalpataru Industries
2.06 | Fifth Year after Completion of Fourth Year after DLP (Considered 6% Cumulative enhancement on 4th Year AICMC Rate ) | 1.00 | Annum |  | 161829.22 | 161829.22 | 81927.32 | 81927.32 | 81927.32 | Kalpataru Industries
2.07 | Supply of FK-5-1-12 Clean agent gas (as and when required for refilling on need basis) as per the directions of Engineer- In - Charge | 200.00 | Kg |  | 3540.00 | 708000.00 | 1435.00 | 287000.00 | 287000.00 | Kalpataru Industries
| Total in Figures |  |  |  |  | 3994262.56 |  | 1950696.11
Lowest Amount Quoted BY: Kalpataru Industries(1950696.11)

## BOQ Summary
BOQ Summary Details Tender Title: Construction of NDB Building at Puducherry Airport SH Tender ID: 2025_AAI_253723_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Kalpataru Industries (BID ID -930129) | 1950696.11 | L1
| 2 | GLOBE DETECTIVE AGENCY PVT. LTD., Electronics Division (BID ID -922787) | 3994262.56 | L2