## BoQ1
Government eProcurement System Created By: Sachin Khangar Created Date/Time: 01-Dec-2025 04:00 PM Tender Title: Provision of area Lighting for garden and children park area in AAI residential colony including Allied electrical work at Vadodara Airport Tender ID: 2025_AAI_254295_1
Tender Inviting Authority: Joint.Gen. Manager(E-E), AAI, CA, Vadodara
Name of Work :Provision of lighting for garden, children park, entrance road along with other elctrical work inside AAI residential colony, Vadodara.
Contract No:
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Techno Electricals (GSTN-24AAGFT9086M1ZG) BID ID -928597 |  | BR Power Control and Automation Services (GSTN-06AREPS4024K1ZP) BID ID -928624 |  | surbhi association (GSTN-23AGKPD2522N1ZK) BID ID -928772 |  | ENGINEERING SOLUTIONS (GSTN-NA) BID ID -928680 |  | Krishsons International Engineers And Consultants (I) Pvt. Ltd (GSTN-NA) BID ID -928788
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Design, manufacture & Supply of 14M high mast system complete with all accessories as per detailed tender technical specification. Mast shaft shall be in two sections, hot dip galvanised and suitable for wind velocity minimum 50m/s. It shall also include accessories for high mast inclduing head frame, steel wire rope 6 mm dia (constructed from stainless steel AISI 316 or better) with electrically operated raising and lowering mechanism, luminaries carriage suitable to install 8 nos. of LED Light fixtures in 0°-180°of horizontal plane and suitable counterweight in 180°-360°of horizontal plane with its accissories in symmetrical arrangement, double drum winch, 2 nos. 1.1 KV grade 5C x 2.5Sqmm flexible EPR/ PCP cotton braided copper conductor trailing cable, 5 pin [3P + N + E] plug and 32A water tight GT connector(IP67) with cable sleev, junction box, lightening finial, LED obstructuion light, Foundation bolts manufactured from special steel along with nuts, washers, anchor plate and common template (as per OEM standard) etc. The mast shall have an integral power tool motor, manual handle installed inside the base compartment for its operation including supply of all the required harware items etc. complete as required as per tender specifications. | 4.00 | Each |  | 183000.00 | 732000.00 | 111684.00 | 446736.00 | 225000.00 | 900000.00 | 170160.00 | 680640.00 | 105000.00 | 420000.00 | 420000.00 | Krishsons International Engineers And Consultants (I) Pvt. Ltd
2.00 | Supply, Erection, Testing and Commissioning of hot dipped galvanized octagonal Street light pole of 7 metre long made out of 3mm thick sheet having top dia 70 mm and bottom dia 130 mm with single arm of size 500mm at boom angle as per lighting design complete with 12 mm thick MS sheet base plate of size 220 mm X 220 mm i/c stiffner and 04 Nos. foundation bolts of size 20 mm dia and suitable size cut-out opening for cable entry as per techincal specification including errection on the CC pedestal etc complete as required. The pole shall be installed in RCC foundation made as per manufacturer recommended design including excavation & refilling in soil/hard rock/concrete with the help of breaker machine by laying iron barmesh fabricated with 8 mm, 10 mm & 12 mm dia iron bar as per the manufacturer design complete as required as per tender technical specifications. (cost of the Lighting design and pole foundation work is included in the item) | 16.00 | Each |  | 10808.00 | 172928.00 | 15941.00 | 255056.00 | 15295.00 | 244720.00 | 16800.00 | 268800.00 | 12990.00 | 207840.00 | 172928.00 | Techno Electricals
3.00 | Supply of Flood Light, powder coated pressure die cast aluminum body with built in or separate driver as per the requirement with Driver efficiency >85%, Input voltage: Input voltage: 140-270 Volt AC, freq 50/60 hz, Operating temp range -15 deg to 50 deg centigrade, internal surge protection of 5 KV L,N,E as per IEC 61000-4-5, Driver efficiency >85%,THD < 10% as per IEC 61000-3-2 , P. F.≥0.95, IP-66,IK-10, CRI >80 , under voltage and over voltage protection, EMI-EMC as per CISPR-15, lenses for beam angle 30 deg- 120deg as per the application and the project requirement deg, suitable tilt able fitting, life time (LED,Driver & electrical circuitry) of minimum 50000 Burning Hours with 70% of initial Lumen maintained till life ends as per LM80 extrapolation IES TM-21-11 report , CCT 5700K (As per ANSI Bin) , SDCM(Standard Deviation Color Matching) <5, Maximum power consumption should not more than the specified rating and Fixture shall be of relevant BIS standard complete in all respect etc. as required with Minimum 5 year OEM warranty. System lumen efficacy ≥120 and <135 lm/Watt output . LM79 & LM80 Test report from NABL lab for all testing required for LED fixtures as per BIS shall be submitted. Shape size and CCT shall be as approved by Engineer-in-Charge as per requirement & as per tender specifications. (Thermal management: heat sink of aluminum housing such that LED junction temperature shall not rise above 90°C).- 300W | 20.00 | Each |  | 9970.00 | 199400.00 | 10102.00 | 202040.00 | 11500.00 | 230000.00 | 10200.00 | 204000.00 | 8900.00 | 178000.00 | 178000.00 | Krishsons International Engineers And Consultants (I) Pvt. Ltd
4.00 | Supply of Street light LED fixture powder coated pressure die cast aluminum body with driver as per the requirement with Driver efficiency >85%, Input voltage: 140-270 Volt AC, freq 50/60 hz, Operating temp range -15 deg to 50 deg centigrade, internal surge protection of 5 KV L,N,E as per IEC 61000-4-5, Driver efficiency >85%,THD < 10% as per IEC 61000-3-2 , P. F.≥0.95, IP- 66,IK-10, CRI >80, under voltage and over voltage protection, EMIEMC As per CISPR 15 , lenses for beam angle as per IESNA type I/II/III as per the width of the road and the project requirement., suitable to fit in up to 65mm dia pipe, life time (LED,Driver & electrical circuitry) of minimum 50000 Burning Hours with 70% of initial Lumen maintained till life ends as per LM80 extrapolation IES TM-21-11 report, CCT 3000°K / 4000°K / 5700°K /6000°K/6500°K (As per ANSI Bin), SDCM(Standard Deviation Color Matching) <5, Maximum power consumption should not more than the specified rating and Fixture shall be of relevant BIS standard complete in all respect etc. as required with Minimum 5 year OEM warranty. System lumen efficacy ≥120 <135 lm/Watt output . LM79 & LM80 Test report from NABL lab for all testing required for LED fixtures as per BIS shall be submitted. Shape size and CCT shall be as approved by Engineer-in-Charge as per requirement & as per tender specifications. (Thermal management: heat sink of aluminum housing such that LED junction temperature shall not rise above 90°C).- 70W | 20.00 | Each |  | 2520.00 | 50400.00 | 2617.00 | 52340.00 | 2300.00 | 46000.00 | 2040.00 | 40800.00 | 2300.00 | 46000.00 | 40800.00 | ENGINEERING SOLUTIONS
5.00 | Installation, Testing & Commissioning of 14M high mast system complete with all accessories including Soil testing, design & construction of RCC foundation suitable for 50M/s wind velocity withstand capacity with all materials and labour as per manufacturers recomendations including excavation, backfilling and concreting with grade not less than M25 as per the approved Foundation design. along with fixing of templates, foundation bolts, trailing cable with plug and GT connector, installation of LED Flood Light luminiaries, LED Aviation obstruction light & its wiring, numbering, necessary wiring from junction box to indiviual luminaire & MCB in base compartment with all required accessories, terminations, connection etc. complete as required as per approved lighting design scheme, foundation drawing and tender specifications. | 4.00 | Job |  | 67000.00 | 268000.00 | 115001.00 | 460004.00 | 125000.00 | 500000.00 | 80000.00 | 320000.00 | 60000.00 | 240000.00 | 240000.00 | Krishsons International Engineers And Consultants (I) Pvt. Ltd
6.00 | Supply and fixing of side hinged-door fixed with base SMC junction Box of size 250mmx200mmx100mm (Loop-in-Loop-out Box) on the GI pole with suitable size MS clamp including providing & fixing 63A, 4Pole connector (for loop in & loop out to terminate 2Nos, 4 core 25 sq. mm. armoured aluminum cable) and 6Amp SP MCB 'C' curve in din rail, Interconnection etc. as required. (Make: Sintex: model no. JS-JB-2520 or its equivalent) | 16.00 | Nos. |  | 1700.00 | 27200.00 | 2175.00 | 34800.00 | 1400.00 | 22400.00 | 2880.00 | 46080.00 | 700.00 | 11200.00 | 11200.00 | Krishsons International Engineers And Consultants (I) Pvt. Ltd
7.00 | ITC of LED street light fitting on existing pole of height upto 8mtr. from ground level including supplying and drawing 3C x 1.5 sq.mm FR PVC insulated copper conductor cable in the pole from fitting to pole junction box including connection, testing and commissioning etc. complete as required. | 12.00 | Nos. |  | 1000.00 | 12000.00 | 961.00 | 11532.00 | 400.00 | 4800.00 | 960.00 | 11520.00 | 700.00 | 8400.00 | 4800.00 | surbhi association
8.00 | Feeder Pillar (HIGH MAST PANEL) Supply, Installation, Testing and commissioning of Outdoor type double door, weather proof, fully compartmentalised, free standing type, duly painted outdoor type feeder pillar/control cum power panel (IP 55 protection) fabricated from 2mm thick CRCA sheet with outer door having lever type SS handle lock and having Switchgears & Accessories:- (i) 1 no. 40 Amps 4P MCB Incomer, (ii) digital astronomical time Switch, (iii) 1no. 32A C-curve 10KA 4P MCB and 1 no. 25 Amps 4P Contactors connected via timer for automatic and manual switching of luminaires, (iv) Toggle swith for auto/maual selection, (v) 2 nos. 4P power contactors (25 Amps) with LED lit push buttons each for lowering and raising of lantern carriage of high mast directly connected to main bus, (vi) 1 no. 32A 4P MCB and two nos. 15A Power outlet Switch-socket outgoning directly connected to main bus, (vii) 2.5sqmm sizes power and control wirings with control MCB, (viii) R-Y-B indication lamp, (ix) Digital voltage and ampare meter and other required controls, switchgears and accessories required for satisfactory operation of high mast lighting tower along with Earth bus, MS angle mounting legs , Suitable size cement concrete foundation with all around 600mm width cement concrete pedestal i/c fixing of HDPE pipe in foundation for cable entry complete as per tender specification and drawing as required. (Feeder Pillar should be PTTA type only) | 4.00 | Job |  | 37000.00 | 148000.00 | 94699.00 | 378796.00 | 30000.00 | 120000.00 | 55000.00 | 220000.00 | 90000.00 | 360000.00 | 120000.00 | surbhi association
9.00 | LT Panel (Old Power House) Design, fabrication, supply, installation, testing and commissioning of Indoor type, weather proof, dust & vermin proof, Epoxy powder coated with 7 tank chemical process, RAL-7032 Shade, duly painted, fully compartmentalised free standing type outdoor type Floor Mounted panel (with IP 54 protection) fabricated from 2mm thick CRCA sheet including making suitable size concreate foundation, providing suitable angle/ channels frame (400mm minimum height from Ground floor), providing suitable size of HDPE bend pipe in foundation for cable entry, supply and fixing of following switchgears and accessories complete with busbars,glande plates, neutral link, interconnections, earth connections, control MCBs, cast rasin type CT's, multifunction meters with selector switches and LED phase indicating lamps, rivetted metal plate nomenclature etc complete as required as per tender specifications, Drawing, site requirement and approved make. (Main LT Panel) Incomer: 1) 630 A, 4P, 50 kA (Icu= 100% Ics) thermal magnetic release type MCCB having overload and short circuit protection along with suitable extended rotary handle and spreaders - 02 Nos. (Both Incomer shall be electrically and mechnically interlocked with 2 lock and 1 key) 2) 3 phase Multi function meter (Shows Voltage, Current, Power, Energy & Frequency) with 3 line LCD Display, RS485 CL-0.5 including protection fuses/MCBs and 3 Nos of class 1.0, 15VA CTs Each - 02 Nos. 3) Indication Lamp R, Y & B (LED Type) -02 set 4) Indication Lamp for on/off/trip R,G & W (LED Type) -02 set | 1.00 | Job |  | 350000.00 | 350000.00 | 725644.00 | 725644.00 | 615000.00 | 615000.00 | 300000.00 | 300000.00 | 690000.00 | 690000.00 | 300000.00 | ENGINEERING SOLUTIONS
9.01 | Outgoing : 1) 63A, MCCB, 4P, 35-37KA (Icu= 100% Ics) with extended rotary handle - 06 Nos. 2) Indication Lamp R & G (LED type) - 06 Set 3) 125A, MCCB, 4P, 35-37 KA (Icu= 100% Ics) with extended rotary handle - 04 Nos. 4) Indication Lamp R & G (LED type) - 04 Set 5) 250 A, MCCB, 4P, 35-37KA (Icu= 100% Ics) with extended rotary handle - 05 Nos. 6) Indication Lamp R & G (LED type) - 05 Set Other : 1) 900A AL busbar, 4 Pole 2) Necessary CT & Control wiring arrangement. 3) Power terminal Block and other accessories 4) Three Phase Surge Protection Device (SPD) having nominal dischage current (L-N/N-PE) =25 /100 kA (8/20 us) Lightning impulse current (L1 + L2 + L 3 + N -PE=100kA (10/350 us) & (L-N / N-PE = 25/100 kA) with voltage protection level <=1.5 kV (L-N/N-PE) including all accessories for installing on the mains power entry point at the busbar shall be of modular type. [ Make:-DEHN Model No. DV M TT 255 FM (951 315) or equivalent appproved make ] - 01 No. (Feeder Pillar should be PTTA type only)
10.01 | Supply of following size and rating ceiling fans :- 900mm, AC 1 Ph. capacitor start run motor with air delivery 135 CM/Min (Minimum) , Class-'B' insulation, 3 nos. metal (CRCA) blades, 30 cm long down rod, double ball bearing, 2 nos. canopies, shackle kit, safety rope, copper winding, steel/Al body Power Factor not less than 0.9, Service Value (CM/M/W) minimum 3.2CMW, 380 RPM at 230V (all tolerance as per IS : 374-2019), suitable for operation with regulator for speed control and all remaining accessories including safety pin, nut bolts, washers, suitable for 230 V, 50 Hz, single phase AC Ceiling Fan compliant to IS 374:2019 with minimum 2 years warranty etc. complete as required. | 50.00 | Each |  | 2700.00 | 135000.00 | 1744.00 | 87200.00 | 1550.00 | 77500.00 | 4200.00 | 210000.00 | 1630.00 | 81500.00 | 77500.00 | surbhi association
10.02 | Supply of following size and rating ceiling fans :- 1200mm, service value ≥ 6.0 CM/Min/Watt, air delivery 215 CM/Min (Minimum) with Brush Less Direct Current (BLDC) Motor, class of insulation: B, 3 nos. metal (Aluminum alloy) blades, 30 cm long down rod, double ball bearing, 2 nos. canopies, shackle kit, safety rope, copper winding, steel/Al body Power Factor not less than 0.9, Service Value (CM/M/W) minimum 7CMW, 350 RPM (tolerance as per IS : 374-2019), THD (Total Harmonic Distortion) less than 10%, 4KV grade surge protection, suitable for operation with step regulator(capacitor type) for speed control and all remaining accessories including safety pin, nut bolts, washers, temperature rise=50 degree C (max.), insulation resistance more than 2 mega ohm, suitable for 230 V, 50 Hz, single phase AC Ceiling Fan compliant to IS 374:2019 with minimum 2 years warranty etc. complete as required. | 180.00 | Each |  | 2696.00 | 485280.00 | 2402.00 | 432360.00 | 2200.00 | 396000.00 | 5400.00 | 972000.00 | 2150.00 | 387000.00 | 387000.00 | Krishsons International Engineers And Consultants (I) Pvt. Ltd
11.00 | Supply of plastic body, 300mm sweep, 900 rpm heavy duty exhaust fan suitable for 220-240 volts, 50hz, single phase A.C supply with all accessories including supply of louvers / shutters etc as required. | 50.00 | Each |  | 3200.00 | 160000.00 | 2855.00 | 142750.00 | 1450.00 | 72500.00 | 3000.00 | 150000.00 | 1350.00 | 67500.00 | 67500.00 | Krishsons International Engineers And Consultants (I) Pvt. Ltd
12.00 | Installation, testing and commissioning of ceiling fan, including wiring the down rods of standard length (upto 30 cm) with 1.5 sq. mm FRLS PVC insulated, copper conductor, single core cable etc as required. | 193.00 | Each |  | 200.00 | 38600.00 | 502.00 | 96886.00 | 90.00 | 17370.00 | 700.00 | 135100.00 | 100.00 | 19300.00 | 17370.00 | surbhi association
13.00 | Installation of exhaust fan upto 300mm i/c louvers/shutters in the existing wall, including modifying the hole to suit the size of exhaust fan, making good the damage, connection, testing, commissioning etc as required. | 41.00 | Each |  | 800.00 | 32800.00 | 503.00 | 20623.00 | 80.00 | 3280.00 | 600.00 | 24600.00 | 100.00 | 4100.00 | 3280.00 | surbhi association
14.01 | Supply of following size XLPE insulated PVC sheathed Aluminium conductor armoured power cable of 1.1 KV grade confirming to IS 7098 (Part-I) with up to date ammendment etc. complete as required. 3.5C x 50 sq. mm. | 200.00 | Mtrs. |  | 275.00 | 55000.00 | 297.00 | 59400.00 | 335.00 | 67000.00 | 300.00 | 60000.00 | 300.00 | 60000.00 | 55000.00 | Techno Electricals
14.02 | Supply of following size XLPE insulated PVC sheathed Aluminium conductor armoured power cable of 1.1 KV grade confirming to IS 7098 (Part-I) with up to date ammendment etc. complete as required. 3.5C x 25 sq. mm. | 500.00 | Mtrs. |  | 168.00 | 84000.00 | 173.00 | 86500.00 | 205.00 | 102500.00 | 160.00 | 80000.00 | 195.00 | 97500.00 | 80000.00 | ENGINEERING SOLUTIONS
14.03 | Supply of following size XLPE insulated PVC sheathed Aluminium conductor armoured power cable of 1.1 KV grade confirming to IS 7098 (Part-I) with up to date ammendment etc. complete as required. 4C x 16 sq. mm. | 400.00 | Mtrs. |  | 130.00 | 52000.00 | 149.00 | 59600.00 | 165.00 | 66000.00 | 150.00 | 60000.00 | 180.00 | 72000.00 | 52000.00 | Techno Electricals
15.00 | Supply of 50mm dia.(O.D.) HDPE pipe (High Density Polyethylene) of grade PE80, PN6 ISI marked along with all accessories like socket, bend, couplers etc. conforming to IS 4984:1995 with latest ammendments complete as required. | 800.00 | Mtrs. |  | 85.00 | 68000.00 | 112.00 | 89600.00 | 100.00 | 80000.00 | 75.00 | 60000.00 | 90.00 | 72000.00 | 60000.00 | ENGINEERING SOLUTIONS
16.00 | Laying of DWC/HDPE pipe (High Density Polyethylene) of 50mm dia. direct in ground up to a depth of 75 cm including excavation and refilling the trench complete with fitting, cutting and jointing etc. as required. | 800.00 | Mtrs. |  | 90.00 | 72000.00 | 140.00 | 112000.00 | 80.00 | 64000.00 | 54.00 | 43200.00 | 70.00 | 56000.00 | 43200.00 | ENGINEERING SOLUTIONS
17.00 | Laying of 110mm B-class GI pipe direct in ground up to a depth of 300mm under hard/concrere/bituminous surface including breaking of all type of surface and repairing the same with providing and laying 100mm thick in position cement concrete of 1:3:6 ( i.e 1 cement: 3 coarse sand: 6 graded stone) including desposing the excavated dirt/soil/boulder at a location directed by E-I-C complete as required. | 30.00 | Mtrs. |  | 350.00 | 10500.00 | 475.00 | 14250.00 | 1700.00 | 51000.00 | 130.00 | 3900.00 | 400.00 | 12000.00 | 3900.00 | ENGINEERING SOLUTIONS
18.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade Upto 35 sq. mm cable size in the existing RCC/ HUME/ METAL pipe as required. | 650.00 | Mtrs. |  | 25.00 | 16250.00 | 85.00 | 55250.00 | 20.00 | 13000.00 | 50.00 | 32500.00 | 15.00 | 9750.00 | 9750.00 | Krishsons International Engineers And Consultants (I) Pvt. Ltd
19.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade above 35 sqmm. And Upto 95sqmm. sq. mm cable size in the existing RCC/ HUME/ METAL pipe as required. | 150.00 | Mtrs. |  | 25.00 | 3750.00 | 111.00 | 16650.00 | 30.00 | 4500.00 | 144.00 | 21600.00 | 20.00 | 3000.00 | 3000.00 | Krishsons International Engineers And Consultants (I) Pvt. Ltd
20.01 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 kV grade as required. 3.5 x 50 sq. mm. | 4.00 | Each |  | 400.00 | 1600.00 | 802.00 | 3208.00 | 350.00 | 1400.00 | 650.00 | 2600.00 | 365.00 | 1460.00 | 1400.00 | surbhi association
20.02 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 kV grade as required. 3.5 x 25 sq. mm. | 10.00 | Each |  | 350.00 | 3500.00 | 626.00 | 6260.00 | 250.00 | 2500.00 | 500.00 | 5000.00 | 299.00 | 2990.00 | 2500.00 | surbhi association
20.03 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 kV grade as required. 4C x 16 sq. mm. | 24.00 | Each |  | 300.00 | 7200.00 | 493.00 | 11832.00 | 200.00 | 4800.00 | 500.00 | 12000.00 | 300.00 | 7200.00 | 4800.00 | surbhi association
21.00 | Earthing with G.I. earth plate 600 mm X 600 mm X 6 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 meter long etc. with charcoal/ coke and salt as required. | 8.00 | Each |  | 6500.00 | 52000.00 | 10020.00 | 80160.00 | 6500.00 | 52000.00 | 18000.00 | 144000.00 | 5000.00 | 40000.00 | 40000.00 | Krishsons International Engineers And Consultants (I) Pvt. Ltd
22.00 | Providing and fixing 25 mm X 5 mm G.I. strip in 40 mm dia G.I. pipe from earth electrode including connection with G.I. nut, bolt, spring, washer excavation and re-filling etc. as required. | 50.00 | Mtrs. |  | 600.00 | 30000.00 | 264.00 | 13200.00 | 500.00 | 25000.00 | 180.00 | 9000.00 | 600.00 | 30000.00 | 9000.00 | ENGINEERING SOLUTIONS
23.00 | Providing and fixing 25 mm X 5 mm G.I. strip on surface or in recess for connections etc. as required. | 30.00 | Mtrs. |  | 225.00 | 6750.00 | 230.00 | 6900.00 | 150.00 | 4500.00 | 180.00 | 5400.00 | 155.00 | 4650.00 | 4500.00 | surbhi association
24.00 | Earthing with G.I. earth pipe 4.5 meter long, 40 mm dia including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe etc. with charcoal/ coke and salt as required. | 10.00 | Each |  | 6000.00 | 60000.00 | 8003.00 | 80030.00 | 6500.00 | 65000.00 | 19200.00 | 192000.00 | 4000.00 | 40000.00 | 40000.00 | Krishsons International Engineers And Consultants (I) Pvt. Ltd
25.00 | Providing and laying earth connection from earth electrode with 6 SWG dia G.I. Wire in 15 mm dia G.I. pipe from earth electrode including connection with G.I. thimble excavation and re-filling as required. | 40.00 | Mtrs. |  | 225.00 | 9000.00 | 55.00 | 2200.00 | 240.00 | 9600.00 | 10.00 | 400.00 | 150.00 | 6000.00 | 400.00 | ENGINEERING SOLUTIONS
26.00 | Providing and fixing 6 SWG dia G.I. wire on surface or in recess for loop earthing as required. | 500.00 | Mtrs. |  | 19.00 | 9500.00 | 38.00 | 19000.00 | 22.00 | 11000.00 | 27.00 | 13500.00 | 20.00 | 10000.00 | 9500.00 | Techno Electricals
| Total in Figures |  |  |  |  | 3352658.00 |  | 4062807.00 |  | 3873370.00 |  | 4328640.00 |  | 3245390.00
Lowest Amount Quoted BY: Krishsons International Engineers And Consultants (I) Pvt. Ltd(3245390.00)

## BOQ Summary
BOQ Summary Details Tender Title: Provision of area Lighting for garden and children park area in AAI residential colony including Allied electrical work at Vadodara Airport Tender ID: 2025_AAI_254295_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Krishsons International Engineers And Consultants (I) Pvt. Ltd (BID ID -928788) | 3245390.00 | L1
| 2 | Techno Electricals (BID ID -928597) | 3352658.00 | L2
| 3 | surbhi association (BID ID -928772) | 3873370.00 | L3
| 4 | BR Power Control and Automation Services (BID ID -928624) | 4062807.00 | L4
| 5 | ENGINEERING SOLUTIONS (BID ID -928680) | 4328640.00 | L5